13204566 | OTA-WKM-C-0364-Insulator Set-OHW-OTA-2 | OTA-WKM-C0364 | OTA-WKM-C0364-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-08 15:01
13247615 | OTA-WKM-C-0364-Earthwire Attachment | OTA-WKM-C0364 | OTA-WKM-C0364-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-09 | WO# 3000629
13247615 | OTA-WKM-C-0364-Earthwire Attachment | OTA-WKM-C0364 | OTA-WKM-C0364-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-09 | WO# 3000629
13247615 | OTA-WKM-C-0364-Earthwire Attachment | OTA-WKM-C0364 | OTA-WKM-C0364-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-09 | WO# 3000629
13247615 | OTA-WKM-C-0364-Earthwire Attachment | OTA-WKM-C0364 | OTA-WKM-C0364-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-09 | WO# 3000629
13286383 | OTA-WKM-C-0364-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0364 | OTA-WKM-C0364-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 Attach Point Replacement 24-25 project
13286383 | OTA-WKM-C-0364-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0364 | OTA-WKM-C0364-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 Attach Point Replacement 24-25 project
13286383 | OTA-WKM-C-0364-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0364 | OTA-WKM-C0364-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 Attach Point Replacement 24-25 project
13286383 | OTA-WKM-C-0364-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0364 | OTA-WKM-C0364-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 Attach Point Replacement 24-25 project
10046896 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-2 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 15:21
10046896 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-2 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 15:21
10046896 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-2 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046896 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-2 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-20 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046896 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-2 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 15:21
10046897 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-1 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 15:20
10046897 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-1 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 15:20
10046897 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-1 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046897 | OTA-WKM-C-0364-0365-Conductor-OHW-OTA-1 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 15:20
10046898 | OTA-WKM-C-0364-0365-Earthwire-A0 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 15:06
10046898 | OTA-WKM-C-0364-0365-Earthwire-A0 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 15:06 | Surface pitting
13329848 | OTA-WKM-C-0364-0365-Earthwire-C0 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 | CA copied from EW A0 Feb/2026
13329848 | OTA-WKM-C-0364-0365-Earthwire-C0 | OTA-WKM-C0364-0365 | OTA-WKM-C0364-0365-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 | Surface pitting. CA copied from EW A0 Feb/2026
10046087 | OTA-WKM-C-0365-Tower | OTA-WKM-C0365 | OTA-WKM-C0365-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-12 | CA - E/W Attachmetn plates rusty and metal loss
10046087 | OTA-WKM-C-0365-Tower | OTA-WKM-C0365 | OTA-WKM-C0365-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-12 | CA - E/W Attachmetn plates rusty and metal loss
10046087 | OTA-WKM-C-0365-Tower | OTA-WKM-C0365 | OTA-WKM-C0365-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-12 | CA - E/W Attachmetn plates rusty and metal loss
10046087 | OTA-WKM-C-0365-Tower | OTA-WKM-C0365 | OTA-WKM-C0365-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-12 | CA - E/W Attachmetn plates rusty and metal loss
10046087 | OTA-WKM-C-0365-Tower | OTA-WKM-C0365 | OTA-WKM-C0365-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-12 | CA - E/W Attachmetn plates rusty and metal loss
10046087 | OTA-WKM-C-0365-Tower | OTA-WKM-C0365 | OTA-WKM-C0365-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-12 | CA - E/W Attachmetn plates rusty and metal loss
10046091 | OTA-WKM-C-0365-Earthwire HW Set | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:00
10046091 | OTA-WKM-C-0365-Earthwire HW Set | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:00
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
12054908 | OTA-WKM-C-0365-Tower Foundation | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:50
13004435 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 | 2014 | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:51
13004435 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 | 2014 | INSE_SUSP COLD END COND | Susp Cold End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-26 15:51
13004435 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 | 2014 | INSE_SUSP HOT END COND | Susp Hot End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-26 15:51
13004435 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 | 2014 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-26 15:51
13004435 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 | 2014 | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-03 | Replaced Insulators Y Tongues Y Ball Socket Clevis clamps
13004436 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 | 2016 | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-07-26 15:54
13004436 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 | 2016 | INSE_SUSP COLD END COND | Susp Cold End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-26 15:54
13004436 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 | 2016 | INSE_SUSP HOT END COND | Susp Hot End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-26 15:54
13004436 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 | 2016 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-26 15:54
13004436 | OTA-WKM-C-0365-Insulator Set-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 | 2016 | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-30 | SR100194-Replaced insulators for all 3 phases including hot and cold hardware and armour rods - OHW-OTA-2
13040098 | OTA-WKM-C-0365-Earthwire Attachment | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-18 08:00 | Updating to 4 Readings
13040098 | OTA-WKM-C-0365-Earthwire Attachment | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-26 15:55
13040098 | OTA-WKM-C-0365-Earthwire Attachment | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-26 15:55
13040098 | OTA-WKM-C-0365-Earthwire Attachment | OTA-WKM-C0365 | OTA-WKM-C0365-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-18 08:00 | Updating to 4 Readings
13073657 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:57
13073657 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:57
13073657 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:57
13073657 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0365 | OTA-WKM-C0365-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:57
13073658 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:59
13073658 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:59
13073658 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:59
13073658 | OTA-WKM-C-0365-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0365 | OTA-WKM-C0365-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 15:59
10046899 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-2 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-26 16:01
10046899 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-2 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-20 | 1965 | COSE_DAMPER COND | Damper Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:01
10046899 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-2 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-04-12 | Routine CA
10046899 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-2 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:01
10046900 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-1 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-26 16:01
10046900 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-1 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-10 | 1965 | COSE_DAMPER COND | Damper Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:01
10046900 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-1 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2011-04-12 | 2xERD & 4xSAD dead-end joint
10046900 | OTA-WKM-C-0365-0366-Conductor-OHW-OTA-1 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:01
10046901 | OTA-WKM-C-0365-0366-Earthwire-A0 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:12
10046901 | OTA-WKM-C-0365-0366-Earthwire-A0 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 16:12
10046901 | OTA-WKM-C-0365-0366-Earthwire-A0 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-09-17 | CA
10046901 | OTA-WKM-C-0365-0366-Earthwire-A0 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-09-17 | CA
13329849 | OTA-WKM-C-0365-0366-Earthwire-C0 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 | CA copied from EW A0 Feb/2026
13329849 | OTA-WKM-C-0365-0366-Earthwire-C0 | OTA-WKM-C0365-0366 | OTA-WKM-C0365-0366-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-26 | CA copied from EW A0 Feb/2026
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Crossarm Jumper atachment steel and bolts rusty
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Crossarm Jumper atachment steel and bolts rusty
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Crossarm Jumper atachment steel and bolts rusty
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Crossarm Jumper atachment steel and bolts rusty
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Crossarm Jumper atachment steel and bolts rusty
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-05-01 09:02
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-06-28 | SR100194TWR-Replaced RC tower steel 179 x 2 180 x 2 188 x 2
10046092 | OTA-WKM-C-0366-Tower | OTA-WKM-C0366 | OTA-WKM-C0366-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Crossarm Jumper atachment steel and bolts rusty
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046094 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 1965 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:00
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 10:55
10046095 | OTA-WKM-C-0366-Insulator Set-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 1965 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 10:55
10046096 | OTA-WKM-C-0366-Earthwire HW Set | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA
10046096 | OTA-WKM-C-0366-Earthwire HW Set | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:15
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
12054909 | OTA-WKM-C-0366-Tower Foundation | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 12:04
13040099 | OTA-WKM-C-0366-Earthwire Attachment | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-09-18 08:00 | Updating to 4 Readings
13040099 | OTA-WKM-C-0366-Earthwire Attachment | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 11:05
13040099 | OTA-WKM-C-0366-Earthwire Attachment | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:05
13040099 | OTA-WKM-C-0366-Earthwire Attachment | OTA-WKM-C0366 | OTA-WKM-C0366-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-09-18 08:00 | Updating to 4 Readings
13286384 | OTA-WKM-C-0366-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Att Pt Project
13286384 | OTA-WKM-C-0366-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Att Pt Project
13286384 | OTA-WKM-C-0366-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0366 | OTA-WKM-C0366-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Att Pt Project
13286385 | OTA-WKM-C-0366-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-05 | Replaced during RSA2 24-25 Att Pt Project
13286385 | OTA-WKM-C-0366-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-05 | Replaced during RSA2 24-25 Att Pt Project
13286385 | OTA-WKM-C-0366-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-05 | Replaced during RSA2 24-25 Att Pt Project
13286385 | OTA-WKM-C-0366-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0366 | OTA-WKM-C0366-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-05 | Replaced during RSA2 24-25 Att Pt Project
10046902 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-2 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046902 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-2 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046902 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-2 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1999-10-15 | <Not Specified>
10046902 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-2 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046902 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-2 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-20 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046903 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-1 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046903 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-1 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046903 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-1 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Red Phase ERD inside FWD
10046903 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-1 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - Red Phase ERD inside FWD
10046903 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-1 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046903 | OTA-WKM-C-0366-0367-Conductor-OHW-OTA-1 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-10 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:19
10046904 | OTA-WKM-C-0366-0367-Earthwire-A0 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-00 |  | EASE_DAMPER COND | Damper Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2002-12-06 | <Not Specified>
10046904 | OTA-WKM-C-0366-0367-Earthwire-A0 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:22 | Surface pitting
10046904 | OTA-WKM-C-0366-0367-Earthwire-A0 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-09-17 | CA
13329850 | OTA-WKM-C-0366-0367-Earthwire-C0 | OTA-WKM-C0366-0367 | OTA-WKM-C0366-0367-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 | Surface pitting. CA copied from EW A0 Feb/2026
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-09-26 12:31
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-06-27 | SR100194TWR-Replaced steel 112 on C-D and D-A faces 129 on C-D and D-A faces
10046097 | OTA-WKM-C-0367-Tower | OTA-WKM-C0367 | OTA-WKM-C0367-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12054910 | OTA-WKM-C-0367-Tower Foundation | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 10:41
12058827 | OTA-WKM-C-0367-Earthwire HW Set | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:50 | Wrong overlay
12058827 | OTA-WKM-C-0367-Earthwire HW Set | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 11:50
13040100 | OTA-WKM-C-0367-Earthwire Attachment | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-15 08:00 | Updating to 4 Readings
13040100 | OTA-WKM-C-0367-Earthwire Attachment | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 11:42
13040100 | OTA-WKM-C-0367-Earthwire Attachment | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 11:42
13040100 | OTA-WKM-C-0367-Earthwire Attachment | OTA-WKM-C0367 | OTA-WKM-C0367-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2019-08-15 08:00 | Updating to 4 Readings
13073661 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:45
13073661 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:45
13073661 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:45
13073661 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:45
13073662 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:46
13073662 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:46
13073662 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:46
13073662 | OTA-WKM-C-0367-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:46
13185485 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-13 11:34
13185485 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 11:34
13185485 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 11:34
13185485 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-1 | OTA-WKM-C0367 | OTA-WKM-C0367-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 11:34
13204567 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-13 11:41
13204567 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 11:41
13204567 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 11:41
13204567 | OTA-WKM-C-0367-Insulator Set-OHW-OTA-2 | OTA-WKM-C0367 | OTA-WKM-C0367-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 11:41
10046905 | OTA-WKM-C-0367-0368-Conductor-OHW-OTA-2 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:48
10046905 | OTA-WKM-C-0367-0368-Conductor-OHW-OTA-2 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:48
10046905 | OTA-WKM-C-0367-0368-Conductor-OHW-OTA-2 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:48 | Surface pitting on ring
10046906 | OTA-WKM-C-0367-0368-Conductor-OHW-OTA-1 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 11:48
10046906 | OTA-WKM-C-0367-0368-Conductor-OHW-OTA-1 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:48
10046906 | OTA-WKM-C-0367-0368-Conductor-OHW-OTA-1 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-02 | RSA2 25-26 Subconductor Spacer Replacement Project
10046907 | OTA-WKM-C-0367-0368-Earthwire-A0 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:49
10046907 | OTA-WKM-C-0367-0368-Earthwire-A0 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 11:49 | Surface pitting
13329851 | OTA-WKM-C-0367-0368-Earthwire-C0 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 | CA copied from EW A0 Feb/2026
13329851 | OTA-WKM-C-0367-0368-Earthwire-C0 | OTA-WKM-C0367-0368 | OTA-WKM-C0367-0368-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 | Surface pitting. CA copied from EW A0 Feb/2026
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-09-26 10:28
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-06-27 | SR100194TWR-Replaced RC steel 200 x 3 and 206 x 1
10046102 | OTA-WKM-C-0368-Tower | OTA-WKM-C0368 | OTA-WKM-C0368-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-07-30 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 14:01
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:01
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 14:01
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:01
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 14:01
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:01
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 14:01
12054911 | OTA-WKM-C-0368-Tower Foundation | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:01
12058828 | OTA-WKM-C-0368-Earthwire HW Set | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:51
12058828 | OTA-WKM-C-0368-Earthwire HW Set | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:51
13040101 | OTA-WKM-C-0368-Earthwire Attachment | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 | Replaced
13040101 | OTA-WKM-C-0368-Earthwire Attachment | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:36 | Been replaced since last inspection
13040101 | OTA-WKM-C-0368-Earthwire Attachment | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:36 | Been replaced since last inspection
13040101 | OTA-WKM-C-0368-Earthwire Attachment | OTA-WKM-C0368 | OTA-WKM-C0368-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 | Replaced
13073663 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50 | Significant corrosion
13073663 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50
13073663 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50 | Significant corrosion
13073663 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50 | Significant corrosion
13073664 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50 | Significant corrosion
13073664 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50
13073664 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50 | Significant corrosion
13073664 | OTA-WKM-C-0368-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:50 | Significant corrosion
13185486 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 14:37
13185486 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:37
13185486 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:37
13185486 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-1 | OTA-WKM-C0368 | OTA-WKM-C0368-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:37
13185487 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 14:37
13185487 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:37
13185487 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:37
13185487 | OTA-WKM-C-0368-Insulator Set-OHW-OTA-2 | OTA-WKM-C0368 | OTA-WKM-C0368-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 14:37
10046908 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-2 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 14:06
10046908 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-2 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:06
10046908 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-2 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-03 | Routine CA
10046908 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-2 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-03 | Routine CA
10046909 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-1 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 14:05
10046909 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-1 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:05
10046909 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-1 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-03 | Routine CA
10046909 | OTA-WKM-C-0368-0369-Conductor-OHW-OTA-1 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-03 | Routine CA
10046910 | OTA-WKM-C-0368-0369-Earthwire-A0 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-00 |  | EASE_DAMPER COND | Damper Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:54 | Drooping both CCT BWD side
10046910 | OTA-WKM-C-0368-0369-Earthwire-A0 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 14:54
13329852 | OTA-WKM-C-0368-0369-Earthwire-C0 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-00 |  | EASE_DAMPER COND | Damper Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | Drooping both CCT BWD side. CA copied from EW A0 Feb/2026
13329852 | OTA-WKM-C-0368-0369-Earthwire-C0 | OTA-WKM-C0368-0369 | OTA-WKM-C0368-0369-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | CA copied from EW A0 Feb/2026
10046107 | OTA-WKM-C-0369-Tower | OTA-WKM-C0369 | OTA-WKM-C0369-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-03 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046107 | OTA-WKM-C-0369-Tower | OTA-WKM-C0369 | OTA-WKM-C0369-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-03 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046107 | OTA-WKM-C-0369-Tower | OTA-WKM-C0369 | OTA-WKM-C0369-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-03 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046107 | OTA-WKM-C-0369-Tower | OTA-WKM-C0369 | OTA-WKM-C0369-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-03 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046107 | OTA-WKM-C-0369-Tower | OTA-WKM-C0369 | OTA-WKM-C0369-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-03 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046107 | OTA-WKM-C-0369-Tower | OTA-WKM-C0369 | OTA-WKM-C0369-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-09-08 | Tower refurbishment up to MAD area
10046107 | OTA-WKM-C-0369-Tower | OTA-WKM-C0369 | OTA-WKM-C0369-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-03 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12054912 | OTA-WKM-C-0369-Tower Foundation | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 09:58
12058829 | OTA-WKM-C-0369-Earthwire HW Set | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:15 | Surface pitting wrong overlay
12058829 | OTA-WKM-C-0369-Earthwire HW Set | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 12:15
13004437 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 | 2014 | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 12:01
13004437 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 | 2014 | INSE_SUSP COLD END COND | Susp Cold End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:01
13004437 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 | 2014 | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:01
13004437 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 | 2014 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:01
13004437 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 | 2014 | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-04 | All 3 phases now new. Replaced Glass Insulators Y Ball Clevis Socket Tongues Shackles
13004438 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 | 2016 | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 12:01
13004438 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 | 2016 | INSE_SUSP COLD END COND | Susp Cold End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:01
13004438 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 | 2016 | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:01
13004438 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 | 2016 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:01
13004438 | OTA-WKM-C-0369-Insulator Set-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 | 2016 | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-30 | SR100194-Replaced insulators for all 3 phases including hot and cold hardware and armour rods - OHW-OTA-2
13073666 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:13 | Wind wear
13073666 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:13 | Significant corrosion
13073666 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:13 | Significant corrosion
13073666 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0369 | OTA-WKM-C0369-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:13 | Significant corrosion
13247616 | OTA-WKM-C-0369-Earthwire Attachment | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-02-23 | WO# 2004088
13247616 | OTA-WKM-C-0369-Earthwire Attachment | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:04
13247616 | OTA-WKM-C-0369-Earthwire Attachment | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 12:04
13247616 | OTA-WKM-C-0369-Earthwire Attachment | OTA-WKM-C0369 | OTA-WKM-C0369-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-02-23 | WO# 2004088
13286386 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 Attach Point Replacement 24-25 project
13286386 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 Attach Point Replacement 24-25 project
13286386 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 Attach Point Replacement 24-25 project
13286386 | OTA-WKM-C-0369-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0369 | OTA-WKM-C0369-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 Attach Point Replacement 24-25 project
10046911 | OTA-WKM-C-0369-0370-Conductor-OHW-OTA-2 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 12:16
10046911 | OTA-WKM-C-0369-0370-Conductor-OHW-OTA-2 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:16
10046911 | OTA-WKM-C-0369-0370-Conductor-OHW-OTA-2 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:16 | Surface pitting on ring
10046912 | OTA-WKM-C-0369-0370-Conductor-OHW-OTA-1 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 12:16
10046912 | OTA-WKM-C-0369-0370-Conductor-OHW-OTA-1 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:16
10046912 | OTA-WKM-C-0369-0370-Conductor-OHW-OTA-1 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-02 | RSA2 25-26 Subconductor Spacer Replacement Project
10046913 | OTA-WKM-C-0369-0370-Earthwire-A0 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:17
10046913 | OTA-WKM-C-0369-0370-Earthwire-A0 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 12:17 | Surface pitting
10046913 | OTA-WKM-C-0369-0370-Earthwire-A0 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
13329853 | OTA-WKM-C-0369-0370-Earthwire-C0 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 | CA copied from EW A0 Feb/2026
13329853 | OTA-WKM-C-0369-0370-Earthwire-C0 | OTA-WKM-C0369-0370 | OTA-WKM-C0369-0370-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 | Surface pitting. CA copied from EW A0 Feb/2026
10046112 | OTA-WKM-C-0370-Tower | OTA-WKM-C0370 | OTA-WKM-C0370-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046112 | OTA-WKM-C-0370-Tower | OTA-WKM-C0370 | OTA-WKM-C0370-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046112 | OTA-WKM-C-0370-Tower | OTA-WKM-C0370 | OTA-WKM-C0370-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046112 | OTA-WKM-C-0370-Tower | OTA-WKM-C0370 | OTA-WKM-C0370-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046112 | OTA-WKM-C-0370-Tower | OTA-WKM-C0370 | OTA-WKM-C0370-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046112 | OTA-WKM-C-0370-Tower | OTA-WKM-C0370 | OTA-WKM-C0370-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-09-09 | Tower refurbishment including MAD area CCT1
10046112 | OTA-WKM-C-0370-Tower | OTA-WKM-C0370 | OTA-WKM-C0370-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 13:20
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-13 13:20
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 13:20
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-13 13:20
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 13:20
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-13 13:20
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 13:20
12054913 | OTA-WKM-C-0370-Tower Foundation | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-13 13:20
12058830 | OTA-WKM-C-0370-Earthwire HW Set | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:43 | Surface pittingwrong overlay
12058830 | OTA-WKM-C-0370-Earthwire HW Set | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-13 13:43
13040103 | OTA-WKM-C-0370-Earthwire Attachment | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-17 08:00 | Updating to 4 Readings
13040103 | OTA-WKM-C-0370-Earthwire Attachment | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 13:39
13040103 | OTA-WKM-C-0370-Earthwire Attachment | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-13 13:39
13040103 | OTA-WKM-C-0370-Earthwire Attachment | OTA-WKM-C0370 | OTA-WKM-C0370-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-17 08:00 | Updating to 4 Readings
13073667 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41 | Wind wear
13073667 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41
13073667 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41
13073667 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41
13073668 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41 | Wind wear
13073668 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41
13073668 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41
13073668 | OTA-WKM-C-0370-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:41
13285423 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | Replaced during 24-25 Ins replacement project
13285423 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | Replaced during 24-25 Ins replacement project
13285423 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | Replaced during 24-25 Ins replacement project
13285423 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-1 | OTA-WKM-C0370 | OTA-WKM-C0370-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | Replaced during 24-25 Ins replacement project
13285424 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
13285424 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
13285424 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
13285424 | OTA-WKM-C-0370-Insulator Set-OHW-OTA-2 | OTA-WKM-C0370 | OTA-WKM-C0370-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
10046914 | OTA-WKM-C-0370-0371-Conductor-OHW-OTA-2 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 13:47
10046914 | OTA-WKM-C-0370-0371-Conductor-OHW-OTA-2 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:47
10046914 | OTA-WKM-C-0370-0371-Conductor-OHW-OTA-2 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-02 | RSA2 25-26 Subconductor Spacer Replacement Project
10046915 | OTA-WKM-C-0370-0371-Conductor-OHW-OTA-1 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-13 13:45
10046915 | OTA-WKM-C-0370-0371-Conductor-OHW-OTA-1 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:45
10046915 | OTA-WKM-C-0370-0371-Conductor-OHW-OTA-1 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:45
10046916 | OTA-WKM-C-0370-0371-Earthwire-A0 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:51
10046916 | OTA-WKM-C-0370-0371-Earthwire-A0 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 13:51
13329854 | OTA-WKM-C-0370-0371-Earthwire-C0 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 | CA copied from EW A0 Feb/2026
13329854 | OTA-WKM-C-0370-0371-Earthwire-C0 | OTA-WKM-C0370-0371 | OTA-WKM-C0370-0371-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-13 | CA copied from EW A0 Feb/2026
10046117 | OTA-WKM-C-0371-Tower | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046117 | OTA-WKM-C-0371-Tower | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046117 | OTA-WKM-C-0371-Tower | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046117 | OTA-WKM-C-0371-Tower | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046117 | OTA-WKM-C-0371-Tower | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046117 | OTA-WKM-C-0371-Tower | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-08-03 | Tower refurbishment up to MAD area
10046117 | OTA-WKM-C-0371-Tower | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
10294520 | OTA-WKM-C-0371-Tower Foundation | OTA-WKM-C0371 | OTA-WKM-C0371-00 | 2009 | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:25
12058831 | OTA-WKM-C-0371-Earthwire HW Set | OTA-WKM-C0371 | OTA-WKM-C0371-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:03 | Wrong overlay
12058831 | OTA-WKM-C-0371-Earthwire HW Set | OTA-WKM-C0371 | OTA-WKM-C0371-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-14 09:03
13040104 | OTA-WKM-C-0371-Earthwire Attachment | OTA-WKM-C0371 | OTA-WKM-C0371-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-09-17 08:00 | Updating to 4 Readings
13040104 | OTA-WKM-C-0371-Earthwire Attachment | OTA-WKM-C0371 | OTA-WKM-C0371-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:04
13040104 | OTA-WKM-C-0371-Earthwire Attachment | OTA-WKM-C0371 | OTA-WKM-C0371-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:04 | Wind wear
13040104 | OTA-WKM-C-0371-Earthwire Attachment | OTA-WKM-C0371 | OTA-WKM-C0371-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-09-17 08:00 | Updating to 4 Readings
13073669 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:01
13073669 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:01
13073669 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:01
13073669 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:01
13073670 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:05
13073670 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:05
13073670 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:05
13073670 | OTA-WKM-C-0371-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:05
13185488 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:27
13185488 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:27
13185488 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:27
13185488 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-2 | OTA-WKM-C0371 | OTA-WKM-C0371-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 08:27
13285425 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2024-08-05 | Replaced during 24-25 Ins replacement project
13285425 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-05 | Replaced during 24-25 Ins replacement project
13285425 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-05 | Replaced during 24-25 Ins replacement project
13285425 | OTA-WKM-C-0371-Insulator Set-OHW-OTA-1 | OTA-WKM-C0371 | OTA-WKM-C0371-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-05 | Replaced during 24-25 Ins replacement project
10046917 | OTA-WKM-C-0371-0372-Conductor-OHW-OTA-2 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-14 08:53
10046917 | OTA-WKM-C-0371-0372-Conductor-OHW-OTA-2 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:53
10046917 | OTA-WKM-C-0371-0372-Conductor-OHW-OTA-2 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:53
10046918 | OTA-WKM-C-0371-0372-Conductor-OHW-OTA-1 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-14 08:53
10046918 | OTA-WKM-C-0371-0372-Conductor-OHW-OTA-1 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:53
10046918 | OTA-WKM-C-0371-0372-Conductor-OHW-OTA-1 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:53
10046919 | OTA-WKM-C-0371-0372-Earthwire-A0 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:06
10046919 | OTA-WKM-C-0371-0372-Earthwire-A0 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:06 | Surface pitting
13329855 | OTA-WKM-C-0371-0372-Earthwire-C0 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 | CA copied from EW A0 Feb/2026
13329855 | OTA-WKM-C-0371-0372-Earthwire-C0 | OTA-WKM-C0371-0372 | OTA-WKM-C0371-0372-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 | Surface pitting. CA copied from EW A0 Feb/2026
10046122 | OTA-WKM-C-0372-Tower | OTA-WKM-C0372 | OTA-WKM-C0372-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-04 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046122 | OTA-WKM-C-0372-Tower | OTA-WKM-C0372 | OTA-WKM-C0372-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-04 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046122 | OTA-WKM-C-0372-Tower | OTA-WKM-C0372 | OTA-WKM-C0372-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-04 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046122 | OTA-WKM-C-0372-Tower | OTA-WKM-C0372 | OTA-WKM-C0372-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-04 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046122 | OTA-WKM-C-0372-Tower | OTA-WKM-C0372 | OTA-WKM-C0372-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-04 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046122 | OTA-WKM-C-0372-Tower | OTA-WKM-C0372 | OTA-WKM-C0372-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-07-25 | Tower refurbishment to MAD area
10046122 | OTA-WKM-C-0372-Tower | OTA-WKM-C0372 | OTA-WKM-C0372-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-04 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:37
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 07:37
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:37
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 07:37
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:37
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 07:37
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:37
12054914 | OTA-WKM-C-0372-Tower Foundation | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 07:37
12058832 | OTA-WKM-C-0372-Earthwire HW Set | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:11 | Wrong overlay
12058832 | OTA-WKM-C-0372-Earthwire HW Set | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-14 08:11
13040105 | OTA-WKM-C-0372-Earthwire Attachment | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13040105 | OTA-WKM-C-0372-Earthwire Attachment | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13040105 | OTA-WKM-C-0372-Earthwire Attachment | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13040105 | OTA-WKM-C-0372-Earthwire Attachment | OTA-WKM-C0372 | OTA-WKM-C0372-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13073671 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:07
13073671 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:07
13073671 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:07
13073671 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:07
13073672 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:08
13073672 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:08
13073672 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:08
13073672 | OTA-WKM-C-0372-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:08
13185489 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 | 2018 | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 07:39
13185489 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 | 2018 | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:39
13185489 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 | 2018 | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:39
13185489 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-1 | OTA-WKM-C0372 | OTA-WKM-C0372-10 | 2018 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:39
13185490 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 07:40
13185490 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:40
13185490 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:40
13185490 | OTA-WKM-C-0372-Insulator Set-OHW-OTA-2 | OTA-WKM-C0372 | OTA-WKM-C0372-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 07:40
10046920 | OTA-WKM-C-0372-0373-Conductor-OHW-OTA-2 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-14 07:43
10046920 | OTA-WKM-C-0372-0373-Conductor-OHW-OTA-2 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 07:43
10046920 | OTA-WKM-C-0372-0373-Conductor-OHW-OTA-2 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 07:43
10046921 | OTA-WKM-C-0372-0373-Conductor-OHW-OTA-1 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-14 07:43
10046921 | OTA-WKM-C-0372-0373-Conductor-OHW-OTA-1 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 07:43
10046921 | OTA-WKM-C-0372-0373-Conductor-OHW-OTA-1 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 07:43
10046922 | OTA-WKM-C-0372-0373-Earthwire-A0 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:07
10046922 | OTA-WKM-C-0372-0373-Earthwire-A0 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 08:07
13329856 | OTA-WKM-C-0372-0373-Earthwire-C0 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 | CA copied from EW A0 Feb/2026
13329856 | OTA-WKM-C-0372-0373-Earthwire-C0 | OTA-WKM-C0372-0373 | OTA-WKM-C0372-0373-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 | CA copied from EW A0 Feb/2026
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-07-11 | Tower refurbishment to MAD area
10046127 | OTA-WKM-C-0373-Tower | OTA-WKM-C0373 | OTA-WKM-C0373-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-07
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12054915 | OTA-WKM-C-0373-Tower Foundation | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 08:44
12058833 | OTA-WKM-C-0373-Earthwire HW Set | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:18 | Wrong overlay
12058833 | OTA-WKM-C-0373-Earthwire HW Set | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-14 10:18
13040106 | OTA-WKM-C-0373-Earthwire Attachment | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13040106 | OTA-WKM-C-0373-Earthwire Attachment | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13040106 | OTA-WKM-C-0373-Earthwire Attachment | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13040106 | OTA-WKM-C-0373-Earthwire Attachment | OTA-WKM-C0373 | OTA-WKM-C0373-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-20 | Replaced EW Att point during Routine maintenance Work
13073673 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:13
13073673 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:13
13073673 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:13
13073673 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:13
13073674 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:18
13073674 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:18
13073674 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:18
13073674 | OTA-WKM-C-0373-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:18
13185491 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 10:10
13185491 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 10:10
13185491 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 10:10
13185491 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-1 | OTA-WKM-C0373 | OTA-WKM-C0373-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-14 10:10
13218506 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 09:36
13218506 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 09:36
13218506 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 09:36
13218506 | OTA-WKM-C-0373-Insulator Set-OHW-OTA-2 | OTA-WKM-C0373 | OTA-WKM-C0373-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-14 09:36
10046923 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-2 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-14 09:43
10046923 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-2 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:43
10046923 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-2 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046923 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-2 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-20 | 1965 | COSE_REPAIR ROD COND | Repair Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046923 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-2 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:43
10046924 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-1 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-14 09:42
10046924 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-1 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:42
10046924 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-1 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2014-02-27 | Fit extended midspan joint x1
10046924 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-1 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-10 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046924 | OTA-WKM-C-0373-0374-Conductor-OHW-OTA-1 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 09:42
10046925 | OTA-WKM-C-0373-0374-Earthwire-A0 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:20
10046925 | OTA-WKM-C-0373-0374-Earthwire-A0 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 10:20 | Surface pitting
13329857 | OTA-WKM-C-0373-0374-Earthwire-C0 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 | CA copied from EW A0 Feb/2026
13329857 | OTA-WKM-C-0373-0374-Earthwire-C0 | OTA-WKM-C0373-0374 | OTA-WKM-C0373-0374-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-14 | Surface pitting. CA copied from EW A0 Feb/2026
10046132 | OTA-WKM-C-0374-Tower | OTA-WKM-C0374 | OTA-WKM-C0374-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046132 | OTA-WKM-C-0374-Tower | OTA-WKM-C0374 | OTA-WKM-C0374-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046132 | OTA-WKM-C-0374-Tower | OTA-WKM-C0374 | OTA-WKM-C0374-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046132 | OTA-WKM-C-0374-Tower | OTA-WKM-C0374 | OTA-WKM-C0374-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046132 | OTA-WKM-C-0374-Tower | OTA-WKM-C0374 | OTA-WKM-C0374-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10046132 | OTA-WKM-C-0374-Tower | OTA-WKM-C0374 | OTA-WKM-C0374-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-09-09 | Tower refurbishment up to MAD area
10046132 | OTA-WKM-C-0374-Tower | OTA-WKM-C0374 | OTA-WKM-C0374-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-19 | CA - E/W attachment plates rusty
10332808 | OTA-WKM-C-0374-Earthwire HW Set | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:15
10332808 | OTA-WKM-C-0374-Earthwire HW Set | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-08-03 17:15
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
12054916 | OTA-WKM-C-0374-Tower Foundation | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:04
13004439 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2014 | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:05
13004439 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2014 | INSE_SUSP COLD END COND | Susp Cold End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-08-03 17:05
13004439 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2014 | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-08-03 17:05
13004439 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2014 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-08-03 17:05
13004439 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2014 | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-03 | Replaced Yoke Plate Socket Clevis clamps Y Tongues Y Ball Clevis
13004440 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-03 17:07
13004440 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-08-03 17:07
13004440 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-08-03 17:07
13004440 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-08-03 17:07
13004440 | OTA-WKM-C-0374-Insulator Set-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-30 | SR100194-Replaced insulators for all 3 phases including hot and cold hardware and armour rods - OHW-OTA-2
13040107 | OTA-WKM-C-0374-Earthwire Attachment | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-16 08:00 | Updating to 4 Readings
13040107 | OTA-WKM-C-0374-Earthwire Attachment | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-08-03 17:08
13040107 | OTA-WKM-C-0374-Earthwire Attachment | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-08-03 17:08
13040107 | OTA-WKM-C-0374-Earthwire Attachment | OTA-WKM-C0374 | OTA-WKM-C0374-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-16 08:00 | Updating to 4 Readings
13073676 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:14
13073676 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:14
13073676 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:14
13073676 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0374 | OTA-WKM-C0374-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:14
13300453 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-30 17:06
13300453 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-30 17:06
13300453 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-30 17:06
13300453 | OTA-WKM-C-0374-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0374 | OTA-WKM-C0374-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-30 17:06
10046926 | OTA-WKM-C-0374-0375-Conductor-OHW-OTA-2 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-08-03 17:16
10046926 | OTA-WKM-C-0374-0375-Conductor-OHW-OTA-2 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-20 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-08-03 17:16
10046926 | OTA-WKM-C-0374-0375-Conductor-OHW-OTA-2 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:16
10046927 | OTA-WKM-C-0374-0375-Conductor-OHW-OTA-1 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-08-03 17:16
10046927 | OTA-WKM-C-0374-0375-Conductor-OHW-OTA-1 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-10 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-08-03 17:16
10046927 | OTA-WKM-C-0374-0375-Conductor-OHW-OTA-1 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:16
10046928 | OTA-WKM-C-0374-0375-Earthwire-A0 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:17 | Deformed damper
10046928 | OTA-WKM-C-0374-0375-Earthwire-A0 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 17:17
10046928 | OTA-WKM-C-0374-0375-Earthwire-A0 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-09-15 | CA
13329858 | OTA-WKM-C-0374-0375-Earthwire-C0 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 | Deformed damper. CA copied from EW A0 Feb/2026
13329858 | OTA-WKM-C-0374-0375-Earthwire-C0 | OTA-WKM-C0374-0375 | OTA-WKM-C0374-0375-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-08-03 | CA copied from EW A0 Feb/2026
10046137 | OTA-WKM-C-0375-Tower | OTA-WKM-C0375 | OTA-WKM-C0375-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046137 | OTA-WKM-C-0375-Tower | OTA-WKM-C0375 | OTA-WKM-C0375-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046137 | OTA-WKM-C-0375-Tower | OTA-WKM-C0375 | OTA-WKM-C0375-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046137 | OTA-WKM-C-0375-Tower | OTA-WKM-C0375 | OTA-WKM-C0375-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046137 | OTA-WKM-C-0375-Tower | OTA-WKM-C0375 | OTA-WKM-C0375-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046137 | OTA-WKM-C-0375-Tower | OTA-WKM-C0375 | OTA-WKM-C0375-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-20 | Tower refurbishment up to MAD area
10046137 | OTA-WKM-C-0375-Tower | OTA-WKM-C0375 | OTA-WKM-C0375-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12054917 | OTA-WKM-C-0375-Tower Foundation | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:15
12058834 | OTA-WKM-C-0375-Earthwire HW Set | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:10 | Wrong overlay
12058834 | OTA-WKM-C-0375-Earthwire HW Set | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:10
13040108 | OTA-WKM-C-0375-Earthwire Attachment | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-26 12:21 | New attachment point
13040108 | OTA-WKM-C-0375-Earthwire Attachment | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-26 12:21 | Replaced the attachment point nuts and bolts
13040108 | OTA-WKM-C-0375-Earthwire Attachment | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-26 12:20 | Replaced the ew attachment point steel
13040108 | OTA-WKM-C-0375-Earthwire Attachment | OTA-WKM-C0375 | OTA-WKM-C0375-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-26 12:22 | New
13073677 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:02
13073677 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:02
13073677 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:02
13073677 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:02
13073678 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 14:52
13073678 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 14:52
13073678 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 14:52
13073678 | OTA-WKM-C-0375-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 14:52
13186194 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:18
13186194 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 12:18
13186194 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 12:18
13186194 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-1 | OTA-WKM-C0375 | OTA-WKM-C0375-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 12:18
13186195 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 12:19
13186195 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 12:19
13186195 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 12:19
13186195 | OTA-WKM-C-0375-Insulator Set-OHW-OTA-2 | OTA-WKM-C0375 | OTA-WKM-C0375-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 12:19
10046929 | OTA-WKM-C-0375-0376-Conductor-OHW-OTA-2 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-07 15:07
10046929 | OTA-WKM-C-0375-0376-Conductor-OHW-OTA-2 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:07
10046929 | OTA-WKM-C-0375-0376-Conductor-OHW-OTA-2 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:07
10046930 | OTA-WKM-C-0375-0376-Conductor-OHW-OTA-1 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-07 15:07
10046930 | OTA-WKM-C-0375-0376-Conductor-OHW-OTA-1 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:07
10046930 | OTA-WKM-C-0375-0376-Conductor-OHW-OTA-1 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:07
10046931 | OTA-WKM-C-0375-0376-Earthwire-A0 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:09
10046931 | OTA-WKM-C-0375-0376-Earthwire-A0 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:09 | Surface pitting
13329859 | OTA-WKM-C-0375-0376-Earthwire-C0 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 | CA copied from EW A0 Feb/2026
13329859 | OTA-WKM-C-0375-0376-Earthwire-C0 | OTA-WKM-C0375-0376 | OTA-WKM-C0375-0376-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 | Surface pitting. CA copied from EW A0 Feb/2026
10046142 | OTA-WKM-C-0376-Tower | OTA-WKM-C0376 | OTA-WKM-C0376-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046142 | OTA-WKM-C-0376-Tower | OTA-WKM-C0376 | OTA-WKM-C0376-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046142 | OTA-WKM-C-0376-Tower | OTA-WKM-C0376 | OTA-WKM-C0376-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046142 | OTA-WKM-C-0376-Tower | OTA-WKM-C0376 | OTA-WKM-C0376-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046142 | OTA-WKM-C-0376-Tower | OTA-WKM-C0376 | OTA-WKM-C0376-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046142 | OTA-WKM-C-0376-Tower | OTA-WKM-C0376 | OTA-WKM-C0376-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-27 | Tower refurbishment including MAD area CCT1 & CCT2
10046142 | OTA-WKM-C-0376-Tower | OTA-WKM-C0376 | OTA-WKM-C0376-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10307875 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 | 2010 | INSE_ARMOUR ROD COND | Armour Rod Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-08 13:59
10307875 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 | 2010 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:59
10307875 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 | 2010 | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-08 13:59
10307875 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 | 2010 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 13:59
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12054918 | OTA-WKM-C-0376-Tower Foundation | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:27
12058835 | OTA-WKM-C-0376-Earthwire HW Set | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
12058835 | OTA-WKM-C-0376-Earthwire HW Set | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-08 14:14
13040109 | OTA-WKM-C-0376-Earthwire Attachment | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-15 08:00 | Updating to 4 Readings
13040109 | OTA-WKM-C-0376-Earthwire Attachment | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-02-08 14:14
13040109 | OTA-WKM-C-0376-Earthwire Attachment | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
13040109 | OTA-WKM-C-0376-Earthwire Attachment | OTA-WKM-C0376 | OTA-WKM-C0376-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-09-15 08:00 | Updating to 4 Readings
13073679 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13073679 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13073679 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13073679 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0376 | OTA-WKM-C0376-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13073680 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13073680 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13073680 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13073680 | OTA-WKM-C-0376-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:57
13285426 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
13285426 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
13285426 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
13285426 | OTA-WKM-C-0376-Insulator Set-OHW-OTA-2 | OTA-WKM-C0376 | OTA-WKM-C0376-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
10046932 | OTA-WKM-C-0376-0377-Conductor-OHW-OTA-2 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
10046932 | OTA-WKM-C-0376-0377-Conductor-OHW-OTA-2 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
10046932 | OTA-WKM-C-0376-0377-Conductor-OHW-OTA-2 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
10046933 | OTA-WKM-C-0376-0377-Conductor-OHW-OTA-1 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
10046933 | OTA-WKM-C-0376-0377-Conductor-OHW-OTA-1 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
10046933 | OTA-WKM-C-0376-0377-Conductor-OHW-OTA-1 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:14
10046934 | OTA-WKM-C-0376-0377-Earthwire-A0 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:15
10046934 | OTA-WKM-C-0376-0377-Earthwire-A0 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:15
13329860 | OTA-WKM-C-0376-0377-Earthwire-C0 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 | CA copied from EW A0 Feb/2026
13329860 | OTA-WKM-C-0376-0377-Earthwire-C0 | OTA-WKM-C0376-0377 | OTA-WKM-C0376-0377-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 | CA copied from EW A0 Feb/2026
10046147 | OTA-WKM-C-0377-Tower | OTA-WKM-C0377 | OTA-WKM-C0377-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-05 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046147 | OTA-WKM-C-0377-Tower | OTA-WKM-C0377 | OTA-WKM-C0377-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-05 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046147 | OTA-WKM-C-0377-Tower | OTA-WKM-C0377 | OTA-WKM-C0377-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-05 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046147 | OTA-WKM-C-0377-Tower | OTA-WKM-C0377 | OTA-WKM-C0377-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-05 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046147 | OTA-WKM-C-0377-Tower | OTA-WKM-C0377 | OTA-WKM-C0377-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-05 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046147 | OTA-WKM-C-0377-Tower | OTA-WKM-C0377 | OTA-WKM-C0377-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-22 | Tower refurbishment up to MAD area
10046147 | OTA-WKM-C-0377-Tower | OTA-WKM-C0377 | OTA-WKM-C0377-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-05 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12054919 | OTA-WKM-C-0377-Tower Foundation | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:33
12058836 | OTA-WKM-C-0377-Earthwire HW Set | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:46 | Wrong overlay
12058836 | OTA-WKM-C-0377-Earthwire HW Set | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-08 13:46
13040110 | OTA-WKM-C-0377-Earthwire Attachment | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-10 | Replaced
13040110 | OTA-WKM-C-0377-Earthwire Attachment | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-08 13:45 | Been replaced
13040110 | OTA-WKM-C-0377-Earthwire Attachment | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-08 13:45 | Been replaced
13040110 | OTA-WKM-C-0377-Earthwire Attachment | OTA-WKM-C0377 | OTA-WKM-C0377-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2024-02-10 | Replaced
13073681 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:42 | Wind wear
13073681 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:42
13073681 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:42
13073681 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:42 | Significant corrosion
13073682 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:45
13073682 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:45
13073682 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:45
13073682 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:45
13186196 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:34
13186196 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 11:34
13186196 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 11:34
13186196 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 11:34
13186197 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:34
13186197 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 11:34
13186197 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 11:34
13186197 | OTA-WKM-C-0377-Insulator Set-OHW-OTA-2 | OTA-WKM-C0377 | OTA-WKM-C0377-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 11:34
13286387 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | RSA2 Attach Point Replacement 24-25
13286387 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | RSA2 Attach Point Replacement 24-25
13286387 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | RSA2 Attach Point Replacement 24-25
13286387 | OTA-WKM-C-0377-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0377 | OTA-WKM-C0377-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | RSA2 Attach Point Replacement 24-25
10046935 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-2 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 13:46
10046935 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-2 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:46
10046935 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-2 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046935 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-2 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:46
10046936 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-1 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 13:46
10046936 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-1 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:46
10046936 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-1 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-02 | Routine CA
10046936 | OTA-WKM-C-0377-0378-Conductor-OHW-OTA-1 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:46
10046937 | OTA-WKM-C-0377-0378-Earthwire-A0 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:47
10046937 | OTA-WKM-C-0377-0378-Earthwire-A0 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 13:47
10046937 | OTA-WKM-C-0377-0378-Earthwire-A0 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-09-14 | CA
13329861 | OTA-WKM-C-0377-0378-Earthwire-C0 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 | CA copied from EW A0 Feb/2026
13329861 | OTA-WKM-C-0377-0378-Earthwire-C0 | OTA-WKM-C0377-0378 | OTA-WKM-C0377-0378-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 | CA copied from EW A0 Feb/2026
10046152 | OTA-WKM-C-0378-Tower | OTA-WKM-C0378 | OTA-WKM-C0378-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046152 | OTA-WKM-C-0378-Tower | OTA-WKM-C0378 | OTA-WKM-C0378-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046152 | OTA-WKM-C-0378-Tower | OTA-WKM-C0378 | OTA-WKM-C0378-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046152 | OTA-WKM-C-0378-Tower | OTA-WKM-C0378 | OTA-WKM-C0378-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046152 | OTA-WKM-C-0378-Tower | OTA-WKM-C0378 | OTA-WKM-C0378-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046152 | OTA-WKM-C-0378-Tower | OTA-WKM-C0378 | OTA-WKM-C0378-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-27 | Tower refurbishment including MAD area CCT1 & CCT2
10046152 | OTA-WKM-C-0378-Tower | OTA-WKM-C0378 | OTA-WKM-C0378-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
12054920 | OTA-WKM-C-0378-Tower Foundation | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 11:39
13186198 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-07 15:35
13186198 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 15:35
13186198 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 15:35
13186198 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-07 15:35
13298789 | OTA-WKM-C-0378-Earthwire HW Set | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-09-18 | Replaced during routine maintenance work
13298789 | OTA-WKM-C-0378-Earthwire HW Set | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-09-10 | Replaced during routine maintenance work.
13298790 | OTA-WKM-C-0378-Earthwire Attachment | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-09-10 | Replaced during routine maintenance work
13298790 | OTA-WKM-C-0378-Earthwire Attachment | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-09-10 | Replaced during routine maintenance work
13298790 | OTA-WKM-C-0378-Earthwire Attachment | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-09-10 | Replaced during routine maintenance work
13298790 | OTA-WKM-C-0378-Earthwire Attachment | OTA-WKM-C0378 | OTA-WKM-C0378-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-09-10 | Replaced during routine maintenance work
13299645 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:47
13299645 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:46
13299645 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:46
13299645 | OTA-WKM-C-0378-Insulator Set-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:46
13300454 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:58
13300454 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:58
13300454 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:58
13300454 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0378 | OTA-WKM-C0378-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 14:58
13300455 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-12 07:29
13300455 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-12 07:29
13300455 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-12 07:29
13300455 | OTA-WKM-C-0378-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0378 | OTA-WKM-C0378-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-12 07:29
10046938 | OTA-WKM-C-0378-0379-Conductor-OHW-OTA-2 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 14:34
10046938 | OTA-WKM-C-0378-0379-Conductor-OHW-OTA-2 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:34
10046938 | OTA-WKM-C-0378-0379-Conductor-OHW-OTA-2 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:34
10046939 | OTA-WKM-C-0378-0379-Conductor-OHW-OTA-1 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-08 14:33
10046939 | OTA-WKM-C-0378-0379-Conductor-OHW-OTA-1 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:33
10046939 | OTA-WKM-C-0378-0379-Conductor-OHW-OTA-1 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | Routine CA
10046939 | OTA-WKM-C-0378-0379-Conductor-OHW-OTA-1 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-08 14:33
10046940 | OTA-WKM-C-0378-0379-Earthwire-A0 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:38
10046940 | OTA-WKM-C-0378-0379-Earthwire-A0 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 15:38 | Surface pitting
13329862 | OTA-WKM-C-0378-0379-Earthwire-C0 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 | CA copied from EW A0 Feb/2026
13329862 | OTA-WKM-C-0378-0379-Earthwire-C0 | OTA-WKM-C0378-0379 | OTA-WKM-C0378-0379-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-07 | Surface pitting. CA copied from EW A0 Feb/2026
10046157 | OTA-WKM-C-0379-Tower | OTA-WKM-C0379 | OTA-WKM-C0379-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046157 | OTA-WKM-C-0379-Tower | OTA-WKM-C0379 | OTA-WKM-C0379-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046157 | OTA-WKM-C-0379-Tower | OTA-WKM-C0379 | OTA-WKM-C0379-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046157 | OTA-WKM-C-0379-Tower | OTA-WKM-C0379 | OTA-WKM-C0379-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046157 | OTA-WKM-C-0379-Tower | OTA-WKM-C0379 | OTA-WKM-C0379-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
10046157 | OTA-WKM-C-0379-Tower | OTA-WKM-C0379 | OTA-WKM-C0379-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-22 | Tower refurbishment up to MAD area
10046157 | OTA-WKM-C-0379-Tower | OTA-WKM-C0379 | OTA-WKM-C0379-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12054921 | OTA-WKM-C-0379-Tower Foundation | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:58
12058837 | OTA-WKM-C-0379-Earthwire HW Set | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 15:34 | Wrong overlay
12058837 | OTA-WKM-C-0379-Earthwire HW Set | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-16 15:34
13040112 | OTA-WKM-C-0379-Earthwire Attachment | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-12-10 08:00 | Updating to 4 Readings
13040112 | OTA-WKM-C-0379-Earthwire Attachment | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-16 15:35
13040112 | OTA-WKM-C-0379-Earthwire Attachment | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-16 15:35
13040112 | OTA-WKM-C-0379-Earthwire Attachment | OTA-WKM-C0379 | OTA-WKM-C0379-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-12-10 08:00 | Updating to 4 Readings
13073686 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:37 | Wind wear
13073686 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:37 | Significant corrosion
13073686 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:37 | Significant corrosion
13073686 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:37 | Significant corrosion
13285427 | OTA-WKM-C-0379-Insulator Set-OHW-OTA-1 | OTA-WKM-C0379 | OTA-WKM-C0379-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Reins Project
13285427 | OTA-WKM-C-0379-Insulator Set-OHW-OTA-1 | OTA-WKM-C0379 | OTA-WKM-C0379-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Reins Project
13285427 | OTA-WKM-C-0379-Insulator Set-OHW-OTA-1 | OTA-WKM-C0379 | OTA-WKM-C0379-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Reins Project
13285428 | OTA-WKM-C-0379-Insulator Set-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285428 | OTA-WKM-C-0379-Insulator Set-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285428 | OTA-WKM-C-0379-Insulator Set-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285428 | OTA-WKM-C-0379-Insulator Set-OHW-OTA-2 | OTA-WKM-C0379 | OTA-WKM-C0379-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13286388 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0379 | OTA-WKM-C0379-10 | 2024 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Att Pt Project
13286388 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0379 | OTA-WKM-C0379-10 | 2024 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Att Pt Project
13286388 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0379 | OTA-WKM-C0379-10 | 2024 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Att Pt Project
13286388 | OTA-WKM-C-0379-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0379 | OTA-WKM-C0379-10 | 2024 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Att Pt Project
10046941 | OTA-WKM-C-0379-0380-Conductor-OHW-OTA-2 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-23 14:38
10046941 | OTA-WKM-C-0379-0380-Conductor-OHW-OTA-2 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:38
10046941 | OTA-WKM-C-0379-0380-Conductor-OHW-OTA-2 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:38
10046942 | OTA-WKM-C-0379-0380-Conductor-OHW-OTA-1 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-23 14:38
10046942 | OTA-WKM-C-0379-0380-Conductor-OHW-OTA-1 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:38
10046942 | OTA-WKM-C-0379-0380-Conductor-OHW-OTA-1 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:38
10046943 | OTA-WKM-C-0379-0380-Earthwire-A0 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:40
10046943 | OTA-WKM-C-0379-0380-Earthwire-A0 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:40 | Surface pitting
13329863 | OTA-WKM-C-0379-0380-Earthwire-C0 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 | CA copied from EW A0 Feb/2026
13329863 | OTA-WKM-C-0379-0380-Earthwire-C0 | OTA-WKM-C0379-0380 | OTA-WKM-C0379-0380-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 | Surface pitting. CA copied from EW A0 Feb/2026
10046162 | OTA-WKM-C-0380-Tower | OTA-WKM-C0380 | OTA-WKM-C0380-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046162 | OTA-WKM-C-0380-Tower | OTA-WKM-C0380 | OTA-WKM-C0380-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046162 | OTA-WKM-C-0380-Tower | OTA-WKM-C0380 | OTA-WKM-C0380-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046162 | OTA-WKM-C-0380-Tower | OTA-WKM-C0380 | OTA-WKM-C0380-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046162 | OTA-WKM-C-0380-Tower | OTA-WKM-C0380 | OTA-WKM-C0380-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046162 | OTA-WKM-C-0380-Tower | OTA-WKM-C0380 | OTA-WKM-C0380-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-22 | Tower refurbishment including MAD area CCT2
10046162 | OTA-WKM-C-0380-Tower | OTA-WKM-C0380 | OTA-WKM-C0380-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12054922 | OTA-WKM-C-0380-Tower Foundation | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 11:59
12058838 | OTA-WKM-C-0380-Earthwire HW Set | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:15 | Wrong overlay
12058838 | OTA-WKM-C-0380-Earthwire HW Set | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-23 14:15
13040113 | OTA-WKM-C-0380-Earthwire Attachment | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-23 | Replaced
13040113 | OTA-WKM-C-0380-Earthwire Attachment | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-23 13:58 | Been replaced since last inspection
13040113 | OTA-WKM-C-0380-Earthwire Attachment | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-23 13:58 | Been replaced since last inspection
13040113 | OTA-WKM-C-0380-Earthwire Attachment | OTA-WKM-C0380 | OTA-WKM-C0380-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-23 | Replaced
13186199 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:00
13186199 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 12:00
13186199 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 12:00
13186199 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 12:00
13186200 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 12:03
13186200 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 12:03
13186200 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 12:03
13186200 | OTA-WKM-C-0380-Insulator Set-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 12:03
13262421 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | RSA2 Attach Point Repl 23-24
13262421 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | RSA2 Attach Point Repl 23-24
13262421 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | RSA2 Attach Point Repl 23-24
13262421 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0380 | OTA-WKM-C0380-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | RSA2 Attach Point Repl 23-24
13262422 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 | 2023 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | RSA2 Attach Point Repl 23-24
13262422 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 | 2023 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | RSA2 Attach Point Repl 23-24
13262422 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 | 2023 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | RSA2 Attach Point Repl 23-24
13262422 | OTA-WKM-C-0380-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0380 | OTA-WKM-C0380-20 | 2023 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | RSA2 Attach Point Repl 23-24
10046944 | OTA-WKM-C-0380-0381-Conductor-OHW-OTA-2 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-23 14:16
10046944 | OTA-WKM-C-0380-0381-Conductor-OHW-OTA-2 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:16
10046944 | OTA-WKM-C-0380-0381-Conductor-OHW-OTA-2 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:16
10046945 | OTA-WKM-C-0380-0381-Conductor-OHW-OTA-1 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-23 14:16
10046945 | OTA-WKM-C-0380-0381-Conductor-OHW-OTA-1 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:16
10046945 | OTA-WKM-C-0380-0381-Conductor-OHW-OTA-1 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046945 | OTA-WKM-C-0380-0381-Conductor-OHW-OTA-1 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:16
10046946 | OTA-WKM-C-0380-0381-Earthwire-A0 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:18
10046946 | OTA-WKM-C-0380-0381-Earthwire-A0 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 14:18 | Surface pitting
13329864 | OTA-WKM-C-0380-0381-Earthwire-C0 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 | CA copied from EW A0 Feb/2026
13329864 | OTA-WKM-C-0380-0381-Earthwire-C0 | OTA-WKM-C0380-0381 | OTA-WKM-C0380-0381-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-23 | Surface pitting. CA copied from EW A0 Feb/2026
10046167 | OTA-WKM-C-0381-Tower | OTA-WKM-C0381 | OTA-WKM-C0381-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-30 | Steel members were replaced Z109B /R15X2 Z200B /R15X3 Z70B/R15X1 Z99B/15X1 Z64B/R15X2 Z71B/R15X1 Z206B/R15X1
10046167 | OTA-WKM-C-0381-Tower | OTA-WKM-C0381 | OTA-WKM-C0381-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-30 | Steel members were replaced Z109B /R15X2 Z200B /R15X3 Z70B/R15X1 Z99B/15X1 Z64B/R15X2 Z71B/R15X1 Z206B/R15X1
10046167 | OTA-WKM-C-0381-Tower | OTA-WKM-C0381 | OTA-WKM-C0381-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | "CA - Rusty steel and bolts throughout entire tower, E/W Attachment plates rusty"
10046167 | OTA-WKM-C-0381-Tower | OTA-WKM-C0381 | OTA-WKM-C0381-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | "CA - Rusty steel and bolts throughout entire tower, E/W Attachment plates rusty"
10046167 | OTA-WKM-C-0381-Tower | OTA-WKM-C0381 | OTA-WKM-C0381-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | "CA - Rusty steel and bolts throughout entire tower, E/W Attachment plates rusty"
10046167 | OTA-WKM-C-0381-Tower | OTA-WKM-C0381 | OTA-WKM-C0381-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-22 | Tower refurbishment including MAD area CCT2
10046167 | OTA-WKM-C-0381-Tower | OTA-WKM-C0381 | OTA-WKM-C0381-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | "CA - Rusty steel and bolts throughout entire tower, E/W Attachment plates rusty"
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12054923 | OTA-WKM-C-0381-Tower Foundation | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:18
12058839 | OTA-WKM-C-0381-Earthwire HW Set | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:25 | Wrong overlay
12058839 | OTA-WKM-C-0381-Earthwire HW Set | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:25
13004441 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-20 16:21
13004441 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 16:21
13004441 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 16:21
13004441 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 16:21
13004441 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-03 | Replaced Y Ball Clevis Tongues Yoke Plate Suspension clamps Y Clevis 160Kn Insulator
13004442 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 16:22
13004442 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 16:22
13004442 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 16:22
13004442 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-20 16:22
13004442 | OTA-WKM-C-0381-Insulator Set-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-30 | SR100194-Replaced insulators for all 3 phases - OHW-OTA-2 including hot and cold hardware and armour rods
13040114 | OTA-WKM-C-0381-Earthwire Attachment | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-10-10 08:00 | Updating to 4 Readings
13040114 | OTA-WKM-C-0381-Earthwire Attachment | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-20 16:23
13040114 | OTA-WKM-C-0381-Earthwire Attachment | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-20 16:23
13040114 | OTA-WKM-C-0381-Earthwire Attachment | OTA-WKM-C0381 | OTA-WKM-C0381-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-10-10 08:00 | Updating to 4 Readings
13073689 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
13073689 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
13073689 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
13073689 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0381 | OTA-WKM-C0381-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
13073690 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
13073690 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
13073690 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
13073690 | OTA-WKM-C-0381-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0381 | OTA-WKM-C0381-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:24
10046947 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-2 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-20 16:27
10046947 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-2 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:27
10046947 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-2 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA - Dampers Drooping
10046947 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-2 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:27 | Surface pitting of ring
10046948 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-1 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-20 16:26
10046948 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-1 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:26
10046948 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-1 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA - Dampers Drooping
10046948 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-1 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-10 | 1965 | COSE_REPAIR ROD COND | Repair Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-20 | CA - Dampers Drooping
10046948 | OTA-WKM-C-0381-0382-Conductor-OHW-OTA-1 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-03 | RSA2 25-26 Subconductor Spacer Replacement Project
10046949 | OTA-WKM-C-0381-0382-Earthwire-A0 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:31
10046949 | OTA-WKM-C-0381-0382-Earthwire-A0 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:31 | Surface pitting both CCT
10046949 | OTA-WKM-C-0381-0382-Earthwire-A0 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-12-09 01:00 | CA
13329865 | OTA-WKM-C-0381-0382-Earthwire-C0 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 | CA copied from EW A0 Feb/2026
13329865 | OTA-WKM-C-0381-0382-Earthwire-C0 | OTA-WKM-C0381-0382 | OTA-WKM-C0381-0382-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 | Surface pitting both CCT. CA copied from EW A0 Feb/2026
10046172 | OTA-WKM-C-0382-Tower | OTA-WKM-C0382 | OTA-WKM-C0382-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046172 | OTA-WKM-C-0382-Tower | OTA-WKM-C0382 | OTA-WKM-C0382-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046172 | OTA-WKM-C-0382-Tower | OTA-WKM-C0382 | OTA-WKM-C0382-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046172 | OTA-WKM-C-0382-Tower | OTA-WKM-C0382 | OTA-WKM-C0382-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046172 | OTA-WKM-C-0382-Tower | OTA-WKM-C0382 | OTA-WKM-C0382-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046172 | OTA-WKM-C-0382-Tower | OTA-WKM-C0382 | OTA-WKM-C0382-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-22 | Tower refurbishment up to MAD area
10046172 | OTA-WKM-C-0382-Tower | OTA-WKM-C0382 | OTA-WKM-C0382-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12054924 | OTA-WKM-C-0382-Tower Foundation | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:46
12058840 | OTA-WKM-C-0382-Earthwire HW Set | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:01 | Wrong overlay
12058840 | OTA-WKM-C-0382-Earthwire HW Set | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:01
13004443 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 | 2016 | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 15:47
13004443 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 | 2016 | INSE_SUSP COLD END COND | Susp Cold End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 15:47
13004443 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 | 2016 | INSE_SUSP HOT END COND | Susp Hot End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 15:47
13004443 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 | 2016 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 15:47
13004443 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 | 2016 | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-03 | Replaced Y Tongues Yoke Plate clamps Y Ball Clevis Tongues
13004444 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-16 15:56
13004444 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 15:56
13004444 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 15:56
13004444 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-16 15:56
13004444 | OTA-WKM-C-0382-Insulator Set-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-30 | SR100194-Replaced insulators for all 3 phases - OHW-OTA-2 including hot and cold hardware and armour rods
13040115 | OTA-WKM-C-0382-Earthwire Attachment | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-19 08:41 | New attachment point PLT installed
13040115 | OTA-WKM-C-0382-Earthwire Attachment | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-19 08:30 | New M16X70 DN fitted on both side
13040115 | OTA-WKM-C-0382-Earthwire Attachment | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-19 08:29 | New PLT attachment point fitted on both side
13040115 | OTA-WKM-C-0382-Earthwire Attachment | OTA-WKM-C0382 | OTA-WKM-C0382-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-19 08:42 | Fitted New through bolts and nuts on both side.
13073691 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:04
13073691 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:04
13073691 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:04 | Significant corrosion
13073691 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0382 | OTA-WKM-C0382-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:04 | Significant corrosion
13073692 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:06
13073692 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:06
13073692 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:06
13073692 | OTA-WKM-C-0382-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0382 | OTA-WKM-C0382-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-16 16:06 | Significant corrosion
10046950 | OTA-WKM-C-0382-0383-Conductor-OHW-OTA-2 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-20 16:05
10046950 | OTA-WKM-C-0382-0383-Conductor-OHW-OTA-2 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:05
10046950 | OTA-WKM-C-0382-0383-Conductor-OHW-OTA-2 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:05 | Surface pitting of ring
10046951 | OTA-WKM-C-0382-0383-Conductor-OHW-OTA-1 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-20 16:04
10046951 | OTA-WKM-C-0382-0383-Conductor-OHW-OTA-1 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:04
10046951 | OTA-WKM-C-0382-0383-Conductor-OHW-OTA-1 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-30 | RSA2 25-26 Subconductor Spacer Replacement Project
10046952 | OTA-WKM-C-0382-0383-Earthwire-A0 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:09
10046952 | OTA-WKM-C-0382-0383-Earthwire-A0 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 16:09
13329866 | OTA-WKM-C-0382-0383-Earthwire-C0 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 | CA copied from EW A0 Feb/2026
13329866 | OTA-WKM-C-0382-0383-Earthwire-C0 | OTA-WKM-C0382-0383 | OTA-WKM-C0382-0383-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-20 | CA copied from EW A0 Feb/2026
10046177 | OTA-WKM-C-0383-Tower | OTA-WKM-C0383 | OTA-WKM-C0383-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-06 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046177 | OTA-WKM-C-0383-Tower | OTA-WKM-C0383 | OTA-WKM-C0383-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-06 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046177 | OTA-WKM-C-0383-Tower | OTA-WKM-C0383 | OTA-WKM-C0383-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-06 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046177 | OTA-WKM-C-0383-Tower | OTA-WKM-C0383 | OTA-WKM-C0383-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-06 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046177 | OTA-WKM-C-0383-Tower | OTA-WKM-C0383 | OTA-WKM-C0383-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-06 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046177 | OTA-WKM-C-0383-Tower | OTA-WKM-C0383 | OTA-WKM-C0383-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-27 | Tower refurbishment up to MAD area
10046177 | OTA-WKM-C-0383-Tower | OTA-WKM-C0383 | OTA-WKM-C0383-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-06 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12054925 | OTA-WKM-C-0383-Tower Foundation | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:12
12058841 | OTA-WKM-C-0383-Earthwire HW Set | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:54 | Wrong overlay
12058841 | OTA-WKM-C-0383-Earthwire HW Set | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-21 09:54
13040116 | OTA-WKM-C-0383-Earthwire Attachment | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-11-13 15:34 | Replaced New
13040116 | OTA-WKM-C-0383-Earthwire Attachment | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-11-13 15:33 | Replaced by new
13040116 | OTA-WKM-C-0383-Earthwire Attachment | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-11-13 15:33 | Replaced by new
13040116 | OTA-WKM-C-0383-Earthwire Attachment | OTA-WKM-C0383 | OTA-WKM-C0383-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-11-13 15:34 | Replaced by new
13073693 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0383 | OTA-WKM-C0383-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13073693 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0383 | OTA-WKM-C0383-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13073693 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0383 | OTA-WKM-C0383-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13073693 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0383 | OTA-WKM-C0383-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13073694 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0383 | OTA-WKM-C0383-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13073694 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0383 | OTA-WKM-C0383-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13073694 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0383 | OTA-WKM-C0383-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13073694 | OTA-WKM-C-0383-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0383 | OTA-WKM-C0383-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:36
13285429 | OTA-WKM-C-0383-Insulator Set-OHW-OTA-1 | OTA-WKM-C0383 | OTA-WKM-C0383-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285429 | OTA-WKM-C-0383-Insulator Set-OHW-OTA-1 | OTA-WKM-C0383 | OTA-WKM-C0383-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285429 | OTA-WKM-C-0383-Insulator Set-OHW-OTA-1 | OTA-WKM-C0383 | OTA-WKM-C0383-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285430 | OTA-WKM-C-0383-Insulator Set-OHW-OTA-2 | OTA-WKM-C0383 | OTA-WKM-C0383-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 | Replaced during RSA2 24-25 Reins Project
13285430 | OTA-WKM-C-0383-Insulator Set-OHW-OTA-2 | OTA-WKM-C0383 | OTA-WKM-C0383-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 | Replaced during RSA2 24-25 Reins Project
13285430 | OTA-WKM-C-0383-Insulator Set-OHW-OTA-2 | OTA-WKM-C0383 | OTA-WKM-C0383-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 | Replaced during RSA2 24-25 Reins Project
10046953 | OTA-WKM-C-0383-0384-Conductor-OHW-OTA-2 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 09:34
10046953 | OTA-WKM-C-0383-0384-Conductor-OHW-OTA-2 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:34
10046953 | OTA-WKM-C-0383-0384-Conductor-OHW-OTA-2 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:34
10046954 | OTA-WKM-C-0383-0384-Conductor-OHW-OTA-1 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 09:17
10046954 | OTA-WKM-C-0383-0384-Conductor-OHW-OTA-1 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:17
10046954 | OTA-WKM-C-0383-0384-Conductor-OHW-OTA-1 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-30 | RSA2 25-26 Subconductor Spacer Replacement Project
10046955 | OTA-WKM-C-0383-0384-Earthwire-A0 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:50
10046955 | OTA-WKM-C-0383-0384-Earthwire-A0 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 09:50 | Surface pitting
13329867 | OTA-WKM-C-0383-0384-Earthwire-C0 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | CA copied from EW A0 Feb/2026
13329867 | OTA-WKM-C-0383-0384-Earthwire-C0 | OTA-WKM-C0383-0384 | OTA-WKM-C0383-0384-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | Surface pitting. CA copied from EW A0 Feb/2026
10046182 | OTA-WKM-C-0384-Tower | OTA-WKM-C0384 | OTA-WKM-C0384-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-10 | Fitted new LSD sign and Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046182 | OTA-WKM-C-0384-Tower | OTA-WKM-C0384 | OTA-WKM-C0384-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-10 | Fitted new LSD sign and Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046182 | OTA-WKM-C-0384-Tower | OTA-WKM-C0384 | OTA-WKM-C0384-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-10 | Fitted new LSD sign and Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046182 | OTA-WKM-C-0384-Tower | OTA-WKM-C0384 | OTA-WKM-C0384-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-10 | Fitted new LSD sign and Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046182 | OTA-WKM-C-0384-Tower | OTA-WKM-C0384 | OTA-WKM-C0384-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-10 | Fitted new LSD sign and Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046182 | OTA-WKM-C-0384-Tower | OTA-WKM-C0384 | OTA-WKM-C0384-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-06-16 | Tower refurbishment up to MAD area
10046182 | OTA-WKM-C-0384-Tower | OTA-WKM-C0384 | OTA-WKM-C0384-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-10 | Fitted new LSD sign and Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12054926 | OTA-WKM-C-0384-Tower Foundation | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:22
12058842 | OTA-WKM-C-0384-Earthwire HW Set | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:52 | Wrong overlay
12058842 | OTA-WKM-C-0384-Earthwire HW Set | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:52
13004445 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 08:25
13004445 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13004445 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13004445 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13004445 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-03 | Replaced Yoke Plate Socket Clevis clamps Y Tongues Y Ball Clevis
13004446 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 | 2017 | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 08:25
13004446 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 | 2017 | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13004446 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 | 2017 | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13004446 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 | 2017 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13004446 | OTA-WKM-C-0384-Insulator Set-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 | 2017 | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-30 | SR100194-Replaced insulators for all 3 phases including hot and cold hardware and armour rods - OHW-OTA-2
13073696 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:52
13073696 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:52
13073696 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:52 | Significant corrosion
13073696 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0384 | OTA-WKM-C0384-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:52
13228992 | OTA-WKM-C-0384-Earthwire Attachment | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-03-24
13228992 | OTA-WKM-C-0384-Earthwire Attachment | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13228992 | OTA-WKM-C-0384-Earthwire Attachment | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 08:25
13228992 | OTA-WKM-C-0384-Earthwire Attachment | OTA-WKM-C0384 | OTA-WKM-C0384-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-03-24
13253928 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | Replaced during RSA2 25-26 Att Pt Project
13253928 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | Replaced during RSA2 25-26 Att Pt Project
13253928 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | Replaced during RSA2 25-26 Att Pt Project
13253928 | OTA-WKM-C-0384-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0384 | OTA-WKM-C0384-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | Replaced during RSA2 25-26 Att Pt Project
10046956 | OTA-WKM-C-0384-0385-Conductor-OHW-OTA-2 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 08:30
10046956 | OTA-WKM-C-0384-0385-Conductor-OHW-OTA-2 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:30
10046956 | OTA-WKM-C-0384-0385-Conductor-OHW-OTA-2 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:30
10046957 | OTA-WKM-C-0384-0385-Conductor-OHW-OTA-1 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 08:30
10046957 | OTA-WKM-C-0384-0385-Conductor-OHW-OTA-1 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:30
10046957 | OTA-WKM-C-0384-0385-Conductor-OHW-OTA-1 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:30
10046958 | OTA-WKM-C-0384-0385-Earthwire-A0 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:53
10046958 | OTA-WKM-C-0384-0385-Earthwire-A0 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 08:53 | Surface pitting
13329868 | OTA-WKM-C-0384-0385-Earthwire-C0 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | CA copied from EW A0 Feb/2026
13329868 | OTA-WKM-C-0384-0385-Earthwire-C0 | OTA-WKM-C0384-0385 | OTA-WKM-C0384-0385-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | Surface pitting. CA copied from EW A0 Feb/2026
10046187 | OTA-WKM-C-0385-Tower | OTA-WKM-C0385 | OTA-WKM-C0385-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046187 | OTA-WKM-C-0385-Tower | OTA-WKM-C0385 | OTA-WKM-C0385-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046187 | OTA-WKM-C-0385-Tower | OTA-WKM-C0385 | OTA-WKM-C0385-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046187 | OTA-WKM-C-0385-Tower | OTA-WKM-C0385 | OTA-WKM-C0385-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046187 | OTA-WKM-C-0385-Tower | OTA-WKM-C0385 | OTA-WKM-C0385-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046187 | OTA-WKM-C-0385-Tower | OTA-WKM-C0385 | OTA-WKM-C0385-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-05-25 | Tower refurbishment up to MAD area
10046187 | OTA-WKM-C-0385-Tower | OTA-WKM-C0385 | OTA-WKM-C0385-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10261295 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:03
10261295 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 12:03
10261295 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:03
10261295 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 12:03
10261303 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:23
10261303 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 12:23
10261303 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 12:23
10261303 | OTA-WKM-C-0385-Insulator Set-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:23
10332809 | OTA-WKM-C-0385-Earthwire HW Set | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 15:14 | Surface pittingwrong overlay
10332809 | OTA-WKM-C-0385-Earthwire HW Set | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 15:14
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
12054927 | OTA-WKM-C-0385-Tower Foundation | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 11:52
13040118 | OTA-WKM-C-0385-Earthwire Attachment | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:10
13040118 | OTA-WKM-C-0385-Earthwire Attachment | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:10
13040118 | OTA-WKM-C-0385-Earthwire Attachment | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:10
13040118 | OTA-WKM-C-0385-Earthwire Attachment | OTA-WKM-C0385 | OTA-WKM-C0385-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:10
13073697 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:22
13073697 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:22
13073697 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:22
13073697 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0385 | OTA-WKM-C0385-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:22
13073698 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:22
13073698 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:22
13073698 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:22
13073698 | OTA-WKM-C-0385-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0385 | OTA-WKM-C0385-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 12:22
10046959 | OTA-WKM-C-0385-0386-Conductor-OHW-OTA-2 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:46
10046959 | OTA-WKM-C-0385-0386-Conductor-OHW-OTA-2 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:46
10046959 | OTA-WKM-C-0385-0386-Conductor-OHW-OTA-2 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:46
10046960 | OTA-WKM-C-0385-0386-Conductor-OHW-OTA-1 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:46
10046960 | OTA-WKM-C-0385-0386-Conductor-OHW-OTA-1 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:46
10046960 | OTA-WKM-C-0385-0386-Conductor-OHW-OTA-1 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - Dampers Drooping
10046960 | OTA-WKM-C-0385-0386-Conductor-OHW-OTA-1 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:46
10046961 | OTA-WKM-C-0385-0386-Earthwire-A0 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:16
10046961 | OTA-WKM-C-0385-0386-Earthwire-A0 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 12:16
13329869 | OTA-WKM-C-0385-0386-Earthwire-C0 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | CA copied from EW A0 Feb/2026
13329869 | OTA-WKM-C-0385-0386-Earthwire-C0 | OTA-WKM-C0385-0386 | OTA-WKM-C0385-0386-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | CA copied from EW A0 Feb/2026
10046192 | OTA-WKM-C-0386-Tower | OTA-WKM-C0386 | OTA-WKM-C0386-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-14 | Replaced Steel members 295Ax1 Z112Ax1. Replaced Bolts
10046192 | OTA-WKM-C-0386-Tower | OTA-WKM-C0386 | OTA-WKM-C0386-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-14 | Replaced Steel members 295Ax1 Z112Ax1. Replaced Bolts
10046192 | OTA-WKM-C-0386-Tower | OTA-WKM-C0386 | OTA-WKM-C0386-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-14 | Replaced Steel members 295Ax1 Z112Ax1. Replaced Bolts
10046192 | OTA-WKM-C-0386-Tower | OTA-WKM-C0386 | OTA-WKM-C0386-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-14 | Replaced Steel members 295Ax1 Z112Ax1. Replaced Bolts
10046192 | OTA-WKM-C-0386-Tower | OTA-WKM-C0386 | OTA-WKM-C0386-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-14 | Replaced Steel members 295Ax1 Z112Ax1. Replaced Bolts
10046192 | OTA-WKM-C-0386-Tower | OTA-WKM-C0386 | OTA-WKM-C0386-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-03-01 | Tower refurbishment up to MAD area
10046192 | OTA-WKM-C-0386-Tower | OTA-WKM-C0386 | OTA-WKM-C0386-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-14 | Replaced Steel members 295Ax1 Z112Ax1. Replaced Bolts
10046196 | OTA-WKM-C-0386-Earthwire HW Set | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 12:20 | Wrong overlay
10046196 | OTA-WKM-C-0386-Earthwire HW Set | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 12:20
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:21
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 09:21
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:21
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 09:21
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:21
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 09:21
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 09:21
12054928 | OTA-WKM-C-0386-Tower Foundation | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 09:21
13040119 | OTA-WKM-C-0386-Earthwire Attachment | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-07-10 08:00 | Updating to 4 Readings
13040119 | OTA-WKM-C-0386-Earthwire Attachment | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-21 12:16
13040119 | OTA-WKM-C-0386-Earthwire Attachment | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 12:16
13040119 | OTA-WKM-C-0386-Earthwire Attachment | OTA-WKM-C0386 | OTA-WKM-C0386-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-07-10 08:00 | Updating to 4 Readings
13073699 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13073699 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13073699 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13073699 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13073700 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13073700 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13073700 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13073700 | OTA-WKM-C-0386-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
13186201 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:45
13186201 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 11:45
13186201 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 11:45
13186201 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-1 | OTA-WKM-C0386 | OTA-WKM-C0386-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 11:45
13186202 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:46
13186202 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 11:46
13186202 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 11:46
13186202 | OTA-WKM-C-0386-Insulator Set-OHW-OTA-2 | OTA-WKM-C0386 | OTA-WKM-C0386-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 11:46
10046962 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-2 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 11:50
10046962 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-2 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:50
10046962 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-2 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA
10046962 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-2 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:50
10046963 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-1 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
10046963 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-1 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
10046963 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-1 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-04-27 | CA
10046963 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-1 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-10 | 1965 | COSE_REPAIR ROD COND | Repair Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA
10046963 | OTA-WKM-C-0386-0387-Conductor-OHW-OTA-1 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:48
10046964 | OTA-WKM-C-0386-0387-Earthwire-A0 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 12:18
10046964 | OTA-WKM-C-0386-0387-Earthwire-A0 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 12:18
10046964 | OTA-WKM-C-0386-0387-Earthwire-A0 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-09 | CA
13329870 | OTA-WKM-C-0386-0387-Earthwire-C0 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | CA copied from EW A0 Feb/2026
13329870 | OTA-WKM-C-0386-0387-Earthwire-C0 | OTA-WKM-C0386-0387 | OTA-WKM-C0386-0387-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | CA copied from EW A0 Feb/2026
10046197 | OTA-WKM-C-0387-Tower | OTA-WKM-C0387 | OTA-WKM-C0387-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA
10046197 | OTA-WKM-C-0387-Tower | OTA-WKM-C0387 | OTA-WKM-C0387-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA
10046197 | OTA-WKM-C-0387-Tower | OTA-WKM-C0387 | OTA-WKM-C0387-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA
10046197 | OTA-WKM-C-0387-Tower | OTA-WKM-C0387 | OTA-WKM-C0387-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA
10046197 | OTA-WKM-C-0387-Tower | OTA-WKM-C0387 | OTA-WKM-C0387-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA
10046197 | OTA-WKM-C-0387-Tower | OTA-WKM-C0387 | OTA-WKM-C0387-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-03-24 | Tower refurbishment up to MAD area
10046197 | OTA-WKM-C-0387-Tower | OTA-WKM-C0387 | OTA-WKM-C0387-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA
10332810 | OTA-WKM-C-0387-Earthwire HW Set | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 10:57
10332810 | OTA-WKM-C-0387-Earthwire HW Set | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:57
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
12054929 | OTA-WKM-C-0387-Tower Foundation | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 11:12
13004447 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 10:46
13004447 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:46
13004447 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:46
13004447 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:46
13004448 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 10:46
13004448 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:46
13004448 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:46
13004448 | OTA-WKM-C-0387-Insulator Set-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:46
13040120 | OTA-WKM-C-0387-Earthwire Attachment | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:56
13040120 | OTA-WKM-C-0387-Earthwire Attachment | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:56
13040120 | OTA-WKM-C-0387-Earthwire Attachment | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:56
13040120 | OTA-WKM-C-0387-Earthwire Attachment | OTA-WKM-C0387 | OTA-WKM-C0387-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 10:56
13262423 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-05 | RSA2 Attachment Point Replacement 23-24
13262423 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-05 | RSA2 Attachment Point Replacement 23-24
13262423 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-05 | RSA2 Attachment Point Replacement 23-24
13262423 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0387 | OTA-WKM-C0387-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-05 | RSA2 Attachment Point Replacement 23-24
13262424 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-15 | RSA2 Attach Point Repl 23-24
13262424 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-15 | RSA2 Attach Point Repl 23-24
13262424 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-15 | RSA2 Attach Point Repl 23-24
13262424 | OTA-WKM-C-0387-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0387 | OTA-WKM-C0387-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-15 | RSA2 Attach Point Repl 23-24
10046965 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-2 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 11:14
10046965 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-2 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:14
10046965 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-2 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA - Dampers Drooping
10046965 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-2 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:14
10046966 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-1 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 11:14
10046966 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-1 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:14
10046966 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-1 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2011-05-11 | CA - Dampers Drooping
10046966 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-1 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-10 | 1965 | COSE_REPAIR ROD COND | Repair Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-11 | CA - Dampers Drooping
10046966 | OTA-WKM-C-0387-0388-Conductor-OHW-OTA-1 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:14
10046967 | OTA-WKM-C-0387-0388-Earthwire-A0 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:16
10046967 | OTA-WKM-C-0387-0388-Earthwire-A0 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 11:16 | Surface pitting
10046967 | OTA-WKM-C-0387-0388-Earthwire-A0 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-08-28 | CA
13329871 | OTA-WKM-C-0387-0388-Earthwire-C0 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | CA copied from EW A0 Feb/2026
13329871 | OTA-WKM-C-0387-0388-Earthwire-C0 | OTA-WKM-C0387-0388 | OTA-WKM-C0387-0388-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | Surface pitting. CA copied from EW A0 Feb/2026
10046202 | OTA-WKM-C-0388-Tower | OTA-WKM-C0388 | OTA-WKM-C0388-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA - E/W Attachment plate rusty
10046202 | OTA-WKM-C-0388-Tower | OTA-WKM-C0388 | OTA-WKM-C0388-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA - E/W Attachment plate rusty
10046202 | OTA-WKM-C-0388-Tower | OTA-WKM-C0388 | OTA-WKM-C0388-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA - E/W Attachment plate rusty
10046202 | OTA-WKM-C-0388-Tower | OTA-WKM-C0388 | OTA-WKM-C0388-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA - E/W Attachment plate rusty
10046202 | OTA-WKM-C-0388-Tower | OTA-WKM-C0388 | OTA-WKM-C0388-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA - E/W Attachment plate rusty
10046202 | OTA-WKM-C-0388-Tower | OTA-WKM-C0388 | OTA-WKM-C0388-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-04-14 | Full Tower Refurbishment including CCT1 & CCT2 (2-coat system)
10046202 | OTA-WKM-C-0388-Tower | OTA-WKM-C0388 | OTA-WKM-C0388-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA - E/W Attachment plate rusty
10046206 | OTA-WKM-C-0388-Earthwire HW Set | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:37 | Wrong overlay
10046206 | OTA-WKM-C-0388-Earthwire HW Set | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:37
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
12054930 | OTA-WKM-C-0388-Tower Foundation | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:38
13040121 | OTA-WKM-C-0388-Earthwire Attachment | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-29 08:00 | Updating to 4 Readings
13040121 | OTA-WKM-C-0388-Earthwire Attachment | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 14:44
13040121 | OTA-WKM-C-0388-Earthwire Attachment | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 14:44
13040121 | OTA-WKM-C-0388-Earthwire Attachment | OTA-WKM-C0388 | OTA-WKM-C0388-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-29 08:00 | Updating to 4 Readings
13186203 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:41
13186203 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 14:41
13186203 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 14:41
13186203 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 14:41
13186204 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-21 14:44
13186204 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 14:44
13186204 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 14:44
13186204 | OTA-WKM-C-0388-Insulator Set-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-21 14:44
13262425 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 | 2023 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | Attachment Replacement WO3011753
13262425 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 | 2023 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | Attachment Replacement WO3011753
13262425 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 | 2023 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | Attachment Replacement WO3011753
13262425 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0388 | OTA-WKM-C0388-10 | 2023 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-09 | Attachment Replacement WO3011753
13262426 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 | 2023 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Attachment Replacement WO3011754
13262426 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 | 2023 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Attachment Replacement WO3011754
13262426 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 | 2023 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Attachment Replacement WO3011754
13262426 | OTA-WKM-C-0388-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0388 | OTA-WKM-C0388-20 | 2023 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Attachment Replacement WO3011754
10046968 | OTA-WKM-C-0388-0389-Conductor-OHW-OTA-2 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 15:05
10046968 | OTA-WKM-C-0388-0389-Conductor-OHW-OTA-2 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:05
10046968 | OTA-WKM-C-0388-0389-Conductor-OHW-OTA-2 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:05
10046969 | OTA-WKM-C-0388-0389-Conductor-OHW-OTA-1 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-21 15:05
10046969 | OTA-WKM-C-0388-0389-Conductor-OHW-OTA-1 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:05
10046969 | OTA-WKM-C-0388-0389-Conductor-OHW-OTA-1 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:05
10046970 | OTA-WKM-C-0388-0389-Earthwire-A0 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:38
10046970 | OTA-WKM-C-0388-0389-Earthwire-A0 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 15:38
10046970 | OTA-WKM-C-0388-0389-Earthwire-A0 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-28 | CA
13329872 | OTA-WKM-C-0388-0389-Earthwire-C0 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | CA copied from EW A0 Feb/2026
13329872 | OTA-WKM-C-0388-0389-Earthwire-C0 | OTA-WKM-C0388-0389 | OTA-WKM-C0388-0389-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-21 | CA copied from EW A0 Feb/2026
10046207 | OTA-WKM-C-0389-Tower | OTA-WKM-C0389 | OTA-WKM-C0389-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Rusty steel members on body and Crossarms, CCT2 Insulator attachment windwear and metal loss, E/W Attachment plates with metal loss"
10046207 | OTA-WKM-C-0389-Tower | OTA-WKM-C0389 | OTA-WKM-C0389-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Rusty steel members on body and Crossarms, CCT2 Insulator attachment windwear and metal loss, E/W Attachment plates with metal loss"
10046207 | OTA-WKM-C-0389-Tower | OTA-WKM-C0389 | OTA-WKM-C0389-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Rusty steel members on body and Crossarms, CCT2 Insulator attachment windwear and metal loss, E/W Attachment plates with metal loss"
10046207 | OTA-WKM-C-0389-Tower | OTA-WKM-C0389 | OTA-WKM-C0389-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Rusty steel members on body and Crossarms, CCT2 Insulator attachment windwear and metal loss, E/W Attachment plates with metal loss"
10046207 | OTA-WKM-C-0389-Tower | OTA-WKM-C0389 | OTA-WKM-C0389-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Rusty steel members on body and Crossarms, CCT2 Insulator attachment windwear and metal loss, E/W Attachment plates with metal loss"
10046207 | OTA-WKM-C-0389-Tower | OTA-WKM-C0389 | OTA-WKM-C0389-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-12-21 | Tower refurbishment up to MAD area
10046207 | OTA-WKM-C-0389-Tower | OTA-WKM-C0389 | OTA-WKM-C0389-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Rusty steel members on body and Crossarms, CCT2 Insulator attachment windwear and metal loss, E/W Attachment plates with metal loss"
10332811 | OTA-WKM-C-0389-Earthwire HW Set | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 15:11 | Wrong overlay
10332811 | OTA-WKM-C-0389-Earthwire HW Set | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 15:11
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
12054931 | OTA-WKM-C-0389-Tower Foundation | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:52
13040122 | OTA-WKM-C-0389-Earthwire Attachment | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-29 08:00 | Updating to 4 Readings
13040122 | OTA-WKM-C-0389-Earthwire Attachment | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 15:06
13040122 | OTA-WKM-C-0389-Earthwire Attachment | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 15:06
13040122 | OTA-WKM-C-0389-Earthwire Attachment | OTA-WKM-C0389 | OTA-WKM-C0389-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-29 08:00 | Updating to 4 Readings
13253195 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 TL Insulators 23-24
13253195 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 TL Insulators 23-24
13253195 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 TL Insulators 23-24
13253195 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 TL Insulators 23-24
13253196 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | RSA2 TL Insulators 23-24
13253196 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | RSA2 TL Insulators 23-24
13253196 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | RSA2 TL Insulators 23-24
13253196 | OTA-WKM-C-0389-Insulator Set-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | RSA2 TL Insulators 23-24
13262427 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 Attachment Point Replacement 23-24
13262427 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 Attachment Point Replacement 23-24
13262427 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 Attachment Point Replacement 23-24
13262427 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0389 | OTA-WKM-C0389-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-07 | RSA2 Attachment Point Replacement 23-24
13262428 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 | 2023 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | Attachment Replacement WO3011756
13262428 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 | 2023 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | Attachment Replacement WO3011756
13262428 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 | 2023 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | Attachment Replacement WO3011756
13262428 | OTA-WKM-C-0389-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0389 | OTA-WKM-C0389-20 | 2023 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-12 | Attachment Replacement WO3011756
10046971 | OTA-WKM-C-0389-0390-Conductor-OHW-OTA-2 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 10:59
10046971 | OTA-WKM-C-0389-0390-Conductor-OHW-OTA-2 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:59
10046971 | OTA-WKM-C-0389-0390-Conductor-OHW-OTA-2 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:59
10046972 | OTA-WKM-C-0389-0390-Conductor-OHW-OTA-1 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 10:58
10046972 | OTA-WKM-C-0389-0390-Conductor-OHW-OTA-1 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:58
10046972 | OTA-WKM-C-0389-0390-Conductor-OHW-OTA-1 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:58
10046973 | OTA-WKM-C-0389-0390-Earthwire-A0 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 15:11
10046973 | OTA-WKM-C-0389-0390-Earthwire-A0 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 15:11 | Surface pitting
13329873 | OTA-WKM-C-0389-0390-Earthwire-C0 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | CA copied from EW A0 Feb/2026
13329873 | OTA-WKM-C-0389-0390-Earthwire-C0 | OTA-WKM-C0389-0390 | OTA-WKM-C0389-0390-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | Surface pitting. CA copied from EW A0 Feb/2026
10046212 | OTA-WKM-C-0390-Tower | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-11 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046212 | OTA-WKM-C-0390-Tower | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-11 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046212 | OTA-WKM-C-0390-Tower | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-11 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046212 | OTA-WKM-C-0390-Tower | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-11 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046212 | OTA-WKM-C-0390-Tower | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-11 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046212 | OTA-WKM-C-0390-Tower | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-12-21 | Tower refurbishment up to MAD area
10046212 | OTA-WKM-C-0390-Tower | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-11 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046214 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 15:47
10046214 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:47
10046214 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:47 | Significant corrosion
10046214 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:47 | Significant corrosion
10046215 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 15:49
10046215 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:49
10046215 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:49 | Significant corrosion
10046215 | OTA-WKM-C-0390-Insulator Set-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:49 | Significant corrosion
10046216 | OTA-WKM-C-0390-Earthwire HW Set | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-22 | Replaced during project work
10046216 | OTA-WKM-C-0390-Earthwire HW Set | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-22 | Replaced during project work.
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 16:23
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 16:23
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 16:23
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 16:23
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 16:23
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 16:23
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 16:23
12054932 | OTA-WKM-C-0390-Tower Foundation | OTA-WKM-C0390 | OTA-WKM-C0390-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 16:23
13073707 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13073707 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13073707 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13073707 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0390 | OTA-WKM-C0390-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13073708 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13073708 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13073708 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13073708 | OTA-WKM-C-0390-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0390 | OTA-WKM-C0390-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 15:57
13286454 | OTA-WKM-C-0390-Earthwire Attachment | OTA-WKM-C0390 | OTA-WKM-C0390-00 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-22 | Replaced during RSA2 24-25 Att Pt Project
10046974 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-2 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 16:40
10046974 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-2 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 16:40
10046974 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-2 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046974 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-2 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-20 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046974 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-2 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 16:40
10046975 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-1 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 16:40
10046975 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-1 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 16:40
10046975 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-1 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046975 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-1 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-10 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-01 | Routine CA
10046975 | OTA-WKM-C-0390-0391-Conductor-OHW-OTA-1 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 16:40
10046976 | OTA-WKM-C-0390-0391-Earthwire-A0 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 16:08
10046976 | OTA-WKM-C-0390-0391-Earthwire-A0 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 16:08 | Surface pitting on both circuit
13329874 | OTA-WKM-C-0390-0391-Earthwire-C0 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | CA copied from EW A0 Feb/2026
13329874 | OTA-WKM-C-0390-0391-Earthwire-C0 | OTA-WKM-C0390-0391 | OTA-WKM-C0390-0391-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | Surface pitting on both circuit. CA copied from EW A0 Feb/2026
10046217 | OTA-WKM-C-0391-Tower | OTA-WKM-C0391 | OTA-WKM-C0391-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046217 | OTA-WKM-C-0391-Tower | OTA-WKM-C0391 | OTA-WKM-C0391-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046217 | OTA-WKM-C-0391-Tower | OTA-WKM-C0391 | OTA-WKM-C0391-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046217 | OTA-WKM-C-0391-Tower | OTA-WKM-C0391 | OTA-WKM-C0391-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046217 | OTA-WKM-C-0391-Tower | OTA-WKM-C0391 | OTA-WKM-C0391-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046217 | OTA-WKM-C-0391-Tower | OTA-WKM-C0391 | OTA-WKM-C0391-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-07-14 | Tower refurbishment up to MAD area
10046217 | OTA-WKM-C-0391-Tower | OTA-WKM-C0391 | OTA-WKM-C0391-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046221 | OTA-WKM-C-0391-Earthwire HW Set | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-12 | Replaced hardware when replacing att points
10046221 | OTA-WKM-C-0391-Earthwire HW Set | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-12 | Replaced hardware when replacing att points
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
12054933 | OTA-WKM-C-0391-Tower Foundation | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:31
13040124 | OTA-WKM-C-0391-Earthwire Attachment | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-12 10:37 | Replaced
13040124 | OTA-WKM-C-0391-Earthwire Attachment | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-12 10:36 | Replaced
13040124 | OTA-WKM-C-0391-Earthwire Attachment | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-12 10:36 | Replaced
13040124 | OTA-WKM-C-0391-Earthwire Attachment | OTA-WKM-C0391 | OTA-WKM-C0391-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-12 10:37 | Replaced
13073709 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13
13073709 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13
13073709 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13
13073709 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13
13073710 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13
13073710 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13
13073710 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13 | Significant corrosion
13073710 | OTA-WKM-C-0391-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:13
13186205 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:33
13186205 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 09:33
13186205 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 09:33
13186205 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-1 | OTA-WKM-C0391 | OTA-WKM-C0391-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 09:33
13186206 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 09:34
13186206 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 09:34
13186206 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 09:34
13186206 | OTA-WKM-C-0391-Insulator Set-OHW-OTA-2 | OTA-WKM-C0391 | OTA-WKM-C0391-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 09:34
10046977 | OTA-WKM-C-0391-0392-Conductor-OHW-OTA-2 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 09:46
10046977 | OTA-WKM-C-0391-0392-Conductor-OHW-OTA-2 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:46
10046977 | OTA-WKM-C-0391-0392-Conductor-OHW-OTA-2 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:46 | Significant corrosion
10046978 | OTA-WKM-C-0391-0392-Conductor-OHW-OTA-1 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-11 09:46
10046978 | OTA-WKM-C-0391-0392-Conductor-OHW-OTA-1 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:46
10046978 | OTA-WKM-C-0391-0392-Conductor-OHW-OTA-1 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:46 | Significant corrosion
10046979 | OTA-WKM-C-0391-0392-Earthwire-A0 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:11
10046979 | OTA-WKM-C-0391-0392-Earthwire-A0 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 10:11 | Surface pitting
10046979 | OTA-WKM-C-0391-0392-Earthwire-A0 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-27 | CA
13329875 | OTA-WKM-C-0391-0392-Earthwire-C0 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | CA copied from EW A0 Feb/2026
13329875 | OTA-WKM-C-0391-0392-Earthwire-C0 | OTA-WKM-C0391-0392 | OTA-WKM-C0391-0392-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | Surface pitting. CA copied from EW A0 Feb/2026
10046222 | OTA-WKM-C-0392-Tower | OTA-WKM-C0392 | OTA-WKM-C0392-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046222 | OTA-WKM-C-0392-Tower | OTA-WKM-C0392 | OTA-WKM-C0392-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046222 | OTA-WKM-C-0392-Tower | OTA-WKM-C0392 | OTA-WKM-C0392-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046222 | OTA-WKM-C-0392-Tower | OTA-WKM-C0392 | OTA-WKM-C0392-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046222 | OTA-WKM-C-0392-Tower | OTA-WKM-C0392 | OTA-WKM-C0392-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10046222 | OTA-WKM-C-0392-Tower | OTA-WKM-C0392 | OTA-WKM-C0392-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-07-13 | Tower refurbishment up to MAD area
10046222 | OTA-WKM-C-0392-Tower | OTA-WKM-C0392 | OTA-WKM-C0392-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - E/W attachment plates have metal loss
10332812 | OTA-WKM-C-0392-Earthwire HW Set | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-07-10 00:10 | Replaced Earth wire armour rods on both sides of Str.
10332812 | OTA-WKM-C-0392-Earthwire HW Set | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-07-10 00:09 | Replaced Earth wire Hard ware and attachment plate on both sides of Str.
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
12054934 | OTA-WKM-C-0392-Tower Foundation | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:54
13040125 | OTA-WKM-C-0392-Earthwire Attachment | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-28 08:00 | Updating to 4 Readings
13040125 | OTA-WKM-C-0392-Earthwire Attachment | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-11 09:49
13040125 | OTA-WKM-C-0392-Earthwire Attachment | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-11 09:49
13040125 | OTA-WKM-C-0392-Earthwire Attachment | OTA-WKM-C0392 | OTA-WKM-C0392-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-28 08:00 | Updating to 4 Readings
13073711 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50
13073711 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50
13073711 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50
13073711 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50
13073712 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50
13073712 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50
13073712 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50 | Significant corrosion
13073712 | OTA-WKM-C-0392-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:50
13186207 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-10 11:04
13186207 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 11:04
13186207 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 11:04
13186207 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-1 | OTA-WKM-C0392 | OTA-WKM-C0392-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 11:04
13186208 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-10 11:04
13186208 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 11:04
13186208 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 11:04
13186208 | OTA-WKM-C-0392-Insulator Set-OHW-OTA-2 | OTA-WKM-C0392 | OTA-WKM-C0392-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 11:04
10046980 | OTA-WKM-C-0392-0393-Conductor-OHW-OTA-2 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-10 11:08
10046980 | OTA-WKM-C-0392-0393-Conductor-OHW-OTA-2 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 11:08
10046980 | OTA-WKM-C-0392-0393-Conductor-OHW-OTA-2 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA
10046981 | OTA-WKM-C-0392-0393-Conductor-OHW-OTA-1 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-10 11:07
10046981 | OTA-WKM-C-0392-0393-Conductor-OHW-OTA-1 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 11:07
10046981 | OTA-WKM-C-0392-0393-Conductor-OHW-OTA-1 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA
10046982 | OTA-WKM-C-0392-0393-Earthwire-A0 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:53
10046982 | OTA-WKM-C-0392-0393-Earthwire-A0 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 09:53
13329876 | OTA-WKM-C-0392-0393-Earthwire-C0 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | CA copied from EW A0 Feb/2026
13329876 | OTA-WKM-C-0392-0393-Earthwire-C0 | OTA-WKM-C0392-0393 | OTA-WKM-C0392-0393-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-11 | CA copied from EW A0 Feb/2026
10046227 | OTA-WKM-C-0393-Tower | OTA-WKM-C0393 | OTA-WKM-C0393-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046227 | OTA-WKM-C-0393-Tower | OTA-WKM-C0393 | OTA-WKM-C0393-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046227 | OTA-WKM-C-0393-Tower | OTA-WKM-C0393 | OTA-WKM-C0393-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046227 | OTA-WKM-C-0393-Tower | OTA-WKM-C0393 | OTA-WKM-C0393-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046227 | OTA-WKM-C-0393-Tower | OTA-WKM-C0393 | OTA-WKM-C0393-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046227 | OTA-WKM-C-0393-Tower | OTA-WKM-C0393 | OTA-WKM-C0393-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-07-13 | Tower refurbishment up to MAD area
10046227 | OTA-WKM-C-0393-Tower | OTA-WKM-C0393 | OTA-WKM-C0393-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12054935 | OTA-WKM-C-0393-Tower Foundation | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 10:53
12058843 | OTA-WKM-C-0393-Earthwire HW Set | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 10:00
12058843 | OTA-WKM-C-0393-Earthwire HW Set | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 10:00
13004449 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-10 08:53
13004449 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 08:53
13004449 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 08:53
13004449 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 08:53
13004449 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-02 | Old attachment points coded 50% hot and cold hardware successfully replaced to new set.
13004450 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-10 08:54
13004450 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 08:54
13004450 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 08:54
13004450 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-10 08:54
13004450 | OTA-WKM-C-0393-Insulator Set-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-29 | SR100194-Replaced insulators for all 3 phases - OHW-OTA-2 including hot and cold hardware and armour rods
13040126 | OTA-WKM-C-0393-Earthwire Attachment | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-25 08:00 | Updating to 4 Readings
13040126 | OTA-WKM-C-0393-Earthwire Attachment | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:56 | Painted and blasted
13040126 | OTA-WKM-C-0393-Earthwire Attachment | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:56 | Wind wear
13040126 | OTA-WKM-C-0393-Earthwire Attachment | OTA-WKM-C0393 | OTA-WKM-C0393-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-25 08:00 | Updating to 4 Readings
13073714 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:57
13073714 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:57
13073714 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:57
13073714 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0393 | OTA-WKM-C0393-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:57
13286389 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Att Pt Project
13286389 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Att Pt Project
13286389 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Att Pt Project
13286389 | OTA-WKM-C-0393-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0393 | OTA-WKM-C0393-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Att Pt Project
10046983 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-2 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-10 09:04
10046983 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-2 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:04
10046983 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-2 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046983 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-2 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046984 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-1 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-10 09:00
10046984 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-1 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 09:00
10046984 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-1 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046984 | OTA-WKM-C-0393-0394-Conductor-OHW-OTA-1 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046985 | OTA-WKM-C-0393-0394-Earthwire-A0 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 10:01
10046985 | OTA-WKM-C-0393-0394-Earthwire-A0 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 10:01 | Surface pitting on CCT1 EW
13329877 | OTA-WKM-C-0393-0394-Earthwire-C0 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 | CA copied from EW A0 Feb/2026
13329877 | OTA-WKM-C-0393-0394-Earthwire-C0 | OTA-WKM-C0393-0394 | OTA-WKM-C0393-0394-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-10 | Surface pitting on CCT1 EW. CA copied from EW A0 Feb/2026
10046232 | OTA-WKM-C-0394-Tower | OTA-WKM-C0394 | OTA-WKM-C0394-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046232 | OTA-WKM-C-0394-Tower | OTA-WKM-C0394 | OTA-WKM-C0394-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046232 | OTA-WKM-C-0394-Tower | OTA-WKM-C0394 | OTA-WKM-C0394-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046232 | OTA-WKM-C-0394-Tower | OTA-WKM-C0394 | OTA-WKM-C0394-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046232 | OTA-WKM-C-0394-Tower | OTA-WKM-C0394 | OTA-WKM-C0394-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046232 | OTA-WKM-C-0394-Tower | OTA-WKM-C0394 | OTA-WKM-C0394-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-06-16 | Tower refurbishment up to MAD area
10046232 | OTA-WKM-C-0394-Tower | OTA-WKM-C0394 | OTA-WKM-C0394-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046235 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 | 1965 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-18 12:32
10046235 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 | 1965 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:32 | Wind wear
10046235 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 | 1965 | INSE_SUSP HOT END COND | Susp Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:32
10046235 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 | 1965 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:32 | Significant corrosion
10046236 | OTA-WKM-C-0394-Earthwire HW Set | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-20 11:45
10046236 | OTA-WKM-C-0394-Earthwire HW Set | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-20 11:45
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
12054936 | OTA-WKM-C-0394-Tower Foundation | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 11:36
13040127 | OTA-WKM-C-0394-Earthwire Attachment | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-20 11:52 | New Attachment point installed on both side
13040127 | OTA-WKM-C-0394-Earthwire Attachment | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-20 11:50 | New bolts and nuts Fitted with M16X70 DN
13040127 | OTA-WKM-C-0394-Earthwire Attachment | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-20 11:49 | Installed new EW Attachment points plate on both Cct
13040127 | OTA-WKM-C-0394-Earthwire Attachment | OTA-WKM-C0394 | OTA-WKM-C0394-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-20 11:53 | New through bolts and nuts fitted on both side
13073715 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:33
13073715 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:33
13073715 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:33
13073715 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0394 | OTA-WKM-C0394-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:33
13073716 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:29
13073716 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:29
13073716 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:29
13073716 | OTA-WKM-C-0394-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:29
13186209 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-02-18 12:32
13186209 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-18 12:32
13186209 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-18 12:32
13186209 | OTA-WKM-C-0394-Insulator Set-OHW-OTA-2 | OTA-WKM-C0394 | OTA-WKM-C0394-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-02-18 12:32
10046986 | OTA-WKM-C-0394-0395-Conductor-OHW-OTA-2 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-18 12:36
10046986 | OTA-WKM-C-0394-0395-Conductor-OHW-OTA-2 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:36
10046986 | OTA-WKM-C-0394-0395-Conductor-OHW-OTA-2 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:36
10046987 | OTA-WKM-C-0394-0395-Conductor-OHW-OTA-1 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-18 12:36
10046987 | OTA-WKM-C-0394-0395-Conductor-OHW-OTA-1 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:36
10046987 | OTA-WKM-C-0394-0395-Conductor-OHW-OTA-1 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:36
10046988 | OTA-WKM-C-0394-0395-Earthwire-A0 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:37
10046988 | OTA-WKM-C-0394-0395-Earthwire-A0 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 12:37 | Surface pitting
13329878 | OTA-WKM-C-0394-0395-Earthwire-C0 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 | CA copied from EW A0 Feb/2026
13329878 | OTA-WKM-C-0394-0395-Earthwire-C0 | OTA-WKM-C0394-0395 | OTA-WKM-C0394-0395-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 | Surface pitting. CA copied from EW A0 Feb/2026
10046237 | OTA-WKM-C-0395-Tower | OTA-WKM-C0395 | OTA-WKM-C0395-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046237 | OTA-WKM-C-0395-Tower | OTA-WKM-C0395 | OTA-WKM-C0395-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046237 | OTA-WKM-C-0395-Tower | OTA-WKM-C0395 | OTA-WKM-C0395-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046237 | OTA-WKM-C-0395-Tower | OTA-WKM-C0395 | OTA-WKM-C0395-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046237 | OTA-WKM-C-0395-Tower | OTA-WKM-C0395 | OTA-WKM-C0395-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046237 | OTA-WKM-C-0395-Tower | OTA-WKM-C0395 | OTA-WKM-C0395-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-02-28 | Tower refurbishment up to MAD area
10046237 | OTA-WKM-C-0395-Tower | OTA-WKM-C0395 | OTA-WKM-C0395-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59 | Rated as per TP specs
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59 | Rated as per TP specs
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59 | Rated as per to specs
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59 | Rated as per TP specs
10046238 | OTA-WKM-C-0395-Tower Foundation | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 07:59
10046239 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 08:15
10046239 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:15
10046239 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 08:15
10046239 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:15 | Significant corrosion
10046240 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 08:05
10046240 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:05
10046240 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 08:05
10046240 | OTA-WKM-C-0395-Insulator Set-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:05
12058844 | OTA-WKM-C-0395-Earthwire HW Set | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-31 08:02 | Damper not plumbed properly
12058844 | OTA-WKM-C-0395-Earthwire HW Set | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-31 08:02
13073717 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:17
13073717 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:17
13073717 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:17
13073717 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0395 | OTA-WKM-C0395-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:17
13073718 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:19
13073718 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:19
13073718 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:19
13073718 | OTA-WKM-C-0395-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0395 | OTA-WKM-C0395-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:19
13228993 | OTA-WKM-C-0395-Earthwire Attachment | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-04-27
13228993 | OTA-WKM-C-0395-Earthwire Attachment | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-31 08:00
13228993 | OTA-WKM-C-0395-Earthwire Attachment | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-31 08:00
13228993 | OTA-WKM-C-0395-Earthwire Attachment | OTA-WKM-C0395 | OTA-WKM-C0395-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-04-27
10046989 | OTA-WKM-C-0395-0396-Conductor-OHW-OTA-2 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 08:22
10046989 | OTA-WKM-C-0395-0396-Conductor-OHW-OTA-2 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-20 | 1965 | COSE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 08:22
10046989 | OTA-WKM-C-0395-0396-Conductor-OHW-OTA-2 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:22
10046990 | OTA-WKM-C-0395-0396-Conductor-OHW-OTA-1 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 08:20
10046990 | OTA-WKM-C-0395-0396-Conductor-OHW-OTA-1 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-10 | 1965 | COSE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 08:20
10046990 | OTA-WKM-C-0395-0396-Conductor-OHW-OTA-1 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:20
10046991 | OTA-WKM-C-0395-0396-Earthwire-A0 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 08:25
10046991 | OTA-WKM-C-0395-0396-Earthwire-A0 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:25
13329879 | OTA-WKM-C-0395-0396-Earthwire-C0 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 | CA copied from EW A0 Feb/2026
13329879 | OTA-WKM-C-0395-0396-Earthwire-C0 | OTA-WKM-C0395-0396 | OTA-WKM-C0395-0396-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 | CA copied from EW A0 Feb/2026
10046242 | OTA-WKM-C-0396-Tower | OTA-WKM-C0396 | OTA-WKM-C0396-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046242 | OTA-WKM-C-0396-Tower | OTA-WKM-C0396 | OTA-WKM-C0396-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046242 | OTA-WKM-C-0396-Tower | OTA-WKM-C0396 | OTA-WKM-C0396-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046242 | OTA-WKM-C-0396-Tower | OTA-WKM-C0396 | OTA-WKM-C0396-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046242 | OTA-WKM-C-0396-Tower | OTA-WKM-C0396 | OTA-WKM-C0396-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046242 | OTA-WKM-C-0396-Tower | OTA-WKM-C0396 | OTA-WKM-C0396-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-03-01 | Tower refurbishment up to MAD area
10046242 | OTA-WKM-C-0396-Tower | OTA-WKM-C0396 | OTA-WKM-C0396-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
10046243 | OTA-WKM-C-0396-Tower Foundation | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:40
12058845 | OTA-WKM-C-0396-Earthwire HW Set | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-31 09:07
12058845 | OTA-WKM-C-0396-Earthwire HW Set | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 09:07
13040129 | OTA-WKM-C-0396-Earthwire Attachment | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-16 08:00 | Updating to 4 Readings
13040129 | OTA-WKM-C-0396-Earthwire Attachment | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 09:02
13040129 | OTA-WKM-C-0396-Earthwire Attachment | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 09:02
13040129 | OTA-WKM-C-0396-Earthwire Attachment | OTA-WKM-C0396 | OTA-WKM-C0396-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-16 08:00 | Updating to 4 Readings
13073719 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:05
13073719 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:05
13073719 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:05
13073719 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:05
13073720 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:07
13073720 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:07
13073720 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:07
13073720 | OTA-WKM-C-0396-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:07
13204568 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-31 08:58
13204568 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:58
13204568 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 08:58
13204568 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-1 | OTA-WKM-C0396 | OTA-WKM-C0396-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 08:58
13204569 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-07-31 09:01
13204569 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:01
13204569 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-07-31 09:01
13204569 | OTA-WKM-C-0396-Insulator Set-OHW-OTA-2 | OTA-WKM-C0396 | OTA-WKM-C0396-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:01
10046992 | OTA-WKM-C-0396-0397-Conductor-OHW-OTA-2 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046992 | OTA-WKM-C-0396-0397-Conductor-OHW-OTA-2 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-20 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046992 | OTA-WKM-C-0396-0397-Conductor-OHW-OTA-2 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046993 | OTA-WKM-C-0396-0397-Conductor-OHW-OTA-1 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046993 | OTA-WKM-C-0396-0397-Conductor-OHW-OTA-1 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-10 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046993 | OTA-WKM-C-0396-0397-Conductor-OHW-OTA-1 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046994 | OTA-WKM-C-0396-0397-Earthwire-A0 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046994 | OTA-WKM-C-0396-0397-Earthwire-A0 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 09:09
10046994 | OTA-WKM-C-0396-0397-Earthwire-A0 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-26 | CA
13329880 | OTA-WKM-C-0396-0397-Earthwire-C0 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-07-31 | CA copied from EW A0 Feb/2026
13329880 | OTA-WKM-C-0396-0397-Earthwire-C0 | OTA-WKM-C0396-0397 | OTA-WKM-C0396-0397-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-07-31 | CA copied from EW A0 Feb/2026
10046247 | OTA-WKM-C-0397-Tower | OTA-WKM-C0397 | OTA-WKM-C0397-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046247 | OTA-WKM-C-0397-Tower | OTA-WKM-C0397 | OTA-WKM-C0397-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046247 | OTA-WKM-C-0397-Tower | OTA-WKM-C0397 | OTA-WKM-C0397-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046247 | OTA-WKM-C-0397-Tower | OTA-WKM-C0397 | OTA-WKM-C0397-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046247 | OTA-WKM-C-0397-Tower | OTA-WKM-C0397 | OTA-WKM-C0397-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046247 | OTA-WKM-C-0397-Tower | OTA-WKM-C0397 | OTA-WKM-C0397-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 14:15
10046247 | OTA-WKM-C-0397-Tower | OTA-WKM-C0397 | OTA-WKM-C0397-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-12 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046248 | OTA-WKM-C-0397-Tower Foundation | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:17
10046251 | OTA-WKM-C-0397-Earthwire HW Set | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 13:57
10046251 | OTA-WKM-C-0397-Earthwire HW Set | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 13:57
13040130 | OTA-WKM-C-0397-Earthwire Attachment | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 | Replaced EW Hardware Armour Rods Att points both CCT's
13040130 | OTA-WKM-C-0397-Earthwire Attachment | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 | Replaced EW Hardware Armour Rods Att points both CCT's
13040130 | OTA-WKM-C-0397-Earthwire Attachment | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 | Replaced EW Hardware Armour Rods Att points both CCT's
13040130 | OTA-WKM-C-0397-Earthwire Attachment | OTA-WKM-C0397 | OTA-WKM-C0397-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 | Replaced EW Hardware Armour Rods Att points both CCT's
13073721 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:21
13073721 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:21
13073721 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:21
13073721 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:21
13073722 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:31
13073722 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:31
13073722 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:31
13073722 | OTA-WKM-C-0397-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:31
13285431 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285431 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285431 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285431 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-1 | OTA-WKM-C0397 | OTA-WKM-C0397-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285432 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285432 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285432 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285432 | OTA-WKM-C-0397-Insulator Set-OHW-OTA-2 | OTA-WKM-C0397 | OTA-WKM-C0397-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
10046995 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-2 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 14:38
10046995 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-2 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:38
10046995 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-2 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046995 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-2 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:38 | Significant corrosion
10046996 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-1 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 14:37
10046996 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-1 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:37
10046996 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-1 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2007-07-30 | Routine CA
10046996 | OTA-WKM-C-0397-0398-Conductor-OHW-OTA-1 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:37 | Significant corrosion
10046997 | OTA-WKM-C-0397-0398-Earthwire-A0 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:39
10046997 | OTA-WKM-C-0397-0398-Earthwire-A0 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 14:39 | Surface pitting
13329881 | OTA-WKM-C-0397-0398-Earthwire-C0 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | CA copied from EW A0 Feb/2026
13329881 | OTA-WKM-C-0397-0398-Earthwire-C0 | OTA-WKM-C0397-0398 | OTA-WKM-C0397-0398-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | Surface pitting. CA copied from EW A0 Feb/2026
10046252 | OTA-WKM-C-0398-Tower | OTA-WKM-C0398 | OTA-WKM-C0398-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-13 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046252 | OTA-WKM-C-0398-Tower | OTA-WKM-C0398 | OTA-WKM-C0398-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-13 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046252 | OTA-WKM-C-0398-Tower | OTA-WKM-C0398 | OTA-WKM-C0398-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-13 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046252 | OTA-WKM-C-0398-Tower | OTA-WKM-C0398 | OTA-WKM-C0398-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-13 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046252 | OTA-WKM-C-0398-Tower | OTA-WKM-C0398 | OTA-WKM-C0398-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-13 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046252 | OTA-WKM-C-0398-Tower | OTA-WKM-C0398 | OTA-WKM-C0398-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-03-01 | Tower refurbishment up to MAD area
10046252 | OTA-WKM-C-0398-Tower | OTA-WKM-C0398 | OTA-WKM-C0398-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-13 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Dug leg c
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Significant corrosion
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Dug leg c
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Significant corrosion
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Dug leg c
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Significant corrosion
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Dug leg c
10046253 | OTA-WKM-C-0398-Tower Foundation | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 10:20 | Significant corrosion
10046254 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-18 11:04
10046254 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:04
10046254 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:04
10046254 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:04 | Significant corrosion
10046255 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
10046255 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
10046255 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
10046255 | OTA-WKM-C-0398-Insulator Set-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03 | Significant corrosion
12058846 | OTA-WKM-C-0398-Earthwire HW Set | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03 | Wrong overlay
12058846 | OTA-WKM-C-0398-Earthwire HW Set | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03 | Wind wear
13040131 | OTA-WKM-C-0398-Earthwire Attachment | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-14 08:00 | Updating to 4 Readings
13040131 | OTA-WKM-C-0398-Earthwire Attachment | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
13040131 | OTA-WKM-C-0398-Earthwire Attachment | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03 | Wind wear
13040131 | OTA-WKM-C-0398-Earthwire Attachment | OTA-WKM-C0398 | OTA-WKM-C0398-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-14 08:00 | Updating to 4 Readings
13073723 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
13073723 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
13073723 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
13073723 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0398 | OTA-WKM-C0398-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:03
13073724 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:02
13073724 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:02
13073724 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:02
13073724 | OTA-WKM-C-0398-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0398 | OTA-WKM-C0398-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:02
10046998 | OTA-WKM-C-0398-0399-Conductor-OHW-OTA-2 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-04-17 07:55
10046998 | OTA-WKM-C-0398-0399-Conductor-OHW-OTA-2 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-04-17 07:55
10046998 | OTA-WKM-C-0398-0399-Conductor-OHW-OTA-2 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-04-17 07:55
10046999 | OTA-WKM-C-0398-0399-Conductor-OHW-OTA-1 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-04-17 07:55
10046999 | OTA-WKM-C-0398-0399-Conductor-OHW-OTA-1 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-04-17 07:55
10046999 | OTA-WKM-C-0398-0399-Conductor-OHW-OTA-1 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-02 | RSA2 25-26 Subconductor Spacer Replacement Project
10047000 | OTA-WKM-C-0398-0399-Earthwire-A0 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:04
10047000 | OTA-WKM-C-0398-0399-Earthwire-A0 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 11:04
10047000 | OTA-WKM-C-0398-0399-Earthwire-A0 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-21 | CA
13329882 | OTA-WKM-C-0398-0399-Earthwire-C0 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 | CA copied from EW A0 Feb/2026
13329882 | OTA-WKM-C-0398-0399-Earthwire-C0 | OTA-WKM-C0398-0399 | OTA-WKM-C0398-0399-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-02-18 | CA copied from EW A0 Feb/2026
10046257 | OTA-WKM-C-0399-Tower | OTA-WKM-C0399 | OTA-WKM-C0399-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-28 | Fitted anti-climb frame to tower. Tower not reassessed, ratings remain unchanged.
10046257 | OTA-WKM-C-0399-Tower | OTA-WKM-C0399 | OTA-WKM-C0399-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-28 | Fitted anti-climb frame to tower. Tower not reassessed, ratings remain unchanged.
10046257 | OTA-WKM-C-0399-Tower | OTA-WKM-C0399 | OTA-WKM-C0399-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-28 | Fitted anti-climb frame to tower. Tower not reassessed, ratings remain unchanged.
10046257 | OTA-WKM-C-0399-Tower | OTA-WKM-C0399 | OTA-WKM-C0399-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-28 | Fitted anti-climb frame to tower. Tower not reassessed, ratings remain unchanged.
10046257 | OTA-WKM-C-0399-Tower | OTA-WKM-C0399 | OTA-WKM-C0399-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-28 | Fitted anti-climb frame to tower. Tower not reassessed, ratings remain unchanged.
10046257 | OTA-WKM-C-0399-Tower | OTA-WKM-C0399 | OTA-WKM-C0399-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-12-22 | Tower refurbishment up to MAD area
10046257 | OTA-WKM-C-0399-Tower | OTA-WKM-C0399 | OTA-WKM-C0399-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-28 | Fitted anti-climb frame to tower. Tower not reassessed, ratings remain unchanged.
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046258 | OTA-WKM-C-0399-Tower Foundation | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 11:31
10046259 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2025-06-30 13:48
10046259 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-06-30 13:46 | Wind wear
10046259 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-06-30 13:47 | Significant corrosion on socket clevis
10046259 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-06-30 13:47 | Significant corrosion on caps and pins
10046260 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 12:05
10046260 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:05 | Wind wear
10046260 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:05 | Significant corrosion
10046260 | OTA-WKM-C-0399-Insulator Set-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:05 | Significant corrosion
10046261 | OTA-WKM-C-0399-Earthwire HW Set | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:13 | Wrong overlay
10046261 | OTA-WKM-C-0399-Earthwire HW Set | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:13
13040132 | OTA-WKM-C-0399-Earthwire Attachment | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:12
13040132 | OTA-WKM-C-0399-Earthwire Attachment | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:12
13040132 | OTA-WKM-C-0399-Earthwire Attachment | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:12
13040132 | OTA-WKM-C-0399-Earthwire Attachment | OTA-WKM-C0399 | OTA-WKM-C0399-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:12
13073725 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:04 | Wind wear
13073725 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:04
13073725 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:04
13073725 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0399 | OTA-WKM-C0399-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:04 | Significant corrosion
13073726 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:13 | Wind wear
13073726 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:13
13073726 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:13
13073726 | OTA-WKM-C-0399-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0399 | OTA-WKM-C0399-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:13
10047001 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-2 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 12:38
10047001 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-2 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:38
10047001 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-2 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-09 | Routine CA
10047001 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-2 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:38 | Significant corrosion
10047002 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-1 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 12:38
10047002 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-1 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:38
10047002 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-1 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-09 | Routine CA
10047002 | OTA-WKM-C-0399-0400-Conductor-OHW-OTA-1 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-30 | RSA2 25-26 Subconductor Spacer Replacement Project
10047003 | OTA-WKM-C-0399-0400-Earthwire-A0 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:08
10047003 | OTA-WKM-C-0399-0400-Earthwire-A0 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 12:08 | Surface pitting
10047003 | OTA-WKM-C-0399-0400-Earthwire-A0 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-21 | CA
10047003 | OTA-WKM-C-0399-0400-Earthwire-A0 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-08-21 | CA
13329883 | OTA-WKM-C-0399-0400-Earthwire-C0 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | CA copied from EW A0 Feb/2026
13329883 | OTA-WKM-C-0399-0400-Earthwire-C0 | OTA-WKM-C0399-0400 | OTA-WKM-C0399-0400-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | Surface pitting. CA copied from EW A0 Feb/2026
10046262 | OTA-WKM-C-0400-Tower | OTA-WKM-C0400 | OTA-WKM-C0400-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | "CA - Ponding around concrete foundation 2m x 2m x 300mm, SWL Attachment Steel rusty on all phases"
10046262 | OTA-WKM-C-0400-Tower | OTA-WKM-C0400 | OTA-WKM-C0400-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | "CA - Ponding around concrete foundation 2m x 2m x 300mm, SWL Attachment Steel rusty on all phases"
10046262 | OTA-WKM-C-0400-Tower | OTA-WKM-C0400 | OTA-WKM-C0400-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | "CA - Ponding around concrete foundation 2m x 2m x 300mm, SWL Attachment Steel rusty on all phases"
10046262 | OTA-WKM-C-0400-Tower | OTA-WKM-C0400 | OTA-WKM-C0400-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | "CA - Ponding around concrete foundation 2m x 2m x 300mm, SWL Attachment Steel rusty on all phases"
10046262 | OTA-WKM-C-0400-Tower | OTA-WKM-C0400 | OTA-WKM-C0400-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | "CA - Ponding around concrete foundation 2m x 2m x 300mm, SWL Attachment Steel rusty on all phases"
10046262 | OTA-WKM-C-0400-Tower | OTA-WKM-C0400 | OTA-WKM-C0400-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-12-22 | Tower refurbishment up to MAD area
10046262 | OTA-WKM-C-0400-Tower | OTA-WKM-C0400 | OTA-WKM-C0400-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | "CA - Ponding around concrete foundation 2m x 2m x 300mm, SWL Attachment Steel rusty on all phases"
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 09:40 | Coded as per TP specs
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:40 | Blasted and painted
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 09:40 | Coded as per TP specs
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:40 | Blasted and painted
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 09:40 | Coded as per TP specs
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:40 | Blasted and painted
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2023-01-04 09:40 | Coded as per TP specs
10046263 | OTA-WKM-C-0400-Tower Foundation | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:40 | Blasted and painted
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:23
10046264 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 | 1965 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:23
10046266 | OTA-WKM-C-0400-Earthwire HW Set | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:35 | Preformed rod is wrong overlay
10046266 | OTA-WKM-C-0400-Earthwire HW Set | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2023-01-04 10:35
13040133 | OTA-WKM-C-0400-Earthwire Attachment | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-08-22 08:00 | Updating to 4 Readings
13040133 | OTA-WKM-C-0400-Earthwire Attachment | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:24
13040133 | OTA-WKM-C-0400-Earthwire Attachment | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:24
13040133 | OTA-WKM-C-0400-Earthwire Attachment | OTA-WKM-C0400 | OTA-WKM-C0400-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-08-22 08:00 | Updating to 4 Readings
13216919 | OTA-WKM-C-0400-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:51
13216919 | OTA-WKM-C-0400-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0400 | OTA-WKM-C0400-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:51 | Painted
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244598 | OTA-WKM-C-0400-Insulator Set-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:49
13244599 | OTA-WKM-C-0400-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:52
13244599 | OTA-WKM-C-0400-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:52
13244599 | OTA-WKM-C-0400-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0400 | OTA-WKM-C0400-10 | 2022 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-04 09:52
10047004 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-2 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 10:56
10047004 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-2 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:56
10047004 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-2 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - 1 x ERD B-Phase inside
10047004 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-2 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - 1 x ERD B-Phase inside
10047004 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-2 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:56 | Significant corrosion
10047004 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-2 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-20 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:56 | Significant corrosion
10047005 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-1 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2023-01-04 10:56
10047005 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-1 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:56
10047005 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-1 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - 1 x ERD B-Phase inside
10047005 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-1 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-21 | CA - 1 x ERD B-Phase inside
10047005 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-1 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-02 | RSA2 25-26 Subconductor Spacer Replacement Project
10047005 | OTA-WKM-C-0400-0401-Conductor-OHW-OTA-1 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-10 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:56 | Significant corrosion
10047006 | OTA-WKM-C-0400-0401-Earthwire-A0 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:39
10047006 | OTA-WKM-C-0400-0401-Earthwire-A0 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 10:39 | Surface pitting on jumpers
10047006 | OTA-WKM-C-0400-0401-Earthwire-A0 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-21 | CA
13329884 | OTA-WKM-C-0400-0401-Earthwire-C0 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | CA copied from EW A0 Feb/2026
13329884 | OTA-WKM-C-0400-0401-Earthwire-C0 | OTA-WKM-C0400-0401 | OTA-WKM-C0400-0401-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-01-04 | Surface pitting on jumpers. CA copied from EW A0 Feb/2026
10046267 | OTA-WKM-C-0401-Tower | OTA-WKM-C0401 | OTA-WKM-C0401-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046267 | OTA-WKM-C-0401-Tower | OTA-WKM-C0401 | OTA-WKM-C0401-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046267 | OTA-WKM-C-0401-Tower | OTA-WKM-C0401 | OTA-WKM-C0401-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046267 | OTA-WKM-C-0401-Tower | OTA-WKM-C0401 | OTA-WKM-C0401-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046267 | OTA-WKM-C-0401-Tower | OTA-WKM-C0401 | OTA-WKM-C0401-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046267 | OTA-WKM-C-0401-Tower | OTA-WKM-C0401 | OTA-WKM-C0401-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-06-14 | Tower refurbishment up to MAD area
10046267 | OTA-WKM-C-0401-Tower | OTA-WKM-C0401 | OTA-WKM-C0401-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 15:35
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 15:35
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 15:35 | Concrete was damage
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 15:35
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 15:35
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 15:35
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 15:35
10046268 | OTA-WKM-C-0401-Tower Foundation | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 15:35
12058847 | OTA-WKM-C-0401-Earthwire HW Set | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:42 | Surface pitting
12058847 | OTA-WKM-C-0401-Earthwire HW Set | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 16:42
13040134 | OTA-WKM-C-0401-Earthwire Attachment | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2017-05-16
13040134 | OTA-WKM-C-0401-Earthwire Attachment | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 15:42
13040134 | OTA-WKM-C-0401-Earthwire Attachment | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 15:42
13040134 | OTA-WKM-C-0401-Earthwire Attachment | OTA-WKM-C0401 | OTA-WKM-C0401-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2017-05-16
13073730 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:45 | Wind wear
13073730 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:45
13073730 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:45
13073730 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:45
13285433 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 TL Insulators 24-25
13285433 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 TL Insulators 24-25
13285433 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 TL Insulators 24-25
13285433 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 TL Insulators 24-25
13285434 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285434 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285434 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285434 | OTA-WKM-C-0401-Insulator Set-OHW-OTA-2 | OTA-WKM-C0401 | OTA-WKM-C0401-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13286390 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 Attach Point Replacement 24-25
13286390 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 Attach Point Replacement 24-25
13286390 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 Attach Point Replacement 24-25
13286390 | OTA-WKM-C-0401-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0401 | OTA-WKM-C0401-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | RSA2 Attach Point Replacement 24-25
10047007 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-2 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 16:41
10047007 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-2 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:41
10047007 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-2 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10047007 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-2 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:41 | Significant corrosion on u bolt nuts
10047008 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-1 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 16:40
10047008 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-1 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:40
10047008 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-1 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10047008 | OTA-WKM-C-0401-0402-Conductor-OHW-OTA-1 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:40 | Significant corrosion on u bolt nuts
10047009 | OTA-WKM-C-0401-0402-Earthwire-A0 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:40
10047009 | OTA-WKM-C-0401-0402-Earthwire-A0 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:40
13329885 | OTA-WKM-C-0401-0402-Earthwire-C0 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | CA copied from EW A0 Feb/2026
13329885 | OTA-WKM-C-0401-0402-Earthwire-C0 | OTA-WKM-C0401-0402 | OTA-WKM-C0401-0402-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | CA copied from EW A0 Feb/2026
10046272 | OTA-WKM-C-0402-Tower | OTA-WKM-C0402 | OTA-WKM-C0402-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046272 | OTA-WKM-C-0402-Tower | OTA-WKM-C0402 | OTA-WKM-C0402-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046272 | OTA-WKM-C-0402-Tower | OTA-WKM-C0402 | OTA-WKM-C0402-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046272 | OTA-WKM-C-0402-Tower | OTA-WKM-C0402 | OTA-WKM-C0402-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046272 | OTA-WKM-C-0402-Tower | OTA-WKM-C0402 | OTA-WKM-C0402-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046272 | OTA-WKM-C-0402-Tower | OTA-WKM-C0402 | OTA-WKM-C0402-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-06-15 | Tower refurbishment up to MAD area
10046272 | OTA-WKM-C-0402-Tower | OTA-WKM-C0402 | OTA-WKM-C0402-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-18 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046274 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 13:46
10046274 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:46
10046274 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:46 | Significant corrosion on u bolt nut
10046274 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:46 | Significant corrosion on caps and pins
10046275 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 13:45
10046275 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:45 | Wind wear
10046275 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:45 | Significant corrosion on u bolt nut
10046275 | OTA-WKM-C-0402-Insulator Set-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:45 | Significant corrosion on caps and pins
10046276 | OTA-WKM-C-0402-Earthwire HW Set | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-05-18 11:27
10046276 | OTA-WKM-C-0402-Earthwire HW Set | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-18 11:27 | Replaced the ew hardware
13040135 | OTA-WKM-C-0402-Earthwire Attachment | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-18 13:11 | New attachment point
13040135 | OTA-WKM-C-0402-Earthwire Attachment | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-18 13:11 | Replace the attachment point nuts and bolts
13040135 | OTA-WKM-C-0402-Earthwire Attachment | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-18 13:10 | Replaced the attachment point steel
13040135 | OTA-WKM-C-0402-Earthwire Attachment | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-18 13:12 | New attachment point through bolt and nuts
13073731 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47 | Wind wear
13073731 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47
13073731 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47
13073731 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0402 | OTA-WKM-C0402-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47
13073732 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47
13073732 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47
13073732 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47
13073732 | OTA-WKM-C-0402-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0402 | OTA-WKM-C0402-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:47
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
13285024 | OTA-WKM-C-0402-Tower Foundation | OTA-WKM-C0402 | OTA-WKM-C0402-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-22 | Replaced during RSA2 Grillage Refurb 24-25 project
10047010 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-2 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 13:15
10047010 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-2 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:15
10047010 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-2 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10047010 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-2 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:15
10047011 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-1 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 13:14
10047011 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-1 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:14
10047011 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-1 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10047011 | OTA-WKM-C-0402-0403-Conductor-OHW-OTA-1 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 13:14
10047012 | OTA-WKM-C-0402-0403-Earthwire-A0 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:38
10047012 | OTA-WKM-C-0402-0403-Earthwire-A0 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:38
10047012 | OTA-WKM-C-0402-0403-Earthwire-A0 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-20 | CA
13329886 | OTA-WKM-C-0402-0403-Earthwire-C0 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
13329886 | OTA-WKM-C-0402-0403-Earthwire-C0 | OTA-WKM-C0402-0403 | OTA-WKM-C0402-0403-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
10046277 | OTA-WKM-C-0403-Tower | OTA-WKM-C0403 | OTA-WKM-C0403-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046277 | OTA-WKM-C-0403-Tower | OTA-WKM-C0403 | OTA-WKM-C0403-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046277 | OTA-WKM-C-0403-Tower | OTA-WKM-C0403 | OTA-WKM-C0403-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046277 | OTA-WKM-C-0403-Tower | OTA-WKM-C0403 | OTA-WKM-C0403-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046277 | OTA-WKM-C-0403-Tower | OTA-WKM-C0403 | OTA-WKM-C0403-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046277 | OTA-WKM-C-0403-Tower | OTA-WKM-C0403 | OTA-WKM-C0403-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-06-15 | Tower refurbishment up to MAD area
10046277 | OTA-WKM-C-0403-Tower | OTA-WKM-C0403 | OTA-WKM-C0403-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-08 | Routine CA
10046279 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 11:58
10046279 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:58 | Wind wear
10046279 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:58 | Significant corrosion on u bolt and nut
10046279 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:58 | Significant corrosion on caps and pins
10046280 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 11:57
10046280 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:57 | Wind wear
10046280 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:57 | Significant corrosion on u bolt and nut
10046280 | OTA-WKM-C-0403-Insulator Set-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 11:57 | Significant corrosion on caps and pins
10046281 | OTA-WKM-C-0403-Earthwire HW Set | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-05-11 12:28
10046281 | OTA-WKM-C-0403-Earthwire HW Set | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 12:28
13040136 | OTA-WKM-C-0403-Earthwire Attachment | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 12:25 | New attachment point
13040136 | OTA-WKM-C-0403-Earthwire Attachment | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 12:24 | Replaced the bolts
13040136 | OTA-WKM-C-0403-Earthwire Attachment | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 12:24 | Replaced the attachment point steel
13040136 | OTA-WKM-C-0403-Earthwire Attachment | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 12:25 | New
13073733 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:00 | Wind wear
13073733 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:00
13073733 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:00 | Wind wear
13073733 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0403 | OTA-WKM-C0403-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:00 | Significant corrosion
13073734 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:01 | Wind wear
13073734 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:01
13073734 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:01 | Wind wear
13073734 | OTA-WKM-C-0403-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0403 | OTA-WKM-C0403-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:01 | Significant corrosion
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
13285025 | OTA-WKM-C-0403-Tower Foundation | OTA-WKM-C0403 | OTA-WKM-C0403-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-11-29 | Replaced during RSA2 Grillage Refurb 24-25 project
10047013 | OTA-WKM-C-0403-0404-Conductor-OHW-OTA-2 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 12:03
10047013 | OTA-WKM-C-0403-0404-Conductor-OHW-OTA-2 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:03
10047013 | OTA-WKM-C-0403-0404-Conductor-OHW-OTA-2 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:03
10047014 | OTA-WKM-C-0403-0404-Conductor-OHW-OTA-1 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 12:02
10047014 | OTA-WKM-C-0403-0404-Conductor-OHW-OTA-1 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:02
10047014 | OTA-WKM-C-0403-0404-Conductor-OHW-OTA-1 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:02
10047015 | OTA-WKM-C-0403-0404-Earthwire-A0 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:04
10047015 | OTA-WKM-C-0403-0404-Earthwire-A0 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 12:04 | Surface pitting both EW
13329887 | OTA-WKM-C-0403-0404-Earthwire-C0 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
13329887 | OTA-WKM-C-0403-0404-Earthwire-C0 | OTA-WKM-C0403-0404 | OTA-WKM-C0403-0404-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | Surface pitting both EW. CA copied from EW A0 Feb/2026
10046282 | OTA-WKM-C-0404-Tower | OTA-WKM-C0404 | OTA-WKM-C0404-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046282 | OTA-WKM-C-0404-Tower | OTA-WKM-C0404 | OTA-WKM-C0404-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046282 | OTA-WKM-C-0404-Tower | OTA-WKM-C0404 | OTA-WKM-C0404-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046282 | OTA-WKM-C-0404-Tower | OTA-WKM-C0404 | OTA-WKM-C0404-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046282 | OTA-WKM-C-0404-Tower | OTA-WKM-C0404 | OTA-WKM-C0404-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046282 | OTA-WKM-C-0404-Tower | OTA-WKM-C0404 | OTA-WKM-C0404-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-06-15 | Tower refurbishment up to MAD area
10046282 | OTA-WKM-C-0404-Tower | OTA-WKM-C0404 | OTA-WKM-C0404-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02 | Significant corrosion dug leg c
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02 | Significant corrosion dug leg c
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02 | Significant corrosion dug leg c
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02 | Significant corrosion dug leg c
10046283 | OTA-WKM-C-0404-Tower Foundation | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:02
10046286 | OTA-WKM-C-0404-Earthwire HW Set | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 07:52
10046286 | OTA-WKM-C-0404-Earthwire HW Set | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 07:53
13040137 | OTA-WKM-C-0404-Earthwire Attachment | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 | Replaced EW Att point during Routine maintenance Work
13040137 | OTA-WKM-C-0404-Earthwire Attachment | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 | Replaced EW Att point during Routine maintenance Work
13040137 | OTA-WKM-C-0404-Earthwire Attachment | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 | Replaced EW Att point during Routine maintenance Work
13040137 | OTA-WKM-C-0404-Earthwire Attachment | OTA-WKM-C0404 | OTA-WKM-C0404-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 | Replaced EW Att point during Routine maintenance Work
13073735 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13073735 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13073735 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13073735 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13073736 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13073736 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13073736 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13073736 | OTA-WKM-C-0404-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:31
13285435 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Reins Project
13285435 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Reins Project
13285435 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Reins Project
13285435 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-1 | OTA-WKM-C0404 | OTA-WKM-C0404-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Reins Project
13285436 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285436 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285436 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285436 | OTA-WKM-C-0404-Insulator Set-OHW-OTA-2 | OTA-WKM-C0404 | OTA-WKM-C0404-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
10047016 | OTA-WKM-C-0404-0405-Conductor-OHW-OTA-2 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 09:27
10047016 | OTA-WKM-C-0404-0405-Conductor-OHW-OTA-2 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:27
10047016 | OTA-WKM-C-0404-0405-Conductor-OHW-OTA-2 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:27
10047017 | OTA-WKM-C-0404-0405-Conductor-OHW-OTA-1 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 09:26
10047017 | OTA-WKM-C-0404-0405-Conductor-OHW-OTA-1 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:26
10047017 | OTA-WKM-C-0404-0405-Conductor-OHW-OTA-1 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:26
10047018 | OTA-WKM-C-0404-0405-Earthwire-A0 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:25
10047018 | OTA-WKM-C-0404-0405-Earthwire-A0 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:25 | Surface pitting
13329888 | OTA-WKM-C-0404-0405-Earthwire-C0 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
13329888 | OTA-WKM-C-0404-0405-Earthwire-C0 | OTA-WKM-C0404-0405 | OTA-WKM-C0404-0405-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | Surface pitting. CA copied from EW A0 Feb/2026
10046287 | OTA-WKM-C-0405-Tower | OTA-WKM-C0405 | OTA-WKM-C0405-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046287 | OTA-WKM-C-0405-Tower | OTA-WKM-C0405 | OTA-WKM-C0405-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046287 | OTA-WKM-C-0405-Tower | OTA-WKM-C0405 | OTA-WKM-C0405-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046287 | OTA-WKM-C-0405-Tower | OTA-WKM-C0405 | OTA-WKM-C0405-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046287 | OTA-WKM-C-0405-Tower | OTA-WKM-C0405 | OTA-WKM-C0405-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046287 | OTA-WKM-C-0405-Tower | OTA-WKM-C0405 | OTA-WKM-C0405-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-03-25 | Tower refurbishment up to MAD area
10046287 | OTA-WKM-C-0405-Tower | OTA-WKM-C0405 | OTA-WKM-C0405-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046289 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 10:42
10046289 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:42 | Wind wear
10046289 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:42 | Significant corrosion on u bolt and nut
10046289 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:42 | Significant corrosion on caps and pins
10046290 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 10:42
10046290 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:42 | Wind wear
10046290 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:42 | Significant corrosion on u bolt nut
10046290 | OTA-WKM-C-0405-Insulator Set-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:42 | Significant corrosion on caps and pins
10046291 | OTA-WKM-C-0405-Earthwire HW Set | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-05-17 15:58
10046291 | OTA-WKM-C-0405-Earthwire HW Set | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-17 15:58 | Replaced the ew hardware
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
12008357 | OTA-WKM-C-0405-Tower Foundation | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 09:55
13040138 | OTA-WKM-C-0405-Earthwire Attachment | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-17 15:52 | New attachment point
13040138 | OTA-WKM-C-0405-Earthwire Attachment | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-17 15:51 | Replaced the bolts and nut
13040138 | OTA-WKM-C-0405-Earthwire Attachment | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-17 15:51 | Replaced the attachment point steel
13040138 | OTA-WKM-C-0405-Earthwire Attachment | OTA-WKM-C0405 | OTA-WKM-C0405-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-17 15:52 | New
13073737 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:43 | Wind wear
13073737 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:43
13073737 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:43 | Wind wear
13073737 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0405 | OTA-WKM-C0405-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:43 | Significant corrosion
13073738 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:44 | Wind wear
13073738 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:44
13073738 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:44 | Wind wear
13073738 | OTA-WKM-C-0405-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0405 | OTA-WKM-C0405-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:44 | Significant corrosion
10047019 | OTA-WKM-C-0405-0406-Conductor-OHW-OTA-2 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 09:52
10047019 | OTA-WKM-C-0405-0406-Conductor-OHW-OTA-2 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:52
10047019 | OTA-WKM-C-0405-0406-Conductor-OHW-OTA-2 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-15 | RSA2 25-26 Subconductor Spacer Replacement Project
10047020 | OTA-WKM-C-0405-0406-Conductor-OHW-OTA-1 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 09:51
10047020 | OTA-WKM-C-0405-0406-Conductor-OHW-OTA-1 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 09:51
10047020 | OTA-WKM-C-0405-0406-Conductor-OHW-OTA-1 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | RSA2 25-26 Subconductor Spacer Replacement Project
10047021 | OTA-WKM-C-0405-0406-Earthwire-A0 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:49
10047021 | OTA-WKM-C-0405-0406-Earthwire-A0 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 10:49 | Surface pitting of strand
13329889 | OTA-WKM-C-0405-0406-Earthwire-C0 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
13329889 | OTA-WKM-C-0405-0406-Earthwire-C0 | OTA-WKM-C0405-0406 | OTA-WKM-C0405-0406-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | Surface pitting of strand. CA copied from EW A0 Feb/2026
10046292 | OTA-WKM-C-0406-Tower | OTA-WKM-C0406 | OTA-WKM-C0406-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046292 | OTA-WKM-C-0406-Tower | OTA-WKM-C0406 | OTA-WKM-C0406-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046292 | OTA-WKM-C-0406-Tower | OTA-WKM-C0406 | OTA-WKM-C0406-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046292 | OTA-WKM-C-0406-Tower | OTA-WKM-C0406 | OTA-WKM-C0406-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046292 | OTA-WKM-C-0406-Tower | OTA-WKM-C0406 | OTA-WKM-C0406-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046292 | OTA-WKM-C-0406-Tower | OTA-WKM-C0406 | OTA-WKM-C0406-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-03-25 | Tower refurbishment up to MAD area
10046292 | OTA-WKM-C-0406-Tower | OTA-WKM-C0406 | OTA-WKM-C0406-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54 | Significant corrosion dug leg a
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54 | Significant corrosion dug leg a
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54 | Significant corrosion
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54
10046293 | OTA-WKM-C-0406-Tower Foundation | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:54 | Significant corrosion
12058848 | OTA-WKM-C-0406-Earthwire HW Set | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-08 15:00
12058848 | OTA-WKM-C-0406-Earthwire HW Set | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-08 15:00
13073739 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58 | Wind wear
13073739 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58
13073739 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58 | Wind wear
13073739 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58
13073740 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58 | Wind wear
13073740 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58
13073740 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58 | Wind wear
13073740 | OTA-WKM-C-0406-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:58
13216920 | OTA-WKM-C-0406-Earthwire Attachment | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 14:18
13216920 | OTA-WKM-C-0406-Earthwire Attachment | OTA-WKM-C0406 | OTA-WKM-C0406-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-08 14:18
13285437 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285437 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285437 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285437 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-1 | OTA-WKM-C0406 | OTA-WKM-C0406-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285438 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
13285438 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
13285438 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
13285438 | OTA-WKM-C-0406-Insulator Set-OHW-OTA-2 | OTA-WKM-C0406 | OTA-WKM-C0406-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
10047022 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-2 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 14:26
10047022 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-2 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:26
10047022 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-2 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10047022 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-2 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-16 | RSA2 25-26 Subconductor Spacer Replacement Project
10047023 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-1 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 14:25
10047023 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-1 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 14:25
10047023 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-1 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-30 | Routine CA
10047023 | OTA-WKM-C-0406-0407-Conductor-OHW-OTA-1 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | RSA2 25-26 Subconductor Spacer Replacement Project
10047024 | OTA-WKM-C-0406-0407-Earthwire-A0 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:02
10047024 | OTA-WKM-C-0406-0407-Earthwire-A0 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:02
10047024 | OTA-WKM-C-0406-0407-Earthwire-A0 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-19 | CA
13329890 | OTA-WKM-C-0406-0407-Earthwire-C0 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
13329890 | OTA-WKM-C-0406-0407-Earthwire-C0 | OTA-WKM-C0406-0407 | OTA-WKM-C0406-0407-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
10046297 | OTA-WKM-C-0407-Tower | OTA-WKM-C0407 | OTA-WKM-C0407-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Some minor steel on body rusty, Insulator attachments very rusty, E/W Attaachment plates with metal loss R/C"
10046297 | OTA-WKM-C-0407-Tower | OTA-WKM-C0407 | OTA-WKM-C0407-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Some minor steel on body rusty, Insulator attachments very rusty, E/W Attaachment plates with metal loss R/C"
10046297 | OTA-WKM-C-0407-Tower | OTA-WKM-C0407 | OTA-WKM-C0407-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Some minor steel on body rusty, Insulator attachments very rusty, E/W Attaachment plates with metal loss R/C"
10046297 | OTA-WKM-C-0407-Tower | OTA-WKM-C0407 | OTA-WKM-C0407-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Some minor steel on body rusty, Insulator attachments very rusty, E/W Attaachment plates with metal loss R/C"
10046297 | OTA-WKM-C-0407-Tower | OTA-WKM-C0407 | OTA-WKM-C0407-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Some minor steel on body rusty, Insulator attachments very rusty, E/W Attaachment plates with metal loss R/C"
10046297 | OTA-WKM-C-0407-Tower | OTA-WKM-C0407 | OTA-WKM-C0407-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2021-12-22 | Tower refurbishment up to MAD area
10046297 | OTA-WKM-C-0407-Tower | OTA-WKM-C0407 | OTA-WKM-C0407-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | "CA - Some minor steel on body rusty, Insulator attachments very rusty, E/W Attaachment plates with metal loss R/C"
10332813 | OTA-WKM-C-0407-Earthwire HW Set | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 13:31
10332813 | OTA-WKM-C-0407-Earthwire HW Set | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 13:31
13040140 | OTA-WKM-C-0407-Earthwire Attachment | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-15 08:00 | Updating to 4 Readings
13040140 | OTA-WKM-C-0407-Earthwire Attachment | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 13:30
13040140 | OTA-WKM-C-0407-Earthwire Attachment | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 13:30
13040140 | OTA-WKM-C-0407-Earthwire Attachment | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-15 08:00 | Updating to 4 Readings
13073741 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:12 | Wind wear
13073741 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:12
13073741 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:12
13073741 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:12 | Significant corrosion on bolt and nut
13073742 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:13 | Wind wear
13073742 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:13
13073742 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:13
13073742 | OTA-WKM-C-0407-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:13 | Significant corrosion on bolt and nut
13204570 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-12-07 13:09
13204570 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 13:09
13204570 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 13:09
13204570 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-2 | OTA-WKM-C0407 | OTA-WKM-C0407-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 13:09
13216804 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-12-07 13:08
13216804 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 13:08
13216804 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 13:08
13216804 | OTA-WKM-C-0407-Insulator Set-OHW-OTA-1 | OTA-WKM-C0407 | OTA-WKM-C0407-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 13:08
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
13285027 | OTA-WKM-C-0407-Tower Foundation | OTA-WKM-C0407 | OTA-WKM-C0407-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-09 | Replaced during RSA2 Grillage Refurb 24-25 project
10047025 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-2 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 13:20
10047025 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-2 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-20 | 1965 | COSE_DAMPER COND | Damper Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 13:20
10047025 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-2 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA
10047025 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-2 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-16 | RSA2 25-26 Subconductor Spacer Replacement Project
10047026 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-1 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 13:20
10047026 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-1 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-10 | 1965 | COSE_DAMPER COND | Damper Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 13:20
10047026 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-1 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA
10047026 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-1 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-10 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-12 | CA
10047026 | OTA-WKM-C-0407-0408-Conductor-OHW-OTA-1 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | RSA2 25-26 Subconductor Spacer Replacement Project
10047027 | OTA-WKM-C-0407-0408-Earthwire-A0 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 13:22
10047027 | OTA-WKM-C-0407-0408-Earthwire-A0 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 13:22
13329891 | OTA-WKM-C-0407-0408-Earthwire-C0 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 | CA copied from EW A0 Feb/2026
13329891 | OTA-WKM-C-0407-0408-Earthwire-C0 | OTA-WKM-C0407-0408 | OTA-WKM-C0407-0408-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 | CA copied from EW A0 Feb/2026
10046302 | OTA-WKM-C-0408-Tower | OTA-WKM-C0408 | OTA-WKM-C0408-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046302 | OTA-WKM-C-0408-Tower | OTA-WKM-C0408 | OTA-WKM-C0408-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046302 | OTA-WKM-C-0408-Tower | OTA-WKM-C0408 | OTA-WKM-C0408-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046302 | OTA-WKM-C-0408-Tower | OTA-WKM-C0408 | OTA-WKM-C0408-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046302 | OTA-WKM-C-0408-Tower | OTA-WKM-C0408 | OTA-WKM-C0408-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046302 | OTA-WKM-C-0408-Tower | OTA-WKM-C0408 | OTA-WKM-C0408-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 19:20
10046302 | OTA-WKM-C-0408-Tower | OTA-WKM-C0408 | OTA-WKM-C0408-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-31 | Routine CA
10046306 | OTA-WKM-C-0408-Earthwire HW Set | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:06
10046306 | OTA-WKM-C-0408-Earthwire HW Set | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:06
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285028 | OTA-WKM-C-0408-Tower Foundation | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-10 | Replaced during RSA2 Grillage Refurb 24-25 project
13285439 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285439 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285439 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285439 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285440 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 19:28
13285440 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 19:28
13285440 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 19:28
13285440 | OTA-WKM-C-0408-Insulator Set-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 19:28
13286391 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 20:50
13286391 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 20:50
13286391 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 20:49
13286391 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0408 | OTA-WKM-C0408-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 20:50
13286392 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Att Pt Project
13286392 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Att Pt Project
13286392 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Att Pt Project
13286392 | OTA-WKM-C-0408-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0408 | OTA-WKM-C0408-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Att Pt Project
13286462 | OTA-WKM-C-0408-Earthwire Attachment | OTA-WKM-C0408 | OTA-WKM-C0408-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Att Pt Project
10047028 | OTA-WKM-C-0408-0409-Conductor-OHW-OTA-2 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 14:54
10047028 | OTA-WKM-C-0408-0409-Conductor-OHW-OTA-2 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:54
10047028 | OTA-WKM-C-0408-0409-Conductor-OHW-OTA-2 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:54
10047029 | OTA-WKM-C-0408-0409-Conductor-OHW-OTA-1 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 14:55
10047029 | OTA-WKM-C-0408-0409-Conductor-OHW-OTA-1 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:55
10047029 | OTA-WKM-C-0408-0409-Conductor-OHW-OTA-1 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:55
10047030 | OTA-WKM-C-0408-0409-Earthwire-A0 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:31
10047030 | OTA-WKM-C-0408-0409-Earthwire-A0 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 14:31
13329892 | OTA-WKM-C-0408-0409-Earthwire-C0 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 | CA copied from EW A0 Feb/2026
13329892 | OTA-WKM-C-0408-0409-Earthwire-C0 | OTA-WKM-C0408-0409 | OTA-WKM-C0408-0409-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 | CA copied from EW A0 Feb/2026
10046307 | OTA-WKM-C-0409-Tower | OTA-WKM-C0409 | OTA-WKM-C0409-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W attachment plates have metal loss R/C
10046307 | OTA-WKM-C-0409-Tower | OTA-WKM-C0409 | OTA-WKM-C0409-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W attachment plates have metal loss R/C
10046307 | OTA-WKM-C-0409-Tower | OTA-WKM-C0409 | OTA-WKM-C0409-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W attachment plates have metal loss R/C
10046307 | OTA-WKM-C-0409-Tower | OTA-WKM-C0409 | OTA-WKM-C0409-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W attachment plates have metal loss R/C
10046307 | OTA-WKM-C-0409-Tower | OTA-WKM-C0409 | OTA-WKM-C0409-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W attachment plates have metal loss R/C
10046307 | OTA-WKM-C-0409-Tower | OTA-WKM-C0409 | OTA-WKM-C0409-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 11:25
10046307 | OTA-WKM-C-0409-Tower | OTA-WKM-C0409 | OTA-WKM-C0409-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W attachment plates have metal loss R/C
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51 | Significant corrosion dug leg c
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51 | Significant corrosion dug leg c
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51 | Significant corrosion dug leg c
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51
10046308 | OTA-WKM-C-0409-Tower Foundation | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:51 | Significant corrosion dug leg c
10332814 | OTA-WKM-C-0409-Earthwire HW Set | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-09 09:41 | Wrong overly
10332814 | OTA-WKM-C-0409-Earthwire HW Set | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-09 09:41
13040142 | OTA-WKM-C-0409-Earthwire Attachment | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-19 08:00 | Updating to 4 Readings
13040142 | OTA-WKM-C-0409-Earthwire Attachment | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-09 09:40
13040142 | OTA-WKM-C-0409-Earthwire Attachment | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-09 09:40
13040142 | OTA-WKM-C-0409-Earthwire Attachment | OTA-WKM-C0409 | OTA-WKM-C0409-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-19 08:00 | Updating to 4 Readings
13073746 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-09 09:20 | Wind wear
13073746 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-09 09:20
13073746 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-09 09:20 | Wind wear
13073746 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-09 09:20 | Significant corrosion
13285441 | OTA-WKM-C-0409-Insulator Set-OHW-OTA-1 | OTA-WKM-C0409 | OTA-WKM-C0409-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-28 | Replaced during RSA2 24-25 Reins Project
13285441 | OTA-WKM-C-0409-Insulator Set-OHW-OTA-1 | OTA-WKM-C0409 | OTA-WKM-C0409-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-28 | Replaced during RSA2 24-25 Reins Project
13285441 | OTA-WKM-C-0409-Insulator Set-OHW-OTA-1 | OTA-WKM-C0409 | OTA-WKM-C0409-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-28 | Replaced during RSA2 24-25 Reins Project
13285442 | OTA-WKM-C-0409-Insulator Set-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13285442 | OTA-WKM-C-0409-Insulator Set-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13285442 | OTA-WKM-C-0409-Insulator Set-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13285442 | OTA-WKM-C-0409-Insulator Set-OHW-OTA-2 | OTA-WKM-C0409 | OTA-WKM-C0409-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13286393 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0409 | OTA-WKM-C0409-10 | 2024 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-28 | Replaced during RSA2 24-25 Att Pt Project
13286393 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0409 | OTA-WKM-C0409-10 | 2024 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-28 | Replaced during RSA2 24-25 Att Pt Project
13286393 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0409 | OTA-WKM-C0409-10 | 2024 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-28 | Replaced during RSA2 24-25 Att Pt Project
13286393 | OTA-WKM-C-0409-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0409 | OTA-WKM-C0409-10 | 2024 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-28 | Replaced during RSA2 24-25 Att Pt Project
10047031 | OTA-WKM-C-0409-0410-Conductor-OHW-OTA-2 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 15:46
10047031 | OTA-WKM-C-0409-0410-Conductor-OHW-OTA-2 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:46
10047031 | OTA-WKM-C-0409-0410-Conductor-OHW-OTA-2 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-17 | RSA2 25-26 Subconductor Spacer Replacement Project
10047032 | OTA-WKM-C-0409-0410-Conductor-OHW-OTA-1 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-08 15:45
10047032 | OTA-WKM-C-0409-0410-Conductor-OHW-OTA-1 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:45
10047032 | OTA-WKM-C-0409-0410-Conductor-OHW-OTA-1 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:45
10047033 | OTA-WKM-C-0409-0410-Earthwire-A0 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:49
10047033 | OTA-WKM-C-0409-0410-Earthwire-A0 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 15:49
13329893 | OTA-WKM-C-0409-0410-Earthwire-C0 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
13329893 | OTA-WKM-C-0409-0410-Earthwire-C0 | OTA-WKM-C0409-0410 | OTA-WKM-C0409-0410-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 | CA copied from EW A0 Feb/2026
10046312 | OTA-WKM-C-0410-Tower | OTA-WKM-C0410 | OTA-WKM-C0410-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10046312 | OTA-WKM-C-0410-Tower | OTA-WKM-C0410 | OTA-WKM-C0410-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10046312 | OTA-WKM-C-0410-Tower | OTA-WKM-C0410 | OTA-WKM-C0410-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10046312 | OTA-WKM-C-0410-Tower | OTA-WKM-C0410 | OTA-WKM-C0410-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10046312 | OTA-WKM-C-0410-Tower | OTA-WKM-C0410 | OTA-WKM-C0410-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10046312 | OTA-WKM-C-0410-Tower | OTA-WKM-C0410 | OTA-WKM-C0410-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-06-02 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046312 | OTA-WKM-C-0410-Tower | OTA-WKM-C0410 | OTA-WKM-C0410-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51 | Significant corrosion visible from 300mm down from GL
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51 | Significant corrosion
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51 | Significant corrosion
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51 | Significant corrosion
10046313 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 08:51
10046316 | OTA-WKM-C-0410-Earthwire HW Set | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:23
10046316 | OTA-WKM-C-0410-Earthwire HW Set | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:23 | Significant corrosion on y clevis
10323826 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 | 2012 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-03 10:17
10323826 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 | 2012 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 10:17
10323826 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 | 2012 | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-03 10:17
10323826 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 | 2012 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 10:17
10323827 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 | 2012 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-03 10:17
10323827 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 | 2012 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 10:17
10323827 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 | 2012 | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-03 10:17
10323827 | OTA-WKM-C-0410-Insulator Set-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 | 2012 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 10:17
13040143 | OTA-WKM-C-0410-Earthwire Attachment | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 08:00 | Updating to 4 Readings
13040143 | OTA-WKM-C-0410-Earthwire Attachment | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:19
13040143 | OTA-WKM-C-0410-Earthwire Attachment | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:19
13040143 | OTA-WKM-C-0410-Earthwire Attachment | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 08:00 | Updating to 4 Readings
13073747 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22
13073747 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22
13073747 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22 | Significant corrosion on steel attached
13073747 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0410 | OTA-WKM-C0410-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22 | Significant corrosion on bolt and nut
13073748 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22
13073748 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22
13073748 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22
13073748 | OTA-WKM-C-0410-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0410 | OTA-WKM-C0410-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:22 | Significant corrosion on bolt and nut
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
13285029 | OTA-WKM-C-0410-Tower Foundation | OTA-WKM-C0410 | OTA-WKM-C0410-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | RSA2 24-25 Grillage Refurbishment
10047034 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-2 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 10:24
10047034 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-2 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:24
10047034 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-2 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10047034 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-2 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-17 | RSA2 25-26 Subconductor Spacer Replacement Project
10047035 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-1 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 10:24
10047035 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-1 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:24
10047035 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-1 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-25 | Routine CA
10047035 | OTA-WKM-C-0410-0411-Conductor-OHW-OTA-1 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:24 | Significant corrosion on u bolt nut
10047036 | OTA-WKM-C-0410-0411-Earthwire-A0 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:27
10047036 | OTA-WKM-C-0410-0411-Earthwire-A0 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 10:27
10047036 | OTA-WKM-C-0410-0411-Earthwire-A0 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-14 | CA
13329894 | OTA-WKM-C-0410-0411-Earthwire-C0 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 | CA copied from EW A0 Feb/2026
13329894 | OTA-WKM-C-0410-0411-Earthwire-C0 | OTA-WKM-C0410-0411 | OTA-WKM-C0410-0411-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 | CA copied from EW A0 Feb/2026
10046317 | OTA-WKM-C-0411-Tower | OTA-WKM-C0411 | OTA-WKM-C0411-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046317 | OTA-WKM-C-0411-Tower | OTA-WKM-C0411 | OTA-WKM-C0411-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046317 | OTA-WKM-C-0411-Tower | OTA-WKM-C0411 | OTA-WKM-C0411-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046317 | OTA-WKM-C-0411-Tower | OTA-WKM-C0411 | OTA-WKM-C0411-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046317 | OTA-WKM-C-0411-Tower | OTA-WKM-C0411 | OTA-WKM-C0411-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10046317 | OTA-WKM-C-0411-Tower | OTA-WKM-C0411 | OTA-WKM-C0411-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-11-20 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046317 | OTA-WKM-C-0411-Tower | OTA-WKM-C0411 | OTA-WKM-C0411-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
12058849 | OTA-WKM-C-0411-Earthwire HW Set | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:25 | Wrong overlay
12058849 | OTA-WKM-C-0411-Earthwire HW Set | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-13 08:25
13040144 | OTA-WKM-C-0411-Earthwire Attachment | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 | Replaced
13040144 | OTA-WKM-C-0411-Earthwire Attachment | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 20:37 | New DN nuts and bolts installed
13040144 | OTA-WKM-C-0411-Earthwire Attachment | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 20:36 | New attachment point installed
13040144 | OTA-WKM-C-0411-Earthwire Attachment | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 | Replaced
13073749 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:28 | Wind wear
13073749 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:28
13073749 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:28
13073749 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:28 | Significant corrosion
13073750 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:29 | Wind wear
13073750 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:29
13073750 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:29
13073750 | OTA-WKM-C-0411-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-13 08:29 | Significant corrosion
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285030 | OTA-WKM-C-0411-Tower Foundation | OTA-WKM-C0411 | OTA-WKM-C0411-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-12-12 | Replaced during RSA2 Grillage Refurb 24-25 project
13285443 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 08:41
13285443 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 08:41
13285443 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 08:41
13285443 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-1 | OTA-WKM-C0411 | OTA-WKM-C0411-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 08:41
13285444 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
13285444 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
13285444 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
13285444 | OTA-WKM-C-0411-Insulator Set-OHW-OTA-2 | OTA-WKM-C0411 | OTA-WKM-C0411-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
10047037 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-2 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-12 16:29
10047037 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-2 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:29
10047037 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-2 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10047037 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-2 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-17 | RSA2 25-26 Subconductor Spacer Replacement Project
10047038 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-1 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-12 16:27
10047038 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-1 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:27
10047038 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-1 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-14 | Routine CA
10047038 | OTA-WKM-C-0411-0412-Conductor-OHW-OTA-1 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:27
10047039 | OTA-WKM-C-0411-0412-Earthwire-A0 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:26
10047039 | OTA-WKM-C-0411-0412-Earthwire-A0 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:26
13329895 | OTA-WKM-C-0411-0412-Earthwire-C0 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 | CA copied from EW A0 Feb/2026
13329895 | OTA-WKM-C-0411-0412-Earthwire-C0 | OTA-WKM-C0411-0412 | OTA-WKM-C0411-0412-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 | CA copied from EW A0 Feb/2026
10046322 | OTA-WKM-C-0412-Tower | OTA-WKM-C0412 | OTA-WKM-C0412-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W Attachment plates rusty and metal loss
10046322 | OTA-WKM-C-0412-Tower | OTA-WKM-C0412 | OTA-WKM-C0412-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W Attachment plates rusty and metal loss
10046322 | OTA-WKM-C-0412-Tower | OTA-WKM-C0412 | OTA-WKM-C0412-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W Attachment plates rusty and metal loss
10046322 | OTA-WKM-C-0412-Tower | OTA-WKM-C0412 | OTA-WKM-C0412-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W Attachment plates rusty and metal loss
10046322 | OTA-WKM-C-0412-Tower | OTA-WKM-C0412 | OTA-WKM-C0412-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W Attachment plates rusty and metal loss
10046322 | OTA-WKM-C-0412-Tower | OTA-WKM-C0412 | OTA-WKM-C0412-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 11:27
10046322 | OTA-WKM-C-0412-Tower | OTA-WKM-C0412 | OTA-WKM-C0412-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-27 | CA - E/W Attachment plates rusty and metal loss
10332815 | OTA-WKM-C-0412-Earthwire HW Set | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-12 17:29 | .
10332815 | OTA-WKM-C-0412-Earthwire HW Set | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-12 17:29
13040145 | OTA-WKM-C-0412-Earthwire Attachment | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-22 08:00 | Updating to 4 Readings
13040145 | OTA-WKM-C-0412-Earthwire Attachment | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-12 17:30
13040145 | OTA-WKM-C-0412-Earthwire Attachment | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:30
13040145 | OTA-WKM-C-0412-Earthwire Attachment | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-22 08:00 | Updating to 4 Readings
13073751 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32 | Wind wear
13073751 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32
13073751 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32 | Wind wear
13073751 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32 | Significant corrosion
13073752 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0412 | OTA-WKM-C0412-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32 | Wind wear
13073752 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0412 | OTA-WKM-C0412-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32
13073752 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0412 | OTA-WKM-C0412-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32 | Wind wear
13073752 | OTA-WKM-C-0412-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0412 | OTA-WKM-C0412-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 17:32
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285031 | OTA-WKM-C-0412-Tower Foundation | OTA-WKM-C0412 | OTA-WKM-C0412-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-19 | 24-25 Grillage Refurbishment
13285445 | OTA-WKM-C-0412-Insulator Set-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 | Replaced during RSA2 24-25 Reins Project
13285445 | OTA-WKM-C-0412-Insulator Set-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 | Replaced during RSA2 24-25 Reins Project
13285445 | OTA-WKM-C-0412-Insulator Set-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 | Replaced during RSA2 24-25 Reins Project
13285445 | OTA-WKM-C-0412-Insulator Set-OHW-OTA-1 | OTA-WKM-C0412 | OTA-WKM-C0412-10 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 | Replaced during RSA2 24-25 Reins Project
13285446 | OTA-WKM-C-0412-Insulator Set-OHW-OTA-2 | OTA-WKM-C0412 | OTA-WKM-C0412-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 14:07
13285446 | OTA-WKM-C-0412-Insulator Set-OHW-OTA-2 | OTA-WKM-C0412 | OTA-WKM-C0412-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 14:07
13285446 | OTA-WKM-C-0412-Insulator Set-OHW-OTA-2 | OTA-WKM-C0412 | OTA-WKM-C0412-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 14:07
10047040 | OTA-WKM-C-0412-0413-Conductor-OHW-OTA-2 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-12 16:40
10047040 | OTA-WKM-C-0412-0413-Conductor-OHW-OTA-2 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:40
10047040 | OTA-WKM-C-0412-0413-Conductor-OHW-OTA-2 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:40 | Significant corrosion
10047041 | OTA-WKM-C-0412-0413-Conductor-OHW-OTA-1 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-12 16:40
10047041 | OTA-WKM-C-0412-0413-Conductor-OHW-OTA-1 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:40
10047041 | OTA-WKM-C-0412-0413-Conductor-OHW-OTA-1 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-18 | RSA2 25-26 Subconductor Spacer Replacement Project
10047042 | OTA-WKM-C-0412-0413-Earthwire-A0 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:42
10047042 | OTA-WKM-C-0412-0413-Earthwire-A0 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 16:42
13329896 | OTA-WKM-C-0412-0413-Earthwire-C0 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 | CA copied from EW A0 Feb/2026
13329896 | OTA-WKM-C-0412-0413-Earthwire-C0 | OTA-WKM-C0412-0413 | OTA-WKM-C0412-0413-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-12 | CA copied from EW A0 Feb/2026
10046327 | OTA-WKM-C-0413-Tower | OTA-WKM-C0413 | OTA-WKM-C0413-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rust
10046327 | OTA-WKM-C-0413-Tower | OTA-WKM-C0413 | OTA-WKM-C0413-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rust
10046327 | OTA-WKM-C-0413-Tower | OTA-WKM-C0413 | OTA-WKM-C0413-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rust
10046327 | OTA-WKM-C-0413-Tower | OTA-WKM-C0413 | OTA-WKM-C0413-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rust
10046327 | OTA-WKM-C-0413-Tower | OTA-WKM-C0413 | OTA-WKM-C0413-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rust
10046327 | OTA-WKM-C-0413-Tower | OTA-WKM-C0413 | OTA-WKM-C0413-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 13:28
10046327 | OTA-WKM-C-0413-Tower | OTA-WKM-C0413 | OTA-WKM-C0413-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rust
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04 | Significant corrosion dug leg B
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04 | Significant corrosion dug leg B
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04 | Significant corrosion dug leg B
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04
10046328 | OTA-WKM-C-0413-Tower Foundation | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:04 | Significant corrosion dug leg B
10332816 | OTA-WKM-C-0413-Earthwire HW Set | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:43 | Wrong overlay
10332816 | OTA-WKM-C-0413-Earthwire HW Set | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 15:43
13040146 | OTA-WKM-C-0413-Earthwire Attachment | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-19 08:00 | Updating to 4 Readings
13040146 | OTA-WKM-C-0413-Earthwire Attachment | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 16:32
13040146 | OTA-WKM-C-0413-Earthwire Attachment | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 16:32
13040146 | OTA-WKM-C-0413-Earthwire Attachment | OTA-WKM-C0413 | OTA-WKM-C0413-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-19 08:00 | Updating to 4 Readings
13073753 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:56 | Wind wear
13073753 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:56
13073753 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:56
13073753 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:56 | Significant corrosion through bolt and nut
13073754 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:40 | Wind wear
13073754 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:40
13073754 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:40
13073754 | OTA-WKM-C-0413-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:40 | Significant corrosion
13285447 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 TL Insulators 24-25 project
13285447 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 TL Insulators 24-25 project
13285447 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 TL Insulators 24-25 project
13285447 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-1 | OTA-WKM-C0413 | OTA-WKM-C0413-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-31 | Replaced during RSA2 TL Insulators 24-25 project
13285448 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285448 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285448 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285448 | OTA-WKM-C-0413-Insulator Set-OHW-OTA-2 | OTA-WKM-C0413 | OTA-WKM-C0413-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
10047043 | OTA-WKM-C-0413-0414-Conductor-OHW-OTA-2 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 16:07
10047043 | OTA-WKM-C-0413-0414-Conductor-OHW-OTA-2 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:07
10047043 | OTA-WKM-C-0413-0414-Conductor-OHW-OTA-2 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-18 | RSA2 25-26 Subconductor Spacer Replacement Project
10047044 | OTA-WKM-C-0413-0414-Conductor-OHW-OTA-1 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 16:05
10047044 | OTA-WKM-C-0413-0414-Conductor-OHW-OTA-1 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 16:05
10047044 | OTA-WKM-C-0413-0414-Conductor-OHW-OTA-1 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | RSA2 25-26 Subconductor Spacer Replacement Project
10047045 | OTA-WKM-C-0413-0414-Earthwire-A0 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:47
10047045 | OTA-WKM-C-0413-0414-Earthwire-A0 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 15:47
13329897 | OTA-WKM-C-0413-0414-Earthwire-C0 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
13329897 | OTA-WKM-C-0413-0414-Earthwire-C0 | OTA-WKM-C0413-0414 | OTA-WKM-C0413-0414-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
10046332 | OTA-WKM-C-0414-Tower | OTA-WKM-C0414 | OTA-WKM-C0414-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rusty with metal loss
10046332 | OTA-WKM-C-0414-Tower | OTA-WKM-C0414 | OTA-WKM-C0414-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rusty with metal loss
10046332 | OTA-WKM-C-0414-Tower | OTA-WKM-C0414 | OTA-WKM-C0414-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rusty with metal loss
10046332 | OTA-WKM-C-0414-Tower | OTA-WKM-C0414 | OTA-WKM-C0414-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rusty with metal loss
10046332 | OTA-WKM-C-0414-Tower | OTA-WKM-C0414 | OTA-WKM-C0414-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rusty with metal loss
10046332 | OTA-WKM-C-0414-Tower | OTA-WKM-C0414 | OTA-WKM-C0414-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-26 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046332 | OTA-WKM-C-0414-Tower | OTA-WKM-C0414 | OTA-WKM-C0414-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plates rusty with metal loss
10046334 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 | 1965 | INSE_ARMOUR ROD COND | Armour Rod Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 14:53
10046334 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 | 1965 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:53 | Wind wear
10046334 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 | 1965 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 14:53
10046334 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 | 1965 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:53
10046335 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 | 1965 | INSE_ARMOUR ROD COND | Armour Rod Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 14:52
10046335 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 | 1965 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:52 | Wind wear
10046335 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 | 1965 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 14:52
10046335 | OTA-WKM-C-0414-Insulator Set-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 | 1965 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:52
10332817 | OTA-WKM-C-0414-Earthwire HW Set | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:58 | Opposite overlays
10332817 | OTA-WKM-C-0414-Earthwire HW Set | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 14:58
13040147 | OTA-WKM-C-0414-Earthwire Attachment | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-18 08:00 | Updating to 4 Readings
13040147 | OTA-WKM-C-0414-Earthwire Attachment | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 14:54
13040147 | OTA-WKM-C-0414-Earthwire Attachment | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 14:54
13040147 | OTA-WKM-C-0414-Earthwire Attachment | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-18 08:00 | Updating to 4 Readings
13073755 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:55 | Wind wear
13073755 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:55
13073755 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:55
13073755 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0414 | OTA-WKM-C0414-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:55
13073756 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:56 | Wind wear
13073756 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:56
13073756 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:56
13073756 | OTA-WKM-C-0414-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0414 | OTA-WKM-C0414-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:56 | Significant corrosion
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-24 | RSA2 24-25 Grillage Refurbishment
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-24 | RSA2 24-25 Grillage Refurbishment
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-25 | RSA2 24-25 Grillage Refurbishment
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-25 | RSA2 24-25 Grillage Refurbishment
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-25 | RSA2 24-25 Grillage Refurbishment
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-25 | RSA2 24-25 Grillage Refurbishment
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-24 | RSA2 24-25 Grillage Refurbishment
13285032 | OTA-WKM-C-0414-Tower Foundation | OTA-WKM-C0414 | OTA-WKM-C0414-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-24 | RSA2 24-25 Grillage Refurbishment
10047046 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-2 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 14:22
10047046 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-2 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:22
10047046 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-2 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Dampers Drooping
10047046 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-2 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-19 | RSA2 25-26 Subconductor Spacer Replacement Project
10047047 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-1 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 14:20
10047047 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-1 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:20
10047047 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-1 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Dampers Drooping
10047047 | OTA-WKM-C-0414-0415-Conductor-OHW-OTA-1 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | RSA2 25-26 Subconductor Spacer Replacement Project
10047048 | OTA-WKM-C-0414-0415-Earthwire-A0 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:26
10047048 | OTA-WKM-C-0414-0415-Earthwire-A0 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 14:26
10047048 | OTA-WKM-C-0414-0415-Earthwire-A0 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-17 | CA
13329898 | OTA-WKM-C-0414-0415-Earthwire-C0 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
13329898 | OTA-WKM-C-0414-0415-Earthwire-C0 | OTA-WKM-C0414-0415 | OTA-WKM-C0414-0415-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
10046337 | OTA-WKM-C-0415-Tower | OTA-WKM-C0415 | OTA-WKM-C0415-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plate rusty and some metal loss
10046337 | OTA-WKM-C-0415-Tower | OTA-WKM-C0415 | OTA-WKM-C0415-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plate rusty and some metal loss
10046337 | OTA-WKM-C-0415-Tower | OTA-WKM-C0415 | OTA-WKM-C0415-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plate rusty and some metal loss
10046337 | OTA-WKM-C-0415-Tower | OTA-WKM-C0415 | OTA-WKM-C0415-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plate rusty and some metal loss
10046337 | OTA-WKM-C-0415-Tower | OTA-WKM-C0415 | OTA-WKM-C0415-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plate rusty and some metal loss
10046337 | OTA-WKM-C-0415-Tower | OTA-WKM-C0415 | OTA-WKM-C0415-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-05-02 11:47
10046337 | OTA-WKM-C-0415-Tower | OTA-WKM-C0415 | OTA-WKM-C0415-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - E/W Attachment plate rusty and some metal loss
12058850 | OTA-WKM-C-0415-Earthwire HW Set | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 13:21 | Wrong overlay both cct
12058850 | OTA-WKM-C-0415-Earthwire HW Set | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 13:21
13040148 | OTA-WKM-C-0415-Earthwire Attachment | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2014-03-15 08:00 | Updating to 4 Readings
13040148 | OTA-WKM-C-0415-Earthwire Attachment | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 13:19
13040148 | OTA-WKM-C-0415-Earthwire Attachment | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 13:19
13040148 | OTA-WKM-C-0415-Earthwire Attachment | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2014-03-15 08:00 | Updating to 4 Readings
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-27 | RSA2 24-25 Grillage Refurbishment
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-27 | RSA2 24-25 Grillage Refurbishment
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-28 | RSA2 24-25 Grillage Refurbishment
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-28 | RSA2 24-25 Grillage Refurbishment
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-27 | RSA2 24-25 Grillage Refurbishment
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-27 | RSA2 24-25 Grillage Refurbishment
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-28 | RSA2 24-25 Grillage Refurbishment
13285033 | OTA-WKM-C-0415-Tower Foundation | OTA-WKM-C0415 | OTA-WKM-C0415-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-28 | RSA2 24-25 Grillage Refurbishment
13285449 | OTA-WKM-C-0415-Insulator Set-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285449 | OTA-WKM-C-0415-Insulator Set-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285449 | OTA-WKM-C-0415-Insulator Set-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285449 | OTA-WKM-C-0415-Insulator Set-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Reins Project
13285450 | OTA-WKM-C-0415-Insulator Set-OHW-OTA-2 | OTA-WKM-C0415 | OTA-WKM-C0415-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 09:56
13285450 | OTA-WKM-C-0415-Insulator Set-OHW-OTA-2 | OTA-WKM-C0415 | OTA-WKM-C0415-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-20 09:56
13285450 | OTA-WKM-C-0415-Insulator Set-OHW-OTA-2 | OTA-WKM-C0415 | OTA-WKM-C0415-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-20 09:56
13286394 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Att Pt Project
13286394 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Att Pt Project
13286394 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Att Pt Project
13286394 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0415 | OTA-WKM-C0415-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-02 | Replaced during RSA2 24-25 Att Pt Project
13286395 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0415 | OTA-WKM-C0415-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during 24-25 ATT PT REPL
13286395 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0415 | OTA-WKM-C0415-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during 24-25 ATT PT REPL
13286395 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0415 | OTA-WKM-C0415-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during 24-25 ATT PT REPL
13286395 | OTA-WKM-C-0415-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0415 | OTA-WKM-C0415-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during 24-25 Att Pt REPL project
10047049 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-2 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 13:25
10047049 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-2 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 13:25
10047049 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-2 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-19 | RSA2 25-26 Subconductor Spacer Replacement Project
10047050 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-1 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 13:23
10047050 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-1 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 13:23
10047050 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-1 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Dampers Drooping
10047050 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-1 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-10 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Dampers Drooping
10047050 | OTA-WKM-C-0415-0416-Conductor-OHW-OTA-1 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-25 | RSA2 25-26 Subconductor Spacer Replacement Project
10047051 | OTA-WKM-C-0415-0416-Earthwire-A0 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 13:36
10047051 | OTA-WKM-C-0415-0416-Earthwire-A0 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 13:36
13329899 | OTA-WKM-C-0415-0416-Earthwire-C0 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
13329899 | OTA-WKM-C-0415-0416-Earthwire-C0 | OTA-WKM-C0415-0416 | OTA-WKM-C0415-0416-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
10046342 | OTA-WKM-C-0416-Tower | OTA-WKM-C0416 | OTA-WKM-C0416-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Wear on E/W attachment plates
10046342 | OTA-WKM-C-0416-Tower | OTA-WKM-C0416 | OTA-WKM-C0416-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Wear on E/W attachment plates
10046342 | OTA-WKM-C-0416-Tower | OTA-WKM-C0416 | OTA-WKM-C0416-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Wear on E/W attachment plates
10046342 | OTA-WKM-C-0416-Tower | OTA-WKM-C0416 | OTA-WKM-C0416-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Wear on E/W attachment plates
10046342 | OTA-WKM-C-0416-Tower | OTA-WKM-C0416 | OTA-WKM-C0416-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Wear on E/W attachment plates
10046342 | OTA-WKM-C-0416-Tower | OTA-WKM-C0416 | OTA-WKM-C0416-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 07:38
10046342 | OTA-WKM-C-0416-Tower | OTA-WKM-C0416 | OTA-WKM-C0416-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-28 | CA - Wear on E/W attachment plates
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12056595 | OTA-WKM-C-0416-Tower Foundation | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:39
12058851 | OTA-WKM-C-0416-Earthwire HW Set | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:29
12058851 | OTA-WKM-C-0416-Earthwire HW Set | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 11:29
13040149 | OTA-WKM-C-0416-Earthwire Attachment | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-18 08:00 | Updating to 4 Readings
13040149 | OTA-WKM-C-0416-Earthwire Attachment | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 11:29
13040149 | OTA-WKM-C-0416-Earthwire Attachment | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 11:29
13040149 | OTA-WKM-C-0416-Earthwire Attachment | OTA-WKM-C0416 | OTA-WKM-C0416-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-18 08:00 | Updating to 4 Readings
13073759 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30 | Wind wear
13073759 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30
13073759 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30
13073759 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30
13073760 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30 | Wind wear
13073760 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30
13073760 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30
13073760 | OTA-WKM-C-0416-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:30 | Significant corrosion
13285451 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | RSA2 TL Insulators 24-25
13285451 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | Replaced during 24-25 Ins replacement project
13285451 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | Replaced during 24-25 Ins replacement project
13285451 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-1 | OTA-WKM-C0416 | OTA-WKM-C0416-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-06 | Replaced during 24-25 Ins replacement project
13285452 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | replaced during 24-25 Ins repl project
13285452 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | replaced during 24-25 Ins repl project
13285452 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | replaced durin g24-25 Ins repl project
13285452 | OTA-WKM-C-0416-Insulator Set-OHW-OTA-2 | OTA-WKM-C0416 | OTA-WKM-C0416-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | replaced during 24-25 Ins repl project
10047052 | OTA-WKM-C-0416-0417-Conductor-OHW-OTA-2 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 10:44
10047052 | OTA-WKM-C-0416-0417-Conductor-OHW-OTA-2 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:44
10047052 | OTA-WKM-C-0416-0417-Conductor-OHW-OTA-2 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:44
10047053 | OTA-WKM-C-0416-0417-Conductor-OHW-OTA-1 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 11:17
10047053 | OTA-WKM-C-0416-0417-Conductor-OHW-OTA-1 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:17
10047053 | OTA-WKM-C-0416-0417-Conductor-OHW-OTA-1 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:17 | Significant corrosion on u bolt nut
10047054 | OTA-WKM-C-0416-0417-Earthwire-A0 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:28
10047054 | OTA-WKM-C-0416-0417-Earthwire-A0 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 11:28
13329900 | OTA-WKM-C-0416-0417-Earthwire-C0 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
13329900 | OTA-WKM-C-0416-0417-Earthwire-C0 | OTA-WKM-C0416-0417 | OTA-WKM-C0416-0417-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
10046347 | OTA-WKM-C-0417-Tower | OTA-WKM-C0417 | OTA-WKM-C0417-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | "CA - Insulator attachments rusty and metal loss, E/W attachment plates with metal loss 15% R/C"
10046347 | OTA-WKM-C-0417-Tower | OTA-WKM-C0417 | OTA-WKM-C0417-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | "CA - Insulator attachments rusty and metal loss, E/W attachment plates with metal loss 15% R/C"
10046347 | OTA-WKM-C-0417-Tower | OTA-WKM-C0417 | OTA-WKM-C0417-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | "CA - Insulator attachments rusty and metal loss, E/W attachment plates with metal loss 15% R/C"
10046347 | OTA-WKM-C-0417-Tower | OTA-WKM-C0417 | OTA-WKM-C0417-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | "CA - Insulator attachments rusty and metal loss, E/W attachment plates with metal loss 15% R/C"
10046347 | OTA-WKM-C-0417-Tower | OTA-WKM-C0417 | OTA-WKM-C0417-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | "CA - Insulator attachments rusty and metal loss, E/W attachment plates with metal loss 15% R/C"
10046347 | OTA-WKM-C-0417-Tower | OTA-WKM-C0417 | OTA-WKM-C0417-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-25 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046347 | OTA-WKM-C-0417-Tower | OTA-WKM-C0417 | OTA-WKM-C0417-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | "CA - Insulator attachments rusty and metal loss, E/W attachment plates with metal loss 15% R/C"
10046349 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 10:09
10046349 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:09 | Wind wear
10046349 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:09 | Significant corrosion on caps and pins
10046349 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:09 | Significant corrosion on caps and pins
10046350 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 10:08
10046350 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:08 | Wind wear
10046350 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:08 | Significant corrosion on u bolt nuts
10046350 | OTA-WKM-C-0417-Insulator Set-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:08 | Significant corrosion on caps and pins
10332838 | OTA-WKM-C-0417-Earthwire HW Set | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:15
10332838 | OTA-WKM-C-0417-Earthwire HW Set | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 10:15
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:22
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:22
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:22
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 10:22
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:22
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:22 | Significant corrosion on steel interface
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-06 10:22
12056596 | OTA-WKM-C-0417-Tower Foundation | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 10:22
13040150 | OTA-WKM-C-0417-Earthwire Attachment | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-18 08:00 | Updating to 4 Readings
13040150 | OTA-WKM-C-0417-Earthwire Attachment | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 10:11
13040150 | OTA-WKM-C-0417-Earthwire Attachment | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-06 10:11
13040150 | OTA-WKM-C-0417-Earthwire Attachment | OTA-WKM-C0417 | OTA-WKM-C0417-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-18 08:00 | Updating to 4 Readings
13073761 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Wind wear
13073761 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Significant corrosion
13073761 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Significant corrosion
13073761 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0417 | OTA-WKM-C0417-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Significant corrosion
13073762 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Wind wear
13073762 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Significant corrosion
13073762 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Significant corrosion
13073762 | OTA-WKM-C-0417-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0417 | OTA-WKM-C0417-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:14 | Significant corrosion
10047055 | OTA-WKM-C-0417-0418-Conductor-OHW-OTA-2 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 10:20
10047055 | OTA-WKM-C-0417-0418-Conductor-OHW-OTA-2 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:20
10047055 | OTA-WKM-C-0417-0418-Conductor-OHW-OTA-2 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:20
10047056 | OTA-WKM-C-0417-0418-Conductor-OHW-OTA-1 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-06 10:16
10047056 | OTA-WKM-C-0417-0418-Conductor-OHW-OTA-1 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:16
10047056 | OTA-WKM-C-0417-0418-Conductor-OHW-OTA-1 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA
10047056 | OTA-WKM-C-0417-0418-Conductor-OHW-OTA-1 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:16 | Significant corrosion on u bolt nuts
10047057 | OTA-WKM-C-0417-0418-Earthwire-A0 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:21
10047057 | OTA-WKM-C-0417-0418-Earthwire-A0 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 10:21 | Surface pitting
13329901 | OTA-WKM-C-0417-0418-Earthwire-C0 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | CA copied from EW A0 Feb/2026
13329901 | OTA-WKM-C-0417-0418-Earthwire-C0 | OTA-WKM-C0417-0418 | OTA-WKM-C0417-0418-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-06 | Surface pitting. CA copied from EW A0 Feb/2026
10046352 | OTA-WKM-C-0418-Tower | OTA-WKM-C0418 | OTA-WKM-C0418-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA - E/W Attachment plates have wear
10046352 | OTA-WKM-C-0418-Tower | OTA-WKM-C0418 | OTA-WKM-C0418-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA - E/W Attachment plates have wear
10046352 | OTA-WKM-C-0418-Tower | OTA-WKM-C0418 | OTA-WKM-C0418-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA - E/W Attachment plates have wear
10046352 | OTA-WKM-C-0418-Tower | OTA-WKM-C0418 | OTA-WKM-C0418-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA - E/W Attachment plates have wear
10046352 | OTA-WKM-C-0418-Tower | OTA-WKM-C0418 | OTA-WKM-C0418-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA - E/W Attachment plates have wear
10046352 | OTA-WKM-C-0418-Tower | OTA-WKM-C0418 | OTA-WKM-C0418-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-10-19 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046352 | OTA-WKM-C-0418-Tower | OTA-WKM-C0418 | OTA-WKM-C0418-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA - E/W Attachment plates have wear
10046354 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 11:11
10046354 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 11:11 | Wind wear
10046354 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 11:11
10046354 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 11:11
10046355 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 11:11
10046355 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 11:11 | Wind wear
10046355 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 11:11
10046355 | OTA-WKM-C-0418-Insulator Set-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 11:11
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12002022 | OTA-WKM-C-0418-Tower Foundation | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 10:47
12058852 | OTA-WKM-C-0418-Earthwire HW Set | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 11:09 | Wrong overlay
12058852 | OTA-WKM-C-0418-Earthwire HW Set | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 11:09
13040151 | OTA-WKM-C-0418-Earthwire Attachment | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-27 08:00 | Updating to 4 Readings
13040151 | OTA-WKM-C-0418-Earthwire Attachment | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 11:08
13040151 | OTA-WKM-C-0418-Earthwire Attachment | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 11:08
13040151 | OTA-WKM-C-0418-Earthwire Attachment | OTA-WKM-C0418 | OTA-WKM-C0418-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-27 08:00 | Updating to 4 Readings
13073763 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:53 | Wind wear
13073763 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:53
13073763 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:53 | Significant corrosion
13073763 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0418 | OTA-WKM-C0418-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:53 | Significant corrosion on bolt and nut
13073764 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:58 | Wind wear
13073764 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:58
13073764 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:58
13073764 | OTA-WKM-C-0418-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0418 | OTA-WKM-C0418-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:58 | Significant corrosion on bolt and nut
10047058 | OTA-WKM-C-0418-0419-Conductor-OHW-OTA-2 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 10:44
10047058 | OTA-WKM-C-0418-0419-Conductor-OHW-OTA-2 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:44
10047058 | OTA-WKM-C-0418-0419-Conductor-OHW-OTA-2 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-19 | CA
10047058 | OTA-WKM-C-0418-0419-Conductor-OHW-OTA-2 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:44
10047059 | OTA-WKM-C-0418-0419-Conductor-OHW-OTA-1 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 10:41
10047059 | OTA-WKM-C-0418-0419-Conductor-OHW-OTA-1 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:41
10047059 | OTA-WKM-C-0418-0419-Conductor-OHW-OTA-1 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:41
10047060 | OTA-WKM-C-0418-0419-Earthwire-A0 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:44
10047060 | OTA-WKM-C-0418-0419-Earthwire-A0 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 10:44
13329902 | OTA-WKM-C-0418-0419-Earthwire-C0 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 | CA copied from EW A0 Feb/2026
13329902 | OTA-WKM-C-0418-0419-Earthwire-C0 | OTA-WKM-C0418-0419 | OTA-WKM-C0418-0419-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 | CA copied from EW A0 Feb/2026
10046357 | OTA-WKM-C-0419-Tower | OTA-WKM-C0419 | OTA-WKM-C0419-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046357 | OTA-WKM-C-0419-Tower | OTA-WKM-C0419 | OTA-WKM-C0419-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046357 | OTA-WKM-C-0419-Tower | OTA-WKM-C0419 | OTA-WKM-C0419-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046357 | OTA-WKM-C-0419-Tower | OTA-WKM-C0419 | OTA-WKM-C0419-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046357 | OTA-WKM-C-0419-Tower | OTA-WKM-C0419 | OTA-WKM-C0419-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046357 | OTA-WKM-C-0419-Tower | OTA-WKM-C0419 | OTA-WKM-C0419-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-03-28 | Full tower refurbishment including MAD area on CCT2 (2coat system)
10046357 | OTA-WKM-C-0419-Tower | OTA-WKM-C0419 | OTA-WKM-C0419-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12056597 | OTA-WKM-C-0419-Tower Foundation | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 10:55
12058853 | OTA-WKM-C-0419-Earthwire HW Set | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:43
12058853 | OTA-WKM-C-0419-Earthwire HW Set | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:43
13040152 | OTA-WKM-C-0419-Earthwire Attachment | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13040152 | OTA-WKM-C-0419-Earthwire Attachment | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:42
13040152 | OTA-WKM-C-0419-Earthwire Attachment | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:42 | Wind wear
13040152 | OTA-WKM-C-0419-Earthwire Attachment | OTA-WKM-C0419 | OTA-WKM-C0419-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13073765 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:02
13073765 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:02
13073765 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:02
13073765 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:02 | Significant corrosion on bolt and nut
13073766 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:03
13073766 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:03
13073766 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:03
13073766 | OTA-WKM-C-0419-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:03 | Significant corrosion on bolt and nut
13285453 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-07 | Replaced during 24-25 Ins replacement project
13285453 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-07 | Replaced during 24-25 Ins replacement project
13285453 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-07 | Replaced during 24-25 Ins replacement project
13285453 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-1 | OTA-WKM-C0419 | OTA-WKM-C0419-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-07 | Replaced during 24-25 Ins replacement project
13285454 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | replaced during 24-25 Ins project
13285454 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | replaced during 24-25 Ins project
13285454 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | replaced during 24-25 Ins project
13285454 | OTA-WKM-C-0419-Insulator Set-OHW-OTA-2 | OTA-WKM-C0419 | OTA-WKM-C0419-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | replaced during 24-25 Ins project
10047061 | OTA-WKM-C-0419-0420-Conductor-OHW-OTA-2 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 13:35
10047061 | OTA-WKM-C-0419-0420-Conductor-OHW-OTA-2 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:35
10047061 | OTA-WKM-C-0419-0420-Conductor-OHW-OTA-2 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:35 | Significant corrosion
10047062 | OTA-WKM-C-0419-0420-Conductor-OHW-OTA-1 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 12:16
10047062 | OTA-WKM-C-0419-0420-Conductor-OHW-OTA-1 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:16
10047062 | OTA-WKM-C-0419-0420-Conductor-OHW-OTA-1 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:16 | Significant corrosion
10047063 | OTA-WKM-C-0419-0420-Earthwire-A0 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:50
10047063 | OTA-WKM-C-0419-0420-Earthwire-A0 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 11:50
13329903 | OTA-WKM-C-0419-0420-Earthwire-C0 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 | CA copied from EW A0 Feb/2026
13329903 | OTA-WKM-C-0419-0420-Earthwire-C0 | OTA-WKM-C0419-0420 | OTA-WKM-C0419-0420-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 | CA copied from EW A0 Feb/2026
10046362 | OTA-WKM-C-0420-Tower | OTA-WKM-C0420 | OTA-WKM-C0420-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-26 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046362 | OTA-WKM-C-0420-Tower | OTA-WKM-C0420 | OTA-WKM-C0420-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-26 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046362 | OTA-WKM-C-0420-Tower | OTA-WKM-C0420 | OTA-WKM-C0420-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-26 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046362 | OTA-WKM-C-0420-Tower | OTA-WKM-C0420 | OTA-WKM-C0420-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-26 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046362 | OTA-WKM-C-0420-Tower | OTA-WKM-C0420 | OTA-WKM-C0420-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-26 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
10046362 | OTA-WKM-C-0420-Tower | OTA-WKM-C0420 | OTA-WKM-C0420-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-06-06 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046362 | OTA-WKM-C-0420-Tower | OTA-WKM-C0420 | OTA-WKM-C0420-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-26 | Fitted Climbing Deterrent to tower. Tower not reassessed, ratings remain unchanged.
12009209 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 12:45
12009209 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-03 12:45
12009209 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-03 12:45
12009209 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-03 12:45
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12056598 | OTA-WKM-C-0420-Tower Foundation | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-03 12:43
12058854 | OTA-WKM-C-0420-Earthwire HW Set | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:25
12058854 | OTA-WKM-C-0420-Earthwire HW Set | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:25
13040153 | OTA-WKM-C-0420-Earthwire Attachment | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-15 08:00 | Updating to 4 Readings
13040153 | OTA-WKM-C-0420-Earthwire Attachment | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:25
13040153 | OTA-WKM-C-0420-Earthwire Attachment | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:25 | Wind wear
13040153 | OTA-WKM-C-0420-Earthwire Attachment | OTA-WKM-C0420 | OTA-WKM-C0420-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-15 08:00 | Updating to 4 Readings
13073767 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:49
13073767 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:49
13073767 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:49
13073767 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0420 | OTA-WKM-C0420-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:49
13073768 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:50
13073768 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:50
13073768 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:50
13073768 | OTA-WKM-C-0420-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:50
13285455 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
13285455 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
13285455 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
13285455 | OTA-WKM-C-0420-Insulator Set-OHW-OTA-2 | OTA-WKM-C0420 | OTA-WKM-C0420-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 | Replaced during RSA2 24-25 Reins Project
10047064 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-2 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 12:57
10047064 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-2 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:57
10047064 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-2 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10047064 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-2 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-20 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10047064 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-2 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:57 | Significant corrosion on u bolt nut
10047065 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-1 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-03 12:56
10047065 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-1 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:56
10047065 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-1 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2014-03-25 | Fit extended midspan joint x1.
10047065 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-1 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-10 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10047065 | OTA-WKM-C-0420-0421-Conductor-OHW-OTA-1 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 12:56 | Significant corrosion on u bolt nut
10047066 | OTA-WKM-C-0420-0421-Earthwire-A0 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:26
10047066 | OTA-WKM-C-0420-0421-Earthwire-A0 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 13:26 | Surface pitting both EW
10047066 | OTA-WKM-C-0420-0421-Earthwire-A0 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-14 | CA
13329904 | OTA-WKM-C-0420-0421-Earthwire-C0 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 | CA copied from EW A0 Feb/2026
13329904 | OTA-WKM-C-0420-0421-Earthwire-C0 | OTA-WKM-C0420-0421 | OTA-WKM-C0420-0421-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-03 | Surface pitting both EW. CA copied from EW A0 Feb/2026
10046367 | OTA-WKM-C-0421-Tower | OTA-WKM-C0421 | OTA-WKM-C0421-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046367 | OTA-WKM-C-0421-Tower | OTA-WKM-C0421 | OTA-WKM-C0421-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046367 | OTA-WKM-C-0421-Tower | OTA-WKM-C0421 | OTA-WKM-C0421-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046367 | OTA-WKM-C-0421-Tower | OTA-WKM-C0421 | OTA-WKM-C0421-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046367 | OTA-WKM-C-0421-Tower | OTA-WKM-C0421 | OTA-WKM-C0421-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046367 | OTA-WKM-C-0421-Tower | OTA-WKM-C0421 | OTA-WKM-C0421-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-04-04 | Full tower refurbishment including MAD area on CCT2 (2coat system)
10046367 | OTA-WKM-C-0421-Tower | OTA-WKM-C0421 | OTA-WKM-C0421-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046369 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:03
10046369 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:03 | Wind wear
10046369 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:03 | Significant corrosion on clevis and u bolt nuts
10046369 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:03 | Significant corrosion on ball caps and pins
10046370 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:02
10046370 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:02 | Wind wear
10046370 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:02 | Significant corrosion on clevis and u bolt nuts
10046370 | OTA-WKM-C-0421-Insulator Set-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:02 | Significant corrosion on ball caps and pins
10046371 | OTA-WKM-C-0421-Earthwire HW Set | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:06
10046371 | OTA-WKM-C-0421-Earthwire HW Set | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:06
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 10:14
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 10:14
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 10:14
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 10:14 | Rust pitting at concrete/steel interface
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 10:14
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 10:14
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 10:14
12056599 | OTA-WKM-C-0421-Tower Foundation | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 10:14
13040154 | OTA-WKM-C-0421-Earthwire Attachment | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-14 08:00 | Updating to 4 Readings
13040154 | OTA-WKM-C-0421-Earthwire Attachment | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:03
13040154 | OTA-WKM-C-0421-Earthwire Attachment | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:03
13040154 | OTA-WKM-C-0421-Earthwire Attachment | OTA-WKM-C0421 | OTA-WKM-C0421-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-14 08:00 | Updating to 4 Readings
13073769 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:05 | Wind wear
13073769 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:05 | Significant corrosion
13073769 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:05 | Significant corrosion
13073769 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0421 | OTA-WKM-C0421-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:05 | Significant corrosion
13073770 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:06 | Wind wear
13073770 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:06 | Significant corrosion
13073770 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:06 | Significant corrosion
13073770 | OTA-WKM-C-0421-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0421 | OTA-WKM-C0421-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:06 | Significant corrosion
10047067 | OTA-WKM-C-0421-0422-Conductor-OHW-OTA-2 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 12:11
10047067 | OTA-WKM-C-0421-0422-Conductor-OHW-OTA-2 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:11
10047067 | OTA-WKM-C-0421-0422-Conductor-OHW-OTA-2 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:11 | Significant corrosion on u bolt nut
10047068 | OTA-WKM-C-0421-0422-Conductor-OHW-OTA-1 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 12:10
10047068 | OTA-WKM-C-0421-0422-Conductor-OHW-OTA-1 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:10
10047068 | OTA-WKM-C-0421-0422-Conductor-OHW-OTA-1 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:10 | Significant corrosion on u bolt nuts
10047069 | OTA-WKM-C-0421-0422-Earthwire-A0 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:15
10047069 | OTA-WKM-C-0421-0422-Earthwire-A0 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:15
13329905 | OTA-WKM-C-0421-0422-Earthwire-C0 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | CA copied from EW A0 Feb/2026
13329905 | OTA-WKM-C-0421-0422-Earthwire-C0 | OTA-WKM-C0421-0422 | OTA-WKM-C0421-0422-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | CA copied from EW A0 Feb/2026
10046372 | OTA-WKM-C-0422-Tower | OTA-WKM-C0422 | OTA-WKM-C0422-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046372 | OTA-WKM-C-0422-Tower | OTA-WKM-C0422 | OTA-WKM-C0422-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046372 | OTA-WKM-C-0422-Tower | OTA-WKM-C0422 | OTA-WKM-C0422-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046372 | OTA-WKM-C-0422-Tower | OTA-WKM-C0422 | OTA-WKM-C0422-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046372 | OTA-WKM-C-0422-Tower | OTA-WKM-C0422 | OTA-WKM-C0422-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046372 | OTA-WKM-C-0422-Tower | OTA-WKM-C0422 | OTA-WKM-C0422-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-04-04 | Full tower refurbishment including MAD area on CCT2 (2coat system)
10046372 | OTA-WKM-C-0422-Tower | OTA-WKM-C0422 | OTA-WKM-C0422-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-07 | Routine CA
10046374 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 | 1965 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
10046374 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 | 1965 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
10046374 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 | 1965 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
10046374 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 | 1965 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56 | Significant corrosion on caps and pins
10046375 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 | 1965 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
10046375 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 | 1965 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
10046375 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 | 1965 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
10046375 | OTA-WKM-C-0422-Insulator Set-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 | 1965 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56 | Significant corrosion on caps and pin
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12056600 | OTA-WKM-C-0422-Tower Foundation | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 11:40
12058855 | OTA-WKM-C-0422-Earthwire HW Set | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:58
12058855 | OTA-WKM-C-0422-Earthwire HW Set | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 11:58
13040155 | OTA-WKM-C-0422-Earthwire Attachment | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56 | Wind wear
13040155 | OTA-WKM-C-0422-Earthwire Attachment | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56 | Significant corrosion
13040155 | OTA-WKM-C-0422-Earthwire Attachment | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56 | Significant corrosion
13040155 | OTA-WKM-C-0422-Earthwire Attachment | OTA-WKM-C0422 | OTA-WKM-C0422-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56 | Significant corrosion
13073771 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
13073771 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
13073771 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
13073771 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0422 | OTA-WKM-C0422-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
13073772 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
13073772 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
13073772 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
13073772 | OTA-WKM-C-0422-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0422 | OTA-WKM-C0422-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 11:56
10047070 | OTA-WKM-C-0422-0423-Conductor-OHW-OTA-2 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 16:49
10047070 | OTA-WKM-C-0422-0423-Conductor-OHW-OTA-2 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:49
10047070 | OTA-WKM-C-0422-0423-Conductor-OHW-OTA-2 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:49
10047071 | OTA-WKM-C-0422-0423-Conductor-OHW-OTA-1 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 12:34
10047071 | OTA-WKM-C-0422-0423-Conductor-OHW-OTA-1 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:34
10047071 | OTA-WKM-C-0422-0423-Conductor-OHW-OTA-1 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 16:47
10047072 | OTA-WKM-C-0422-0423-Earthwire-A0 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:27
10047072 | OTA-WKM-C-0422-0423-Earthwire-A0 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 12:27 | Surface pitting
13329906 | OTA-WKM-C-0422-0423-Earthwire-C0 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | CA copied from EW A0 Feb/2026
13329906 | OTA-WKM-C-0422-0423-Earthwire-C0 | OTA-WKM-C0422-0423 | OTA-WKM-C0422-0423-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | Surface pitting. CA copied from EW A0 Feb/2026
10046377 | OTA-WKM-C-0423-Tower | OTA-WKM-C0423 | OTA-WKM-C0423-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046377 | OTA-WKM-C-0423-Tower | OTA-WKM-C0423 | OTA-WKM-C0423-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046377 | OTA-WKM-C-0423-Tower | OTA-WKM-C0423 | OTA-WKM-C0423-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046377 | OTA-WKM-C-0423-Tower | OTA-WKM-C0423 | OTA-WKM-C0423-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046377 | OTA-WKM-C-0423-Tower | OTA-WKM-C0423 | OTA-WKM-C0423-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046377 | OTA-WKM-C-0423-Tower | OTA-WKM-C0423 | OTA-WKM-C0423-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-04-04 | Full tower refurbishment including MAD area on CCT2 (2coat system)
10046377 | OTA-WKM-C-0423-Tower | OTA-WKM-C0423 | OTA-WKM-C0423-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046381 | OTA-WKM-C-0423-Earthwire HW Set | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 14:16
10046381 | OTA-WKM-C-0423-Earthwire HW Set | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 14:16
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
12056601 | OTA-WKM-C-0423-Tower Foundation | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-02 13:25
13040156 | OTA-WKM-C-0423-Earthwire Attachment | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13040156 | OTA-WKM-C-0423-Earthwire Attachment | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 14:15
13040156 | OTA-WKM-C-0423-Earthwire Attachment | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 14:15
13040156 | OTA-WKM-C-0423-Earthwire Attachment | OTA-WKM-C0423 | OTA-WKM-C0423-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13073773 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13073773 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13073773 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13073773 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13073774 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13073774 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13073774 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13073774 | OTA-WKM-C-0423-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:56
13285456 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | Replaced during RSA2 24-25 Reins Project
13285456 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | Replaced during RSA2 24-25 Reins Project
13285456 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | Replaced during RSA2 24-25 Reins Project
13285456 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-1 | OTA-WKM-C0423 | OTA-WKM-C0423-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 | Replaced during RSA2 24-25 Reins Project
13285457 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285457 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285457 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
13285457 | OTA-WKM-C-0423-Insulator Set-OHW-OTA-2 | OTA-WKM-C0423 | OTA-WKM-C0423-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-24 | RSA2 TL Insulators 24-25
10047073 | OTA-WKM-C-0423-0424-Conductor-OHW-OTA-2 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 13:38
10047073 | OTA-WKM-C-0423-0424-Conductor-OHW-OTA-2 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:38
10047073 | OTA-WKM-C-0423-0424-Conductor-OHW-OTA-2 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-09 | RSA2 25-26 Subconductor Spacer Replacement Project
10047074 | OTA-WKM-C-0423-0424-Conductor-OHW-OTA-1 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-02 13:36
10047074 | OTA-WKM-C-0423-0424-Conductor-OHW-OTA-1 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 13:36
10047074 | OTA-WKM-C-0423-0424-Conductor-OHW-OTA-1 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-13 | RSA2 25-26 Subconductor Spacer Replacement Project
10047075 | OTA-WKM-C-0423-0424-Earthwire-A0 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 14:11
10047075 | OTA-WKM-C-0423-0424-Earthwire-A0 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 14:11
13329907 | OTA-WKM-C-0423-0424-Earthwire-C0 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | CA copied from EW A0 Feb/2026
13329907 | OTA-WKM-C-0423-0424-Earthwire-C0 | OTA-WKM-C0423-0424 | OTA-WKM-C0423-0424-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-02 | CA copied from EW A0 Feb/2026
10046382 | OTA-WKM-C-0424-Tower | OTA-WKM-C0424 | OTA-WKM-C0424-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-25 | Fitted anticlimb frame to tower. Tower not reassessed, ratings remain unchanged.
10046382 | OTA-WKM-C-0424-Tower | OTA-WKM-C0424 | OTA-WKM-C0424-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-25 | Fitted anticlimb frame to tower. Tower not reassessed, ratings remain unchanged.
10046382 | OTA-WKM-C-0424-Tower | OTA-WKM-C0424 | OTA-WKM-C0424-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-25 | Fitted anticlimb frame to tower. Tower not reassessed, ratings remain unchanged.
10046382 | OTA-WKM-C-0424-Tower | OTA-WKM-C0424 | OTA-WKM-C0424-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-25 | Fitted anticlimb frame to tower. Tower not reassessed, ratings remain unchanged.
10046382 | OTA-WKM-C-0424-Tower | OTA-WKM-C0424 | OTA-WKM-C0424-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-08-25 | Fitted anticlimb frame to tower. Tower not reassessed, ratings remain unchanged.
10046382 | OTA-WKM-C-0424-Tower | OTA-WKM-C0424 | OTA-WKM-C0424-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:37
10046382 | OTA-WKM-C-0424-Tower | OTA-WKM-C0424 | OTA-WKM-C0424-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-08-25 | Fitted anticlimb frame to tower. Tower not reassessed, ratings remain unchanged.
10046386 | OTA-WKM-C-0424-Earthwire HW Set | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2023-05-02 14:57
10046386 | OTA-WKM-C-0424-Earthwire HW Set | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-02 14:57
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
12056602 | OTA-WKM-C-0424-Tower Foundation | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 11:24
13040157 | OTA-WKM-C-0424-Earthwire Attachment | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13040157 | OTA-WKM-C-0424-Earthwire Attachment | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:00
13040157 | OTA-WKM-C-0424-Earthwire Attachment | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-03-25 | Replaced Attachment point plate and HW during routine maintenance.
13040157 | OTA-WKM-C-0424-Earthwire Attachment | OTA-WKM-C0424 | OTA-WKM-C0424-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13073775 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:00
13073775 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:00
13073775 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:00
13073775 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:00
13073776 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:01
13073776 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:01
13073776 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:01
13073776 | OTA-WKM-C-0424-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:01
13285458 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-15 | RSA2 TL Insulators 24-25
13285458 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-15 | RSA2 TL Insulators 24-25
13285458 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-15 | RSA2 TL Insulators 24-25
13285458 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-1 | OTA-WKM-C0424 | OTA-WKM-C0424-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-15 | RSA2 TL Insulators 24-25
13285459 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:36
13285459 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:36
13285459 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 | Replaced during RSA2 24-25 Reins Project
13285459 | OTA-WKM-C-0424-Insulator Set-OHW-OTA-2 | OTA-WKM-C0424 | OTA-WKM-C0424-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:36
10047076 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-2 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 11:39
10047076 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-2 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 11:39
10047076 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-2 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-26 | Routine CA
10047076 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-2 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-09 | RSA2 25-26 Subconductor Spacer Replacement Project
10047077 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-1 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 11:38
10047077 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-1 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 11:38
10047077 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-1 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-26 | Routine CA
10047077 | OTA-WKM-C-0424-0425-Conductor-OHW-OTA-1 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-13 | RSA2 25-26 Subconductor Spacer Replacement Project
10047078 | OTA-WKM-C-0424-0425-Earthwire-A0 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:04
10047078 | OTA-WKM-C-0424-0425-Earthwire-A0 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 12:04 | Surfaces pitting
13329908 | OTA-WKM-C-0424-0425-Earthwire-C0 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 | CA copied from EW A0 Feb/2026
13329908 | OTA-WKM-C-0424-0425-Earthwire-C0 | OTA-WKM-C0424-0425 | OTA-WKM-C0424-0425-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 | Surfaces pitting. CA copied from EW A0 Feb/2026
10046387 | OTA-WKM-C-0425-Tower | OTA-WKM-C0425 | OTA-WKM-C0425-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046387 | OTA-WKM-C-0425-Tower | OTA-WKM-C0425 | OTA-WKM-C0425-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046387 | OTA-WKM-C-0425-Tower | OTA-WKM-C0425 | OTA-WKM-C0425-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046387 | OTA-WKM-C-0425-Tower | OTA-WKM-C0425 | OTA-WKM-C0425-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046387 | OTA-WKM-C-0425-Tower | OTA-WKM-C0425 | OTA-WKM-C0425-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046387 | OTA-WKM-C-0425-Tower | OTA-WKM-C0425 | OTA-WKM-C0425-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-03-13 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046387 | OTA-WKM-C-0425-Tower | OTA-WKM-C0425 | OTA-WKM-C0425-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-26 | Routine CA
10046390 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 | 1965 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-01 13:38
10046390 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 | 1965 | INSE_SUSP COLD END COND | Susp Cold End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:38
10046390 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 | 1965 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 13:38
10046390 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 | 1965 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:38
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12056603 | OTA-WKM-C-0425-Tower Foundation | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 12:50
12058856 | OTA-WKM-C-0425-Earthwire HW Set | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 14:10
12058856 | OTA-WKM-C-0425-Earthwire HW Set | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 14:10
13040158 | OTA-WKM-C-0425-Earthwire Attachment | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13040158 | OTA-WKM-C-0425-Earthwire Attachment | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 14:09 | Rated as per TP specs
13040158 | OTA-WKM-C-0425-Earthwire Attachment | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 14:09 | Rated as per TP specs
13040158 | OTA-WKM-C-0425-Earthwire Attachment | OTA-WKM-C0425 | OTA-WKM-C0425-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-12-09 08:00 | Updating to 4 Readings
13073777 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13073777 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13073777 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13073777 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0425 | OTA-WKM-C0425-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13073778 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13073778 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13073778 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13073778 | OTA-WKM-C-0425-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 13:40
13285460 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2024-10-23 | RSA2 TL Insulators 24-25
13285460 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-23 | RSA2 TL Insulators 24-25
13285460 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-23 | RSA2 TL Insulators 24-25
13285460 | OTA-WKM-C-0425-Insulator Set-OHW-OTA-2 | OTA-WKM-C0425 | OTA-WKM-C0425-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-23 | RSA2 TL Insulators 24-25
10047079 | OTA-WKM-C-0425-0426-Conductor-OHW-OTA-2 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 15:05
10047079 | OTA-WKM-C-0425-0426-Conductor-OHW-OTA-2 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 15:05
10047079 | OTA-WKM-C-0425-0426-Conductor-OHW-OTA-2 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-09 | RSA2 25-26 Subconductor Spacer Replacement Project
10047080 | OTA-WKM-C-0425-0426-Conductor-OHW-OTA-1 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 15:04
10047080 | OTA-WKM-C-0425-0426-Conductor-OHW-OTA-1 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 15:04
10047080 | OTA-WKM-C-0425-0426-Conductor-OHW-OTA-1 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-13 | RSA2 25-26 Subconductor Spacer Replacement Project
10047081 | OTA-WKM-C-0425-0426-Earthwire-A0 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 14:12
10047081 | OTA-WKM-C-0425-0426-Earthwire-A0 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 14:12
10047081 | OTA-WKM-C-0425-0426-Earthwire-A0 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-12-08 01:00 | CA
13329909 | OTA-WKM-C-0425-0426-Earthwire-C0 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 | CA copied from EW A0 Feb/2026
13329909 | OTA-WKM-C-0425-0426-Earthwire-C0 | OTA-WKM-C0425-0426 | OTA-WKM-C0425-0426-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 | CA copied from EW A0 Feb/2026
10046392 | OTA-WKM-C-0426-Tower | OTA-WKM-C0426 | OTA-WKM-C0426-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - E/W attachment plates have metal loss
10046392 | OTA-WKM-C-0426-Tower | OTA-WKM-C0426 | OTA-WKM-C0426-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - E/W attachment plates have metal loss
10046392 | OTA-WKM-C-0426-Tower | OTA-WKM-C0426 | OTA-WKM-C0426-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - E/W attachment plates have metal loss
10046392 | OTA-WKM-C-0426-Tower | OTA-WKM-C0426 | OTA-WKM-C0426-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - E/W attachment plates have metal loss
10046392 | OTA-WKM-C-0426-Tower | OTA-WKM-C0426 | OTA-WKM-C0426-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - E/W attachment plates have metal loss
10046392 | OTA-WKM-C-0426-Tower | OTA-WKM-C0426 | OTA-WKM-C0426-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-25 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046392 | OTA-WKM-C-0426-Tower | OTA-WKM-C0426 | OTA-WKM-C0426-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - E/W attachment plates have metal loss
10332819 | OTA-WKM-C-0426-Earthwire HW Set | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:05
10332819 | OTA-WKM-C-0426-Earthwire HW Set | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 16:05
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 15:39
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 15:39
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 15:39
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 15:39
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 15:39
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 15:39
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-01 15:39
12002023 | OTA-WKM-C-0426-Tower Foundation | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 15:39
13040159 | OTA-WKM-C-0426-Earthwire Attachment | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-11-09 08:00 | Updating to 4 Readings
13040159 | OTA-WKM-C-0426-Earthwire Attachment | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13040159 | OTA-WKM-C-0426-Earthwire Attachment | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13040159 | OTA-WKM-C-0426-Earthwire Attachment | OTA-WKM-C0426 | OTA-WKM-C0426-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-11-09 08:00 | Updating to 4 Readings
13073779 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13073779 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13073779 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13073779 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13073780 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13073780 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13073780 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13073780 | OTA-WKM-C-0426-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:07
13285461 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285461 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285461 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285461 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-1 | OTA-WKM-C0426 | OTA-WKM-C0426-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285462 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285462 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285462 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
13285462 | OTA-WKM-C-0426-Insulator Set-OHW-OTA-2 | OTA-WKM-C0426 | OTA-WKM-C0426-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-18 | Replaced during RSA2 24-25 Reins Project
10047082 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-2 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 15:14
10047082 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-2 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 15:14
10047082 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-2 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - Dampers Drooping
10047082 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-2 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-09 | RSA2 25-26 Subconductor Spacer Replacement Project
10047083 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-1 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-01 15:12
10047083 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-1 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 15:12
10047083 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-1 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-04-02 | CA - Dampers Drooping
10047083 | OTA-WKM-C-0426-0427-Conductor-OHW-OTA-1 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-13 | RSA2 25-26 Subconductor Spacer Replacement Project
10047084 | OTA-WKM-C-0426-0427-Earthwire-A0 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:06
10047084 | OTA-WKM-C-0426-0427-Earthwire-A0 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 16:06
13329910 | OTA-WKM-C-0426-0427-Earthwire-C0 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 | CA copied from EW A0 Feb/2026
13329910 | OTA-WKM-C-0426-0427-Earthwire-C0 | OTA-WKM-C0426-0427 | OTA-WKM-C0426-0427-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-01 | CA copied from EW A0 Feb/2026
10046397 | OTA-WKM-C-0427-Tower | OTA-WKM-C0427 | OTA-WKM-C0427-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-11 | Fitted Climbing Deterrent to tower 4m above ground level. Tower not reassessed, ratings remain unchanged.
10046397 | OTA-WKM-C-0427-Tower | OTA-WKM-C0427 | OTA-WKM-C0427-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-11 | Fitted Climbing Deterrent to tower 4m above ground level. Tower not reassessed, ratings remain unchanged.
10046397 | OTA-WKM-C-0427-Tower | OTA-WKM-C0427 | OTA-WKM-C0427-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-11 | Fitted Climbing Deterrent to tower 4m above ground level. Tower not reassessed, ratings remain unchanged.
10046397 | OTA-WKM-C-0427-Tower | OTA-WKM-C0427 | OTA-WKM-C0427-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-11 | Fitted Climbing Deterrent to tower 4m above ground level. Tower not reassessed, ratings remain unchanged.
10046397 | OTA-WKM-C-0427-Tower | OTA-WKM-C0427 | OTA-WKM-C0427-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-11 | Fitted Climbing Deterrent to tower 4m above ground level. Tower not reassessed, ratings remain unchanged.
10046397 | OTA-WKM-C-0427-Tower | OTA-WKM-C0427 | OTA-WKM-C0427-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-25 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046397 | OTA-WKM-C-0427-Tower | OTA-WKM-C0427 | OTA-WKM-C0427-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-11 | Fitted Climbing Deterrent to tower 4m above ground level. Tower not reassessed, ratings remain unchanged.
10046401 | OTA-WKM-C-0427-Earthwire HW Set | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:56
10046401 | OTA-WKM-C-0427-Earthwire HW Set | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:56
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
12056604 | OTA-WKM-C-0427-Tower Foundation | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 16:14
13073781 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54 | Wind wear
13073781 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54
13073781 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54 | Significant corrosion on steel attached
13073781 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54 | Significant corrosion on through bolt
13073782 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54 | Wind wear
13073782 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54
13073782 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54 | Significant corrosion on steel
13073782 | OTA-WKM-C-0427-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:54 | Significant corrosion on through bolt
13262442 | OTA-WKM-C-0427-Earthwire Attachment | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Replace Earthwire ATT Points WO3011770
13262442 | OTA-WKM-C-0427-Earthwire Attachment | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Replace Earthwire ATT Points WO3011770
13262442 | OTA-WKM-C-0427-Earthwire Attachment | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Replace Earthwire ATT Points WO3011770
13262442 | OTA-WKM-C-0427-Earthwire Attachment | OTA-WKM-C0427 | OTA-WKM-C0427-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-14 | Replace Earthwire ATT Points WO3011770
13285463 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285463 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285463 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285463 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-1 | OTA-WKM-C0427 | OTA-WKM-C0427-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285464 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
13285464 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
13285464 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
13285464 | OTA-WKM-C-0427-Insulator Set-OHW-OTA-2 | OTA-WKM-C0427 | OTA-WKM-C0427-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 | Replaced during RSA2 24-25 Reins Project
10047085 | OTA-WKM-C-0427-0428-Conductor-OHW-OTA-2 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-30 17:57
10047085 | OTA-WKM-C-0427-0428-Conductor-OHW-OTA-2 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:57
10047085 | OTA-WKM-C-0427-0428-Conductor-OHW-OTA-2 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 | RSA2 25-26 Subconductor Spacer Replacement Project
10047086 | OTA-WKM-C-0427-0428-Conductor-OHW-OTA-1 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-30 17:56
10047086 | OTA-WKM-C-0427-0428-Conductor-OHW-OTA-1 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:56
10047086 | OTA-WKM-C-0427-0428-Conductor-OHW-OTA-1 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-15 | RSA2 25-26 Subconductor Spacer Replacement Project
10047087 | OTA-WKM-C-0427-0428-Earthwire-A0 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:58
10047087 | OTA-WKM-C-0427-0428-Earthwire-A0 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 17:58 | Surface pitting of strand
13329911 | OTA-WKM-C-0427-0428-Earthwire-C0 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 | CA copied from EW A0 Feb/2026
13329911 | OTA-WKM-C-0427-0428-Earthwire-C0 | OTA-WKM-C0427-0428 | OTA-WKM-C0427-0428-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 | Surface pitting of strand. CA copied from EW A0 Feb/2026
10046402 | OTA-WKM-C-0428-Tower | OTA-WKM-C0428 | OTA-WKM-C0428-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-02 | CA - E/W attachment plates rusty
10046402 | OTA-WKM-C-0428-Tower | OTA-WKM-C0428 | OTA-WKM-C0428-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-02 | CA - E/W attachment plates rusty
10046402 | OTA-WKM-C-0428-Tower | OTA-WKM-C0428 | OTA-WKM-C0428-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-02 | CA - E/W attachment plates rusty
10046402 | OTA-WKM-C-0428-Tower | OTA-WKM-C0428 | OTA-WKM-C0428-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-02 | CA - E/W attachment plates rusty
10046402 | OTA-WKM-C-0428-Tower | OTA-WKM-C0428 | OTA-WKM-C0428-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-02 | CA - E/W attachment plates rusty
10046402 | OTA-WKM-C-0428-Tower | OTA-WKM-C0428 | OTA-WKM-C0428-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-11-13 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046402 | OTA-WKM-C-0428-Tower | OTA-WKM-C0428 | OTA-WKM-C0428-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-02 | CA - E/W attachment plates rusty
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12056605 | OTA-WKM-C-0428-Tower Foundation | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 16:01
12058857 | OTA-WKM-C-0428-Earthwire HW Set | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:06
12058857 | OTA-WKM-C-0428-Earthwire HW Set | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:06
13040161 | OTA-WKM-C-0428-Earthwire Attachment | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-09 08:00 | Updating to 4 Readings
13040161 | OTA-WKM-C-0428-Earthwire Attachment | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-29 13:04
13040161 | OTA-WKM-C-0428-Earthwire Attachment | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:04
13040161 | OTA-WKM-C-0428-Earthwire Attachment | OTA-WKM-C0428 | OTA-WKM-C0428-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-09 08:00 | Updating to 4 Readings
13073783 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:05
13073783 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:05
13073783 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:05
13073783 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:05
13073784 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:06
13073784 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:06
13073784 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:06
13073784 | OTA-WKM-C-0428-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 13:06
13285465 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285465 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285465 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285465 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-1 | OTA-WKM-C0428 | OTA-WKM-C0428-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285466 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
13285466 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
13285466 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
13285466 | OTA-WKM-C-0428-Insulator Set-OHW-OTA-2 | OTA-WKM-C0428 | OTA-WKM-C0428-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
10047088 | OTA-WKM-C-0428-0429-Conductor-OHW-OTA-2 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 16:09
10047088 | OTA-WKM-C-0428-0429-Conductor-OHW-OTA-2 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 16:09
10047088 | OTA-WKM-C-0428-0429-Conductor-OHW-OTA-2 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-11 | RSA2 25-26 Subconductor Spacer Replacement Project
10047089 | OTA-WKM-C-0428-0429-Conductor-OHW-OTA-1 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 16:08
10047089 | OTA-WKM-C-0428-0429-Conductor-OHW-OTA-1 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 16:08
10047089 | OTA-WKM-C-0428-0429-Conductor-OHW-OTA-1 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-15 | RSA2 25-26 Subconductor Spacer Replacement Project
10047090 | OTA-WKM-C-0428-0429-Earthwire-A0 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 16:11
10047090 | OTA-WKM-C-0428-0429-Earthwire-A0 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 16:11
10047090 | OTA-WKM-C-0428-0429-Earthwire-A0 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-08 | CA
13329912 | OTA-WKM-C-0428-0429-Earthwire-C0 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 | CA copied from EW A0 Feb/2026
13329912 | OTA-WKM-C-0428-0429-Earthwire-C0 | OTA-WKM-C0428-0429 | OTA-WKM-C0428-0429-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 | CA copied from EW A0 Feb/2026
10046407 | OTA-WKM-C-0429-Tower | OTA-WKM-C0429 | OTA-WKM-C0429-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046407 | OTA-WKM-C-0429-Tower | OTA-WKM-C0429 | OTA-WKM-C0429-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046407 | OTA-WKM-C-0429-Tower | OTA-WKM-C0429 | OTA-WKM-C0429-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046407 | OTA-WKM-C-0429-Tower | OTA-WKM-C0429 | OTA-WKM-C0429-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046407 | OTA-WKM-C-0429-Tower | OTA-WKM-C0429 | OTA-WKM-C0429-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046407 | OTA-WKM-C-0429-Tower | OTA-WKM-C0429 | OTA-WKM-C0429-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 17:29
10046407 | OTA-WKM-C-0429-Tower | OTA-WKM-C0429 | OTA-WKM-C0429-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046411 | OTA-WKM-C-0429-Earthwire HW Set | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 15:22
10046411 | OTA-WKM-C-0429-Earthwire HW Set | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 15:22
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
12056606 | OTA-WKM-C-0429-Tower Foundation | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 08:16
13040162 | OTA-WKM-C-0429-Earthwire Attachment | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 | Replaced EW Att point during Routine maintenance Work
13040162 | OTA-WKM-C-0429-Earthwire Attachment | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 | Replaced EW Att point during Routine maintenance Work
13040162 | OTA-WKM-C-0429-Earthwire Attachment | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 | Replaced EW Att point during Routine maintenance Work
13040162 | OTA-WKM-C-0429-Earthwire Attachment | OTA-WKM-C0429 | OTA-WKM-C0429-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 | Replaced EW Att point during Routine maintenance Work
13073785 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:21 | Significant wind wear
13073785 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:21 | Significant corrosion
13073785 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:21 | Significant rust staining
13073785 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:21 | Significant corrosion
13073786 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:22 | Significant wind wear
13073786 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:22 | Significant corrosion
13073786 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:22 | Significant rust staining
13073786 | OTA-WKM-C-0429-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 09:22 | Significant corrosion
13285467 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 13:50
13285467 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 13:49
13285467 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 13:50
13285467 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-1 | OTA-WKM-C0429 | OTA-WKM-C0429-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 13:50
13285468 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 | Replaced during RSA2 24-25 Reins Project
13285468 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 | Replaced during RSA2 24-25 Reins Project
13285468 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 | Replaced during RSA2 24-25 Reins Project
13285468 | OTA-WKM-C-0429-Insulator Set-OHW-OTA-2 | OTA-WKM-C0429 | OTA-WKM-C0429-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 | Replaced during RSA2 24-25 Reins Project
10047091 | OTA-WKM-C-0429-0430-Conductor-OHW-OTA-2 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-19 08:34
10047091 | OTA-WKM-C-0429-0430-Conductor-OHW-OTA-2 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 08:34
10047091 | OTA-WKM-C-0429-0430-Conductor-OHW-OTA-2 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-11 | RSA2 25-26 Subconductor Spacer Replacement Project
10047092 | OTA-WKM-C-0429-0430-Conductor-OHW-OTA-1 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-19 08:30
10047092 | OTA-WKM-C-0429-0430-Conductor-OHW-OTA-1 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 08:30
10047092 | OTA-WKM-C-0429-0430-Conductor-OHW-OTA-1 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-16 | RSA2 25-26 Subconductor Spacer Replacement Project
10047093 | OTA-WKM-C-0429-0430-Earthwire-A0 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 08:35
10047093 | OTA-WKM-C-0429-0430-Earthwire-A0 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 08:35
13329913 | OTA-WKM-C-0429-0430-Earthwire-C0 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 | CA copied from EW A0 Feb/2026
13329913 | OTA-WKM-C-0429-0430-Earthwire-C0 | OTA-WKM-C0429-0430 | OTA-WKM-C0429-0430-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 | CA copied from EW A0 Feb/2026
10046412 | OTA-WKM-C-0430-Tower | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046412 | OTA-WKM-C-0430-Tower | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046412 | OTA-WKM-C-0430-Tower | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046412 | OTA-WKM-C-0430-Tower | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046412 | OTA-WKM-C-0430-Tower | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046412 | OTA-WKM-C-0430-Tower | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046412 | OTA-WKM-C-0430-Tower | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-08-10 | Routine CA
10046416 | OTA-WKM-C-0430-Earthwire HW Set | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 14:35 | Pitting
10046416 | OTA-WKM-C-0430-Earthwire HW Set | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 14:35 | Significant corrosion on the y clives
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
12056607 | OTA-WKM-C-0430-Tower Foundation | OTA-WKM-C0430 | OTA-WKM-C0430-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:55
13073787 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13073787 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13073787 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13073787 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13073788 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13073788 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13073788 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13073788 | OTA-WKM-C-0430-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:57
13285469 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285469 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285469 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285469 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-1 | OTA-WKM-C0430 | OTA-WKM-C0430-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285470 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
13285470 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
13285470 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
13285470 | OTA-WKM-C-0430-Insulator Set-OHW-OTA-2 | OTA-WKM-C0430 | OTA-WKM-C0430-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-25 | RSA2 TL Insulators 24-25
13286466 | OTA-WKM-C-0430-Earthwire Attachment | OTA-WKM-C0430 | OTA-WKM-C0430-00 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-02-21 | Replaced during RSA2 24-25 Att Pt Project
10047094 | OTA-WKM-C-0430-0431-Conductor-OHW-OTA-2 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 14:21
10047094 | OTA-WKM-C-0430-0431-Conductor-OHW-OTA-2 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 14:21
10047094 | OTA-WKM-C-0430-0431-Conductor-OHW-OTA-2 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-12 | RSA2 25-26 Subconductor Spacer Replacement Project
10047095 | OTA-WKM-C-0430-0431-Conductor-OHW-OTA-1 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 14:20
10047095 | OTA-WKM-C-0430-0431-Conductor-OHW-OTA-1 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 14:20
10047095 | OTA-WKM-C-0430-0431-Conductor-OHW-OTA-1 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-16 | RSA2 25-26 Subconductor Spacer Replacement Project
10047096 | OTA-WKM-C-0430-0431-Earthwire-A0 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 14:23
10047096 | OTA-WKM-C-0430-0431-Earthwire-A0 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 14:23
13329914 | OTA-WKM-C-0430-0431-Earthwire-C0 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 | CA copied from EW A0 Feb/2026
13329914 | OTA-WKM-C-0430-0431-Earthwire-C0 | OTA-WKM-C0430-0431 | OTA-WKM-C0430-0431-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 | CA copied from EW A0 Feb/2026
10046417 | OTA-WKM-C-0431-Tower | OTA-WKM-C0431 | OTA-WKM-C0431-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 7m above ground. Tower not reassessed, ratings remain unchanged.
10046417 | OTA-WKM-C-0431-Tower | OTA-WKM-C0431 | OTA-WKM-C0431-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 7m above ground. Tower not reassessed, ratings remain unchanged.
10046417 | OTA-WKM-C-0431-Tower | OTA-WKM-C0431 | OTA-WKM-C0431-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 7m above ground. Tower not reassessed, ratings remain unchanged.
10046417 | OTA-WKM-C-0431-Tower | OTA-WKM-C0431 | OTA-WKM-C0431-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 7m above ground. Tower not reassessed, ratings remain unchanged.
10046417 | OTA-WKM-C-0431-Tower | OTA-WKM-C0431 | OTA-WKM-C0431-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 7m above ground. Tower not reassessed, ratings remain unchanged.
10046417 | OTA-WKM-C-0431-Tower | OTA-WKM-C0431 | OTA-WKM-C0431-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-30 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046417 | OTA-WKM-C-0431-Tower | OTA-WKM-C0431 | OTA-WKM-C0431-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 7m above ground. Tower not reassessed, ratings remain unchanged.
10046421 | OTA-WKM-C-0431-Earthwire HW Set | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:20 | Surface pitting
10046421 | OTA-WKM-C-0431-Earthwire HW Set | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 13:20 | Have been replaced since last inspection
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 12:59
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 12:59
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 12:59
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 12:59
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 12:59
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 12:59
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 12:59
12056608 | OTA-WKM-C-0431-Tower Foundation | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 12:59
13040164 | OTA-WKM-C-0431-Earthwire Attachment | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 12:54
13040164 | OTA-WKM-C-0431-Earthwire Attachment | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 12:54
13040164 | OTA-WKM-C-0431-Earthwire Attachment | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 12:54
13040164 | OTA-WKM-C-0431-Earthwire Attachment | OTA-WKM-C0431 | OTA-WKM-C0431-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2019-08-22 08:00 | Updating to 4 Readings
13204571 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 13:13
13204571 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:13
13204571 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:13
13204571 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:13
13204572 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-18 13:15
13204572 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:15
13204572 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:15
13204572 | OTA-WKM-C-0431-Insulator Set-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-18 13:15
13300456 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-23 | Replaced during RSA2 25-26 Att Pt Project
13300456 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-23 | Replaced during RSA2 25-26 Att Pt Project
13300456 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-23 | Replaced during RSA2 25-26 Att Pt Project
13300456 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0431 | OTA-WKM-C0431-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-23 | Replaced during RSA2 25-26 Att Pt Project
13300457 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-15 18:26
13300457 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-15 18:26
13300457 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-15 18:26
13300457 | OTA-WKM-C-0431-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0431 | OTA-WKM-C0431-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-15 18:27
10047097 | OTA-WKM-C-0431-0432-Conductor-OHW-OTA-2 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 12:57
10047097 | OTA-WKM-C-0431-0432-Conductor-OHW-OTA-2 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-20 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 12:57
10047097 | OTA-WKM-C-0431-0432-Conductor-OHW-OTA-2 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-12 | RSA2 25-26 Subconductor Spacer Replacement Project
10047098 | OTA-WKM-C-0431-0432-Conductor-OHW-OTA-1 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 12:57
10047098 | OTA-WKM-C-0431-0432-Conductor-OHW-OTA-1 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-10 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 12:57
10047098 | OTA-WKM-C-0431-0432-Conductor-OHW-OTA-1 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-16 | RSA2 25-26 Subconductor Spacer Replacement Project
10047099 | OTA-WKM-C-0431-0432-Earthwire-A0 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 13:23
10047099 | OTA-WKM-C-0431-0432-Earthwire-A0 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 13:23
13329915 | OTA-WKM-C-0431-0432-Earthwire-C0 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 | CA copied from EW A0 Feb/2026
13329915 | OTA-WKM-C-0431-0432-Earthwire-C0 | OTA-WKM-C0431-0432 | OTA-WKM-C0431-0432-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 | CA copied from EW A0 Feb/2026
10046422 | OTA-WKM-C-0432-Tower | OTA-WKM-C0432 | OTA-WKM-C0432-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W Attachment plates rusty and with metal loss
10046422 | OTA-WKM-C-0432-Tower | OTA-WKM-C0432 | OTA-WKM-C0432-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W Attachment plates rusty and with metal loss
10046422 | OTA-WKM-C-0432-Tower | OTA-WKM-C0432 | OTA-WKM-C0432-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W Attachment plates rusty and with metal loss
10046422 | OTA-WKM-C-0432-Tower | OTA-WKM-C0432 | OTA-WKM-C0432-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W Attachment plates rusty and with metal loss
10046422 | OTA-WKM-C-0432-Tower | OTA-WKM-C0432 | OTA-WKM-C0432-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W Attachment plates rusty and with metal loss
10046422 | OTA-WKM-C-0432-Tower | OTA-WKM-C0432 | OTA-WKM-C0432-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-03-07 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046422 | OTA-WKM-C-0432-Tower | OTA-WKM-C0432 | OTA-WKM-C0432-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W Attachment plates rusty and with metal loss
10332820 | OTA-WKM-C-0432-Earthwire HW Set | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:43
10332820 | OTA-WKM-C-0432-Earthwire HW Set | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 11:43
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
12056609 | OTA-WKM-C-0432-Tower Foundation | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 10:18
13040165 | OTA-WKM-C-0432-Earthwire Attachment | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 11:39
13040165 | OTA-WKM-C-0432-Earthwire Attachment | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 11:39
13040165 | OTA-WKM-C-0432-Earthwire Attachment | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-19 11:39
13040165 | OTA-WKM-C-0432-Earthwire Attachment | OTA-WKM-C0432 | OTA-WKM-C0432-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-06-09 08:00 | Updating to 4 Readings
13073792 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:42 | Wind wear
13073792 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:42
13073792 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:42 | Significant corrosion on the steel
13073792 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:42
13285471 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285471 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285471 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285471 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285472 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13285472 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13285472 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13285472 | OTA-WKM-C-0432-Insulator Set-OHW-OTA-2 | OTA-WKM-C0432 | OTA-WKM-C0432-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-19 | Replaced during RSA2 24-25 Reins Project
13300458 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-24 | Replaced during RSA2 25-26 Att Pt Project
13300458 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-24 | Replaced during RSA2 25-26 Att Pt Project
13300458 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-24 | Replaced during RSA2 25-26 Att Pt Project
13300458 | OTA-WKM-C-0432-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0432 | OTA-WKM-C0432-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-24 | Replaced during RSA2 25-26 Att Pt Project
10047100 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-2 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-19 11:44
10047100 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-2 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:44
10047100 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-2 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Dampers Drooping
10047100 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-2 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:44
10047101 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-1 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-19 11:44
10047101 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-1 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:44
10047101 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-1 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Dampers Drooping
10047101 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-1 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-10 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Dampers Drooping
10047101 | OTA-WKM-C-0432-0433-Conductor-OHW-OTA-1 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:44
10047102 | OTA-WKM-C-0432-0433-Earthwire-A0 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:46
10047102 | OTA-WKM-C-0432-0433-Earthwire-A0 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 11:46
13329916 | OTA-WKM-C-0432-0433-Earthwire-C0 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 | CA copied from EW A0 Feb/2026
13329916 | OTA-WKM-C-0432-0433-Earthwire-C0 | OTA-WKM-C0432-0433 | OTA-WKM-C0432-0433-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-19 | CA copied from EW A0 Feb/2026
10046427 | OTA-WKM-C-0433-Tower | OTA-WKM-C0433 | OTA-WKM-C0433-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W attachment plates have metal loss
10046427 | OTA-WKM-C-0433-Tower | OTA-WKM-C0433 | OTA-WKM-C0433-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W attachment plates have metal loss
10046427 | OTA-WKM-C-0433-Tower | OTA-WKM-C0433 | OTA-WKM-C0433-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W attachment plates have metal loss
10046427 | OTA-WKM-C-0433-Tower | OTA-WKM-C0433 | OTA-WKM-C0433-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W attachment plates have metal loss
10046427 | OTA-WKM-C-0433-Tower | OTA-WKM-C0433 | OTA-WKM-C0433-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W attachment plates have metal loss
10046427 | OTA-WKM-C-0433-Tower | OTA-WKM-C0433 | OTA-WKM-C0433-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-03-09 | Full tower refurbishment including MAD area on CCT1 & CCT2 (2coat system)
10046427 | OTA-WKM-C-0433-Tower | OTA-WKM-C0433 | OTA-WKM-C0433-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - E/W attachment plates have metal loss
10332821 | OTA-WKM-C-0433-Earthwire HW Set | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 11:14
10332821 | OTA-WKM-C-0433-Earthwire HW Set | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-18 11:14
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
12056610 | OTA-WKM-C-0433-Tower Foundation | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 09:07
13040166 | OTA-WKM-C-0433-Earthwire Attachment | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-18 11:14
13040166 | OTA-WKM-C-0433-Earthwire Attachment | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-18 11:14
13040166 | OTA-WKM-C-0433-Earthwire Attachment | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-18 11:14
13040166 | OTA-WKM-C-0433-Earthwire Attachment | OTA-WKM-C0433 | OTA-WKM-C0433-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-18 11:14
13285473 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Reins Project
13285473 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Reins Project
13285473 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Reins Project
13285473 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 | Replaced during RSA2 24-25 Reins Project
13285474 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13285474 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13285474 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13285474 | OTA-WKM-C-0433-Insulator Set-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13286396 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 11:50
13286396 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 11:50
13286396 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 11:50
13286396 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0433 | OTA-WKM-C0433-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-29 11:50
13286397 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
13286397 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
13286397 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
13286397 | OTA-WKM-C-0433-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0433 | OTA-WKM-C0433-20 | 2024 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
10047103 | OTA-WKM-C-0433-0434-Conductor-OHW-OTA-2 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-18 10:57
10047103 | OTA-WKM-C-0433-0434-Conductor-OHW-OTA-2 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 10:57
10047103 | OTA-WKM-C-0433-0434-Conductor-OHW-OTA-2 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 10:57
10047104 | OTA-WKM-C-0433-0434-Conductor-OHW-OTA-1 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-08 | CA
10047104 | OTA-WKM-C-0433-0434-Conductor-OHW-OTA-1 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-07-08 | CA
10047104 | OTA-WKM-C-0433-0434-Conductor-OHW-OTA-1 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Dampers Drooping
10047105 | OTA-WKM-C-0433-0434-Earthwire-A0 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 11:16
10047105 | OTA-WKM-C-0433-0434-Earthwire-A0 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 11:16
10047105 | OTA-WKM-C-0433-0434-Earthwire-A0 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-08 | CA
13329917 | OTA-WKM-C-0433-0434-Earthwire-C0 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 | CA copied from EW A0 Feb/2026
13329917 | OTA-WKM-C-0433-0434-Earthwire-C0 | OTA-WKM-C0433-0434 | OTA-WKM-C0433-0434-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-18 | CA copied from EW A0 Feb/2026
10046432 | OTA-WKM-C-0434-Tower | OTA-WKM-C0434 | OTA-WKM-C0434-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046432 | OTA-WKM-C-0434-Tower | OTA-WKM-C0434 | OTA-WKM-C0434-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046432 | OTA-WKM-C-0434-Tower | OTA-WKM-C0434 | OTA-WKM-C0434-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046432 | OTA-WKM-C-0434-Tower | OTA-WKM-C0434 | OTA-WKM-C0434-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046432 | OTA-WKM-C-0434-Tower | OTA-WKM-C0434 | OTA-WKM-C0434-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046432 | OTA-WKM-C-0434-Tower | OTA-WKM-C0434 | OTA-WKM-C0434-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2016-07-08 | Grillage refurbishment
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:07
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:07
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:07
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:07
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:07
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:07
12056611 | OTA-WKM-C-0434-Tower Foundation | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:07
12058858 | OTA-WKM-C-0434-Earthwire HW Set | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:34 | 30 for cct 2 and 60 for cct 1 but the ard is not sitting properly
12058858 | OTA-WKM-C-0434-Earthwire HW Set | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-17 10:34
13073795 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:22
13073795 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:22
13073795 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:22
13073795 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:22
13073796 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:20
13073796 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:20
13073796 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:20
13073796 | OTA-WKM-C-0434-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:20
13216921 | OTA-WKM-C-0434-Earthwire Attachment | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:22
13216921 | OTA-WKM-C-0434-Earthwire Attachment | OTA-WKM-C0434 | OTA-WKM-C0434-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 10:22
13285475 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
13285475 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
13285475 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
13285475 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-1 | OTA-WKM-C0434 | OTA-WKM-C0434-10 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
13285476 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Reins Project
13285476 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Reins Project
13285476 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Reins Project
13285476 | OTA-WKM-C-0434-Insulator Set-OHW-OTA-2 | OTA-WKM-C0434 | OTA-WKM-C0434-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Reins Project
10047106 | OTA-WKM-C-0434-0435-Conductor-OHW-OTA-2 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:31
10047106 | OTA-WKM-C-0434-0435-Conductor-OHW-OTA-2 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:31
10047106 | OTA-WKM-C-0434-0435-Conductor-OHW-OTA-2 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:31
10047106 | OTA-WKM-C-0434-0435-Conductor-OHW-OTA-2 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-20 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-13 | RSA2 25-26 Subconductor Spacer Replacement Project
10047107 | OTA-WKM-C-0434-0435-Conductor-OHW-OTA-1 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:32
10047107 | OTA-WKM-C-0434-0435-Conductor-OHW-OTA-1 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:32
10047107 | OTA-WKM-C-0434-0435-Conductor-OHW-OTA-1 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:32
10047108 | OTA-WKM-C-0434-0435-Earthwire-A0 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:40
10047108 | OTA-WKM-C-0434-0435-Earthwire-A0 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 10:40
13329918 | OTA-WKM-C-0434-0435-Earthwire-C0 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 | CA copied from EW A0 Feb/2026
13329918 | OTA-WKM-C-0434-0435-Earthwire-C0 | OTA-WKM-C0434-0435 | OTA-WKM-C0434-0435-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 | CA copied from EW A0 Feb/2026
10046437 | OTA-WKM-C-0435-Tower | OTA-WKM-C0435 | OTA-WKM-C0435-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046437 | OTA-WKM-C-0435-Tower | OTA-WKM-C0435 | OTA-WKM-C0435-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046437 | OTA-WKM-C-0435-Tower | OTA-WKM-C0435 | OTA-WKM-C0435-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046437 | OTA-WKM-C-0435-Tower | OTA-WKM-C0435 | OTA-WKM-C0435-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046437 | OTA-WKM-C-0435-Tower | OTA-WKM-C0435 | OTA-WKM-C0435-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
10046437 | OTA-WKM-C-0435-Tower | OTA-WKM-C0435 | OTA-WKM-C0435-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-06-14 12:46
10046437 | OTA-WKM-C-0435-Tower | OTA-WKM-C0435 | OTA-WKM-C0435-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-24 | Routine CA
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-17 11:04
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 11:04
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 11:04
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 11:04
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 11:04
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 11:04
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 11:04
12056612 | OTA-WKM-C-0435-Tower Foundation | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-17 11:04
12058859 | OTA-WKM-C-0435-Earthwire HW Set | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2025-08-13 10:04
12058859 | OTA-WKM-C-0435-Earthwire HW Set | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 10:04
13073797 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43 | Wind wear
13073797 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43
13073797 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43 | Significant corrosion
13073797 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43
13073798 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43 | Wind wear
13073798 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43
13073798 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43 | Significant corrosion on steel attached
13073798 | OTA-WKM-C-0435-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:43
13285477 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-14 | Replaced during RSA2 24-25 Reins Project
13285477 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-14 | Replaced during RSA2 24-25 Reins Project
13285477 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-14 | Replaced during RSA2 24-25 Reins Project
13285477 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-1 | OTA-WKM-C0435 | OTA-WKM-C0435-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-14 | Replaced during RSA2 24-25 Reins Project
13285478 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
13285478 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
13285478 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
13285478 | OTA-WKM-C-0435-Insulator Set-OHW-OTA-2 | OTA-WKM-C0435 | OTA-WKM-C0435-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Reins Project
13300410 | OTA-WKM-C-0435-Earthwire Attachment | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 10:03
13300410 | OTA-WKM-C-0435-Earthwire Attachment | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 10:03
13300410 | OTA-WKM-C-0435-Earthwire Attachment | OTA-WKM-C0435 | OTA-WKM-C0435-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 10:03
10047109 | OTA-WKM-C-0435-0436-Conductor-OHW-OTA-2 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-17 11:09
10047109 | OTA-WKM-C-0435-0436-Conductor-OHW-OTA-2 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:09
10047109 | OTA-WKM-C-0435-0436-Conductor-OHW-OTA-2 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:09
10047110 | OTA-WKM-C-0435-0436-Conductor-OHW-OTA-1 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-17 11:08
10047110 | OTA-WKM-C-0435-0436-Conductor-OHW-OTA-1 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:08
10047110 | OTA-WKM-C-0435-0436-Conductor-OHW-OTA-1 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:08
10047111 | OTA-WKM-C-0435-0436-Earthwire-A0 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:31
10047111 | OTA-WKM-C-0435-0436-Earthwire-A0 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 11:31
13329919 | OTA-WKM-C-0435-0436-Earthwire-C0 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 | CA copied from EW A0 Feb/2026
13329919 | OTA-WKM-C-0435-0436-Earthwire-C0 | OTA-WKM-C0435-0436 | OTA-WKM-C0435-0436-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-17 | CA copied from EW A0 Feb/2026
10046442 | OTA-WKM-C-0436-Tower | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown. Both CPI's missing.
10046442 | OTA-WKM-C-0436-Tower | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown. Both CPI's missing.
10046442 | OTA-WKM-C-0436-Tower | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown. Both CPI's missing.
10046442 | OTA-WKM-C-0436-Tower | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown. Both CPI's missing.
10046442 | OTA-WKM-C-0436-Tower | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown. Both CPI's missing.
10046442 | OTA-WKM-C-0436-Tower | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown. Both CPI's missing.
10046444 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 15:43
10046444 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:43
10046444 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:43 | Significant corrosion on u bolt nuts
10046444 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:43 | Significant corrosion on caps
10046445 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 15:42
10046445 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:42
10046445 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:42 | Significant corrosion on u bolt nuts
10046445 | OTA-WKM-C-0436-Insulator Set-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:42 | Significant corrosion on caps
10332822 | OTA-WKM-C-0436-Earthwire HW Set | OTA-WKM-C0436 | OTA-WKM-C0436-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:38
10332822 | OTA-WKM-C-0436-Earthwire HW Set | OTA-WKM-C0436 | OTA-WKM-C0436-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 15:38
13040169 | OTA-WKM-C-0436-Earthwire Attachment | OTA-WKM-C0436 | OTA-WKM-C0436-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-10-09 08:00 | Updating to 4 Readings
13040169 | OTA-WKM-C-0436-Earthwire Attachment | OTA-WKM-C0436 | OTA-WKM-C0436-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 15:38
13040169 | OTA-WKM-C-0436-Earthwire Attachment | OTA-WKM-C0436 | OTA-WKM-C0436-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 15:38
13040169 | OTA-WKM-C-0436-Earthwire Attachment | OTA-WKM-C0436 | OTA-WKM-C0436-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-10-09 08:00 | Updating to 4 Readings
13073799 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:39
13073799 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:39
13073799 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:39
13073799 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0436 | OTA-WKM-C0436-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:39
13073800 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:40
13073800 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:40
13073800 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:40
13073800 | OTA-WKM-C-0436-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0436 | OTA-WKM-C0436-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:40
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
13080941 | OTA-WKM-C-0436-Tower Foundation | OTA-WKM-C0436 | OTA-WKM-C0436-00 | 2017 | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 14:26
10047112 | OTA-WKM-C-0436-0437-Conductor-OHW-OTA-2 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 15:37
10047112 | OTA-WKM-C-0436-0437-Conductor-OHW-OTA-2 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:37
10047112 | OTA-WKM-C-0436-0437-Conductor-OHW-OTA-2 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:37
10047113 | OTA-WKM-C-0436-0437-Conductor-OHW-OTA-1 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 15:36
10047113 | OTA-WKM-C-0436-0437-Conductor-OHW-OTA-1 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:36
10047113 | OTA-WKM-C-0436-0437-Conductor-OHW-OTA-1 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 15:36
10047114 | OTA-WKM-C-0436-0437-Earthwire-A0 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 14:35
10047114 | OTA-WKM-C-0436-0437-Earthwire-A0 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 14:35
13329920 | OTA-WKM-C-0436-0437-Earthwire-C0 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 | CA copied from EW A0 Feb/2026
13329920 | OTA-WKM-C-0436-0437-Earthwire-C0 | OTA-WKM-C0436-0437 | OTA-WKM-C0436-0437-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 | CA copied from EW A0 Feb/2026
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2018-05-14 | wo1544119
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046447 | OTA-WKM-C-0437-Tower | OTA-WKM-C0437 | OTA-WKM-C0437-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046449 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-30 13:57
10046449 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 13:57
10046449 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 13:57 | Significant corrosion on u bolt
10046449 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 13:57
10046450 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 13:56
10046450 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 13:56 | Replaced since last inspection
10046450 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 13:56
10046450 | OTA-WKM-C-0437-Insulator Set-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 13:56 | Significant corrosion
10332823 | OTA-WKM-C-0437-Earthwire HW Set | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 13:58
10332823 | OTA-WKM-C-0437-Earthwire HW Set | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-30 13:58
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 12:03
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-30 12:03
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 12:03
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 12:03
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 12:03
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 12:03 | Significant corrosion on steel interface
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-30 12:03
12056614 | OTA-WKM-C-0437-Tower Foundation | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-30 12:03
13216923 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:10
13216923 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:10
13216923 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:10
13216923 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0437 | OTA-WKM-C0437-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:10
13216924 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:09
13216924 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:09
13216924 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:09
13216924 | OTA-WKM-C-0437-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0437 | OTA-WKM-C0437-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:09
13247617 | OTA-WKM-C-0437-Earthwire Attachment | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:11
13247617 | OTA-WKM-C-0437-Earthwire Attachment | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:11
13247617 | OTA-WKM-C-0437-Earthwire Attachment | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:11
13247617 | OTA-WKM-C-0437-Earthwire Attachment | OTA-WKM-C0437 | OTA-WKM-C0437-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-30 12:11
10047115 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-2 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-30 12:17
10047115 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-2 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 12:17
10047115 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-2 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - Dampers Drooping
10047115 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-2 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - Dampers Drooping
10047115 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-2 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 12:17
10047116 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-1 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-30 12:31
10047116 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-1 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 12:31
10047116 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-1 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA
10047116 | OTA-WKM-C-0437-0438-Conductor-OHW-OTA-1 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 12:31
10047117 | OTA-WKM-C-0437-0438-Earthwire-A0 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 14:00
10047117 | OTA-WKM-C-0437-0438-Earthwire-A0 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 14:00
10047117 | OTA-WKM-C-0437-0438-Earthwire-A0 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-08 | CA
10047117 | OTA-WKM-C-0437-0438-Earthwire-A0 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-08-08 | CA
13329921 | OTA-WKM-C-0437-0438-Earthwire-C0 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 | CA copied from EW A0 Feb/2026
13329921 | OTA-WKM-C-0437-0438-Earthwire-C0 | OTA-WKM-C0437-0438 | OTA-WKM-C0437-0438-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-30 | CA copied from EW A0 Feb/2026
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Insulator attachments rusty and metal loss.
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Insulator attachments rusty and metal loss.
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Insulator attachments rusty and metal loss.
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Insulator attachments rusty and metal loss.
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Insulator attachments rusty and metal loss.
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2018-05-14 | wo1544120
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-08 | CA
10046452 | OTA-WKM-C-0438-Tower | OTA-WKM-C0438 | OTA-WKM-C0438-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA - Insulator attachments rusty and metal loss.
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:50
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:50 | Significant corrosion on u bolt nuts
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-29 11:50
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:50
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:50
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:50
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:50
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:50
10046454 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 | 1965 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:50
10046456 | OTA-WKM-C-0438-Earthwire HW Set | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-29 12:26
10046456 | OTA-WKM-C-0438-Earthwire HW Set | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 12:26
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
12056615 | OTA-WKM-C-0438-Tower Foundation | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:51
13040171 | OTA-WKM-C-0438-Earthwire Attachment | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-09 08:00 | Updating to 4 Readings
13040171 | OTA-WKM-C-0438-Earthwire Attachment | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-29 12:26
13040171 | OTA-WKM-C-0438-Earthwire Attachment | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-29 12:26
13040171 | OTA-WKM-C-0438-Earthwire Attachment | OTA-WKM-C0438 | OTA-WKM-C0438-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-09 08:00 | Updating to 4 Readings
13073803 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:34 | Replaced since last inspection
13073803 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:34 | Replaced since last inspection
13073803 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:34 | Been replaced since last inspection
13073803 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-09 | Updating to 4 Readings
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13170129 | OTA-WKM-C-0438-Insulator Set-OHW-OTA-1 | OTA-WKM-C0438 | OTA-WKM-C0438-10 |  | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-29 11:42
13228994 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-14
13228994 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-29 11:34
13228994 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-29 11:34
13228994 | OTA-WKM-C-0438-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0438 | OTA-WKM-C0438-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-10-14
10047118 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-2 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-29 11:59
10047118 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-2 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:59
10047118 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-2 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1999-11-15 | <Not Specified>
10047118 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-2 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA
10047118 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-2 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:59
10047118 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-2 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-20 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 11:59
10047119 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-1 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-08 | CA
10047119 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-1 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-08-08 | CA
10047119 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-1 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1999-11-15 | <Not Specified>
10047119 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-1 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA
10047119 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-1 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA
10047119 | OTA-WKM-C-0438-0439-Conductor-OHW-OTA-1 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-10 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-03 | CA
10047120 | OTA-WKM-C-0438-0439-Earthwire-A0 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 12:32
10047120 | OTA-WKM-C-0438-0439-Earthwire-A0 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 12:32 | Strands pitting
10047120 | OTA-WKM-C-0438-0439-Earthwire-A0 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-08 | CA
10047120 | OTA-WKM-C-0438-0439-Earthwire-A0 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-08-08 | CA
13329922 | OTA-WKM-C-0438-0439-Earthwire-C0 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 | CA copied from EW A0 Feb/2026
13329922 | OTA-WKM-C-0438-0439-Earthwire-C0 | OTA-WKM-C0438-0439 | OTA-WKM-C0438-0439-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-29 | Strands pitting. CA copied from EW A0 Feb/2026
10046457 | OTA-WKM-C-0439-Tower | OTA-WKM-C0439 | OTA-WKM-C0439-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046457 | OTA-WKM-C-0439-Tower | OTA-WKM-C0439 | OTA-WKM-C0439-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046457 | OTA-WKM-C-0439-Tower | OTA-WKM-C0439 | OTA-WKM-C0439-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046457 | OTA-WKM-C-0439-Tower | OTA-WKM-C0439 | OTA-WKM-C0439-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046457 | OTA-WKM-C-0439-Tower | OTA-WKM-C0439 | OTA-WKM-C0439-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046457 | OTA-WKM-C-0439-Tower | OTA-WKM-C0439 | OTA-WKM-C0439-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046459 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 10:28
10046459 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:28 | Wind wear
10046459 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:28 | Rust staining
10046459 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:28 | Flaking rust and wind wear
10046460 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2025-07-01 07:33
10046460 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-01 07:25 | Wind wear
10046460 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-01 07:27 | Significant corrosion
10046460 | OTA-WKM-C-0439-Insulator Set-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-01 07:32 | Significant corrosion on pins and caps
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12056616 | OTA-WKM-C-0439-Tower Foundation | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:10
12058860 | OTA-WKM-C-0439-Earthwire HW Set | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:40
12058860 | OTA-WKM-C-0439-Earthwire HW Set | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:40
13073805 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:39 | Wind wear
13073805 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:39
13073805 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:39
13073805 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0439 | OTA-WKM-C0439-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:39
13073806 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:40 | Wind wear
13073806 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:40
13073806 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:40
13073806 | OTA-WKM-C-0439-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0439 | OTA-WKM-C0439-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:40
13228995 | OTA-WKM-C-0439-Earthwire Attachment | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-05-31
13228995 | OTA-WKM-C-0439-Earthwire Attachment | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:38
13228995 | OTA-WKM-C-0439-Earthwire Attachment | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 10:38
13228995 | OTA-WKM-C-0439-Earthwire Attachment | OTA-WKM-C0439 | OTA-WKM-C0439-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-05-31
10047121 | OTA-WKM-C-0439-0440-Conductor-OHW-OTA-2 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 10:41
10047121 | OTA-WKM-C-0439-0440-Conductor-OHW-OTA-2 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:41
10047121 | OTA-WKM-C-0439-0440-Conductor-OHW-OTA-2 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:41
10047122 | OTA-WKM-C-0439-0440-Conductor-OHW-OTA-1 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 10:41
10047122 | OTA-WKM-C-0439-0440-Conductor-OHW-OTA-1 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:41
10047122 | OTA-WKM-C-0439-0440-Conductor-OHW-OTA-1 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:41
10047123 | OTA-WKM-C-0439-0440-Earthwire-A0 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:43
10047123 | OTA-WKM-C-0439-0440-Earthwire-A0 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 10:43
13329923 | OTA-WKM-C-0439-0440-Earthwire-C0 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 | CA copied from EW A0 Feb/2026
13329923 | OTA-WKM-C-0439-0440-Earthwire-C0 | OTA-WKM-C0439-0440 | OTA-WKM-C0439-0440-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 | CA copied from EW A0 Feb/2026
10046462 | OTA-WKM-C-0440-Tower | OTA-WKM-C0440 | OTA-WKM-C0440-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046462 | OTA-WKM-C-0440-Tower | OTA-WKM-C0440 | OTA-WKM-C0440-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046462 | OTA-WKM-C-0440-Tower | OTA-WKM-C0440 | OTA-WKM-C0440-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046462 | OTA-WKM-C-0440-Tower | OTA-WKM-C0440 | OTA-WKM-C0440-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046462 | OTA-WKM-C-0440-Tower | OTA-WKM-C0440 | OTA-WKM-C0440-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046462 | OTA-WKM-C-0440-Tower | OTA-WKM-C0440 | OTA-WKM-C0440-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-20 10:06
10046462 | OTA-WKM-C-0440-Tower | OTA-WKM-C0440 | OTA-WKM-C0440-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12056617 | OTA-WKM-C-0440-Tower Foundation | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:14
12058861 | OTA-WKM-C-0440-Earthwire HW Set | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:16
12058861 | OTA-WKM-C-0440-Earthwire HW Set | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 09:16
13247618 | OTA-WKM-C-0440-Earthwire Attachment | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-05-31 | WO# 2004036
13247618 | OTA-WKM-C-0440-Earthwire Attachment | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-05-31 | WO# 2004036
13247618 | OTA-WKM-C-0440-Earthwire Attachment | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-05-31 | WO# 2004036
13247618 | OTA-WKM-C-0440-Earthwire Attachment | OTA-WKM-C0440 | OTA-WKM-C0440-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-05-31 | WO# 2004036
13285479 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285479 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285479 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285479 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 | Replaced during RSA2 24-25 Reins Project
13285480 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 15:21
13285480 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 15:20
13285480 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 15:20
13285480 | OTA-WKM-C-0440-Insulator Set-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 15:20
13286399 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 13:24
13286399 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 13:24
13286399 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 13:24
13286399 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0440 | OTA-WKM-C0440-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-30 13:24
13286400 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Att Pt Project
13286400 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Att Pt Project
13286400 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Att Pt Project
13286400 | OTA-WKM-C-0440-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0440 | OTA-WKM-C0440-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-20 | Replaced during RSA2 24-25 Att Pt Project
10047124 | OTA-WKM-C-0440-0441-Conductor-OHW-OTA-2 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 09:46
10047124 | OTA-WKM-C-0440-0441-Conductor-OHW-OTA-2 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 09:46
10047124 | OTA-WKM-C-0440-0441-Conductor-OHW-OTA-2 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-14 | RSA2 25-26 Subconductor Spacer Replacement Project
10047125 | OTA-WKM-C-0440-0441-Conductor-OHW-OTA-1 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 09:45
10047125 | OTA-WKM-C-0440-0441-Conductor-OHW-OTA-1 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 09:45
10047125 | OTA-WKM-C-0440-0441-Conductor-OHW-OTA-1 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 09:45
10047126 | OTA-WKM-C-0440-0441-Earthwire-A0 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 09:46
10047126 | OTA-WKM-C-0440-0441-Earthwire-A0 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 09:46
13329924 | OTA-WKM-C-0440-0441-Earthwire-C0 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 | CA copied from EW A0 Feb/2026
13329924 | OTA-WKM-C-0440-0441-Earthwire-C0 | OTA-WKM-C0440-0441 | OTA-WKM-C0440-0441-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 | CA copied from EW A0 Feb/2026
10046467 | OTA-WKM-C-0441-Tower | OTA-WKM-C0441 | OTA-WKM-C0441-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown.
10046467 | OTA-WKM-C-0441-Tower | OTA-WKM-C0441 | OTA-WKM-C0441-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown.
10046467 | OTA-WKM-C-0441-Tower | OTA-WKM-C0441 | OTA-WKM-C0441-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown.
10046467 | OTA-WKM-C-0441-Tower | OTA-WKM-C0441 | OTA-WKM-C0441-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown.
10046467 | OTA-WKM-C-0441-Tower | OTA-WKM-C0441 | OTA-WKM-C0441-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown.
10046467 | OTA-WKM-C-0441-Tower | OTA-WKM-C0441 | OTA-WKM-C0441-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-14 11:45
10046467 | OTA-WKM-C-0441-Tower | OTA-WKM-C0441 | OTA-WKM-C0441-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA - E/W attachment plates R/C. Tower base overgrown.
10332824 | OTA-WKM-C-0441-Earthwire HW Set | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 12:27
10332824 | OTA-WKM-C-0441-Earthwire HW Set | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 12:27
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
12056618 | OTA-WKM-C-0441-Tower Foundation | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-21 12:12
13040174 | OTA-WKM-C-0441-Earthwire Attachment | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-11-09 08:00 | Updating to 4 Readings
13040174 | OTA-WKM-C-0441-Earthwire Attachment | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 12:27
13040174 | OTA-WKM-C-0441-Earthwire Attachment | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 12:27
13040174 | OTA-WKM-C-0441-Earthwire Attachment | OTA-WKM-C0441 | OTA-WKM-C0441-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-11-09 08:00 | Updating to 4 Readings
13285481 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285481 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285481 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285481 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285482 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 | Replaced 24-25 Reinsulation Project
13285482 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 | Replaced 24-25 Reinsulation Project
13285482 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 | Replaced 24-25 Reinsulation Project
13285482 | OTA-WKM-C-0441-Insulator Set-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 | Replaced 24-25 Reinsulation Project
13286401 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286401 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286401 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286401 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0441 | OTA-WKM-C0441-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286402 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 11:46
13286402 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 11:46
13286402 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 11:46
13286402 | OTA-WKM-C-0441-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0441 | OTA-WKM-C0441-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-14 11:46
10047127 | OTA-WKM-C-0441-0442-Conductor-OHW-OTA-2 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 12:17
10047127 | OTA-WKM-C-0441-0442-Conductor-OHW-OTA-2 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 12:17
10047127 | OTA-WKM-C-0441-0442-Conductor-OHW-OTA-2 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-14 | RSA2 25-26 Subconductor Spacer Replacement Project
10047128 | OTA-WKM-C-0441-0442-Conductor-OHW-OTA-1 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-21 12:17
10047128 | OTA-WKM-C-0441-0442-Conductor-OHW-OTA-1 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 12:17
10047128 | OTA-WKM-C-0441-0442-Conductor-OHW-OTA-1 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-13 | CA
10047128 | OTA-WKM-C-0441-0442-Conductor-OHW-OTA-1 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 12:17
10047129 | OTA-WKM-C-0441-0442-Earthwire-A0 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 12:50
10047129 | OTA-WKM-C-0441-0442-Earthwire-A0 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 12:50
10047129 | OTA-WKM-C-0441-0442-Earthwire-A0 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-11-08 01:00 | CA
13329925 | OTA-WKM-C-0441-0442-Earthwire-C0 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 | CA copied from EW A0 Feb/2026
13329925 | OTA-WKM-C-0441-0442-Earthwire-C0 | OTA-WKM-C0441-0442 | OTA-WKM-C0441-0442-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-21 | CA copied from EW A0 Feb/2026
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046472 | OTA-WKM-C-0442-Tower | OTA-WKM-C0442 | OTA-WKM-C0442-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27 | Significant corrosion
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27 | Significant corrosion
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27 | Significant corrosion
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27 | Dug leg d there significant corrosion
10046473 | OTA-WKM-C-0442-Tower Foundation | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:27
10332825 | OTA-WKM-C-0442-Earthwire HW Set | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:43
10332825 | OTA-WKM-C-0442-Earthwire HW Set | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-22 10:43
13004451 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-22 09:22
13004451 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-22 09:22
13004451 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-22 09:22
13004451 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-22 09:22
13004451 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-02 | Replaced cold end with insulator only hot end recently changed to HAS clamps all looking pretty new attachment point rating 50%.
13004452 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-22 09:23
13004452 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-22 09:23
13004452 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-22 09:23
13004452 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-22 09:23
13004452 | OTA-WKM-C-0442-Insulator Set-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | INSE_WEIGHT COND | Weight Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2017-05-29 | SR100194-Replaced insulators for all 3 phases - OHW-OTA-2 including hot and cold hardware and armour rods
13040175 | OTA-WKM-C-0442-Earthwire Attachment | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-05-19 | Painted to MAD only
13040175 | OTA-WKM-C-0442-Earthwire Attachment | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-23 08:38
13040175 | OTA-WKM-C-0442-Earthwire Attachment | OTA-WKM-C0442 | OTA-WKM-C0442-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-23 08:38
13073811 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:40 | Significant wind wear
13073811 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:40
13073811 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:40
13073811 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0442 | OTA-WKM-C0442-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:40
13073812 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:41 | Rated as per TP specs
13073812 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:41
13073812 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:41
13073812 | OTA-WKM-C-0442-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0442 | OTA-WKM-C0442-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:41 | Significant corrosion
10047130 | OTA-WKM-C-0442-0443-Conductor-OHW-OTA-2 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-22 10:45
10047130 | OTA-WKM-C-0442-0443-Conductor-OHW-OTA-2 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:45
10047130 | OTA-WKM-C-0442-0443-Conductor-OHW-OTA-2 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:45 | Significant corrosion on u-bolt nuts
10047131 | OTA-WKM-C-0442-0443-Conductor-OHW-OTA-1 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-22 10:44
10047131 | OTA-WKM-C-0442-0443-Conductor-OHW-OTA-1 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:44
10047131 | OTA-WKM-C-0442-0443-Conductor-OHW-OTA-1 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:44 | Significant corrosion on u-bolt nut
10047132 | OTA-WKM-C-0442-0443-Earthwire-A0 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:46
10047132 | OTA-WKM-C-0442-0443-Earthwire-A0 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 10:46
13329926 | OTA-WKM-C-0442-0443-Earthwire-C0 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 | CA copied from EW A0 Feb/2026
13329926 | OTA-WKM-C-0442-0443-Earthwire-C0 | OTA-WKM-C0442-0443 | OTA-WKM-C0442-0443-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-22 | CA copied from EW A0 Feb/2026
10046477 | OTA-WKM-C-0443-Tower | OTA-WKM-C0443 | OTA-WKM-C0443-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046477 | OTA-WKM-C-0443-Tower | OTA-WKM-C0443 | OTA-WKM-C0443-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046477 | OTA-WKM-C-0443-Tower | OTA-WKM-C0443 | OTA-WKM-C0443-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046477 | OTA-WKM-C-0443-Tower | OTA-WKM-C0443 | OTA-WKM-C0443-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046477 | OTA-WKM-C-0443-Tower | OTA-WKM-C0443 | OTA-WKM-C0443-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046477 | OTA-WKM-C-0443-Tower | OTA-WKM-C0443 | OTA-WKM-C0443-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10046478 | OTA-WKM-C-0443-Tower Foundation | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 11:19
10332826 | OTA-WKM-C-0443-Earthwire HW Set | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:19
10332826 | OTA-WKM-C-0443-Earthwire HW Set | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 13:19
13040176 | OTA-WKM-C-0443-Earthwire Attachment | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2013-03-15 08:00 | Updating to 4 Readings
13040176 | OTA-WKM-C-0443-Earthwire Attachment | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-28 13:17
13040176 | OTA-WKM-C-0443-Earthwire Attachment | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 13:17
13040176 | OTA-WKM-C-0443-Earthwire Attachment | OTA-WKM-C0443 | OTA-WKM-C0443-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2013-03-15 08:00 | Updating to 4 Readings
13073813 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:18
13073813 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:18
13073813 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:18 | Wind wear
13073813 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:18 | Significant corrosion
13073814 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:19
13073814 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:19
13073814 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:19 | Wind wear
13073814 | OTA-WKM-C-0443-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:19 | Significant corrosion
13186211 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 10:51
13186211 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 10:51
13186211 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 10:51
13186211 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-2 | OTA-WKM-C0443 | OTA-WKM-C0443-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-28 10:51
13218561 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-28 10:50
13218561 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-28 10:50
13218561 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-28 10:50
13218561 | OTA-WKM-C-0443-Insulator Set-OHW-OTA-1 | OTA-WKM-C0443 | OTA-WKM-C0443-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-28 10:50
10047133 | OTA-WKM-C-0443-0444-Conductor-OHW-OTA-2 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 13:15
10047133 | OTA-WKM-C-0443-0444-Conductor-OHW-OTA-2 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:15
10047133 | OTA-WKM-C-0443-0444-Conductor-OHW-OTA-2 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:15 | Significant corrosion on u bolt nuts
10047134 | OTA-WKM-C-0443-0444-Conductor-OHW-OTA-1 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-28 13:14
10047134 | OTA-WKM-C-0443-0444-Conductor-OHW-OTA-1 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:14
10047134 | OTA-WKM-C-0443-0444-Conductor-OHW-OTA-1 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:14 | Significant corrosion on u-bolt nuts
10047135 | OTA-WKM-C-0443-0444-Earthwire-A0 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:21
10047135 | OTA-WKM-C-0443-0444-Earthwire-A0 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 13:21
13329927 | OTA-WKM-C-0443-0444-Earthwire-C0 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 | CA copied from EW A0 Feb/2026
13329927 | OTA-WKM-C-0443-0444-Earthwire-C0 | OTA-WKM-C0443-0444 | OTA-WKM-C0443-0444-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-28 | CA copied from EW A0 Feb/2026
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-06-13 12:49
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046482 | OTA-WKM-C-0444-Tower | OTA-WKM-C0444 | OTA-WKM-C0444-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
10046483 | OTA-WKM-C-0444-Tower Foundation | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 11:25
12058862 | OTA-WKM-C-0444-Earthwire HW Set | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:06
12058862 | OTA-WKM-C-0444-Earthwire HW Set | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-25 12:06
13073815 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:20 | Wind wear
13073815 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:20
13073815 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:20 | Significant corrosion
13073815 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:20 | Significant corrosion
13073816 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:21 | Wind wear
13073816 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:21
13073816 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:21 | Significant corrosion
13073816 | OTA-WKM-C-0444-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:21 | Significant corrosion
13170130 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 | 2018 | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-25 11:27
13170130 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 | 2018 | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:27
13170130 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 | 2018 | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:27
13170130 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-2 | OTA-WKM-C0444 | OTA-WKM-C0444-20 | 2018 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:27
13216925 | OTA-WKM-C-0444-Earthwire Attachment | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:27
13216925 | OTA-WKM-C-0444-Earthwire Attachment | OTA-WKM-C0444 | OTA-WKM-C0444-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:27
13285483 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
13285483 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
13285483 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
13285483 | OTA-WKM-C-0444-Insulator Set-OHW-OTA-1 | OTA-WKM-C0444 | OTA-WKM-C0444-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-13 | Replaced during RSA2 24-25 Reins Project
10047136 | OTA-WKM-C-0444-0445-Conductor-OHW-OTA-2 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-25 12:18
10047136 | OTA-WKM-C-0444-0445-Conductor-OHW-OTA-2 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:18
10047136 | OTA-WKM-C-0444-0445-Conductor-OHW-OTA-2 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:18
10047137 | OTA-WKM-C-0444-0445-Conductor-OHW-OTA-1 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-25 12:17
10047137 | OTA-WKM-C-0444-0445-Conductor-OHW-OTA-1 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:17
10047137 | OTA-WKM-C-0444-0445-Conductor-OHW-OTA-1 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:17
10047138 | OTA-WKM-C-0444-0445-Earthwire-A0 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:08
10047138 | OTA-WKM-C-0444-0445-Earthwire-A0 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 12:08
13329928 | OTA-WKM-C-0444-0445-Earthwire-C0 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 | CA copied from EW A0 Feb/2026
13329928 | OTA-WKM-C-0444-0445-Earthwire-C0 | OTA-WKM-C0444-0445 | OTA-WKM-C0444-0445-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 | CA copied from EW A0 Feb/2026
10046487 | OTA-WKM-C-0445-Tower | OTA-WKM-C0445 | OTA-WKM-C0445-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046487 | OTA-WKM-C-0445-Tower | OTA-WKM-C0445 | OTA-WKM-C0445-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046487 | OTA-WKM-C-0445-Tower | OTA-WKM-C0445 | OTA-WKM-C0445-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046487 | OTA-WKM-C-0445-Tower | OTA-WKM-C0445 | OTA-WKM-C0445-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046487 | OTA-WKM-C-0445-Tower | OTA-WKM-C0445 | OTA-WKM-C0445-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10046487 | OTA-WKM-C-0445-Tower | OTA-WKM-C0445 | OTA-WKM-C0445-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-08-13 | CA
10046487 | OTA-WKM-C-0445-Tower | OTA-WKM-C0445 | OTA-WKM-C0445-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12056620 | OTA-WKM-C-0445-Tower Foundation | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-25 11:36
12058863 | OTA-WKM-C-0445-Earthwire HW Set | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:19
12058863 | OTA-WKM-C-0445-Earthwire HW Set | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-25 14:19
13040178 | OTA-WKM-C-0445-Earthwire Attachment | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-14 08:00 | Updating to 4 Readings
13040178 | OTA-WKM-C-0445-Earthwire Attachment | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:15
13040178 | OTA-WKM-C-0445-Earthwire Attachment | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:15 | Significant loss of metal due of wind wear
13040178 | OTA-WKM-C-0445-Earthwire Attachment | OTA-WKM-C0445 | OTA-WKM-C0445-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-14 08:00 | Updating to 4 Readings
13073817 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:17
13073817 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:17
13073817 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:17
13073817 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:17
13073818 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:18
13073818 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:18
13073818 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:18
13073818 | OTA-WKM-C-0445-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:18
13285484 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-10 | Replaced during RSA2 24-25 Reins Project
13285484 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-10 | Replaced during RSA2 24-25 Reins Project
13285484 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-10 | Replaced during RSA2 24-25 Reins Project
13285484 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-1 | OTA-WKM-C0445 | OTA-WKM-C0445-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-10 | Replaced during RSA2 24-25 Reins Project
13285485 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285485 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285485 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285485 | OTA-WKM-C-0445-Insulator Set-OHW-OTA-2 | OTA-WKM-C0445 | OTA-WKM-C0445-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
10047139 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-2 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-25 14:21
10047139 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-2 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:21
10047139 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-2 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10047139 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-2 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:21
10047140 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-1 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-25 14:20
10047140 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-1 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:20
10047140 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-1 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-23 | Routine CA
10047140 | OTA-WKM-C-0445-0446-Conductor-OHW-OTA-1 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:20
10047141 | OTA-WKM-C-0445-0446-Earthwire-A0 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:22
10047141 | OTA-WKM-C-0445-0446-Earthwire-A0 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 14:22
13329929 | OTA-WKM-C-0445-0446-Earthwire-C0 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 | CA copied from EW A0 Feb/2026
13329929 | OTA-WKM-C-0445-0446-Earthwire-C0 | OTA-WKM-C0445-0446 | OTA-WKM-C0445-0446-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-25 | CA copied from EW A0 Feb/2026
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2025-05-01 09:05
10046492 | OTA-WKM-C-0446-Tower | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046496 | OTA-WKM-C-0446-Earthwire HW Set | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 16:30
10046496 | OTA-WKM-C-0446-Earthwire HW Set | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 16:30
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
12056621 | OTA-WKM-C-0446-Tower Foundation | OTA-WKM-C0446 | OTA-WKM-C0446-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 15:34
13186212 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-15 15:10
13186212 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-15 15:10
13186212 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-15 15:10
13186212 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-15 15:10
13285486 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 | Replaced during 24-25 Ins replacement project
13285486 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 | Replaced during 24-25 Ins replacement project
13285486 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 | Replaced during 24-25 Ins replacement project
13285486 | OTA-WKM-C-0446-Insulator Set-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 | Replaced during 24-25 Ins replacement project
13286404 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Att Pt Project
13286404 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Att Pt Project
13286404 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Att Pt Project
13286404 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0446 | OTA-WKM-C0446-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Att Pt Project
13286405 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 12:26
13286405 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 12:26
13286405 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 | Replaced during RSA2 24-25 Att Pt Project
13286405 | OTA-WKM-C-0446-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0446 | OTA-WKM-C0446-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-11 12:26
13286467 | OTA-WKM-C-0446-Earthwire Attachment | OTA-WKM-C0446 | OTA-WKM-C0446-00 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 | Replaced during RSA2 24-25 Att Pt Project
10047142 | OTA-WKM-C-0446-0447-Conductor-OHW-OTA-2 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-15 15:16
10047142 | OTA-WKM-C-0446-0447-Conductor-OHW-OTA-2 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 15:16
10047142 | OTA-WKM-C-0446-0447-Conductor-OHW-OTA-2 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 15:16
10047143 | OTA-WKM-C-0446-0447-Conductor-OHW-OTA-1 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-15 15:16
10047143 | OTA-WKM-C-0446-0447-Conductor-OHW-OTA-1 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 15:16
10047143 | OTA-WKM-C-0446-0447-Conductor-OHW-OTA-1 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 15:16
10047144 | OTA-WKM-C-0446-0447-Earthwire-A0 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-00 |  | EASE_DAMPER COND | Damper Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-12-08 16:58
10047144 | OTA-WKM-C-0446-0447-Earthwire-A0 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 16:34
10047144 | OTA-WKM-C-0446-0447-Earthwire-A0 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-06-08 | CA
13329930 | OTA-WKM-C-0446-0447-Earthwire-C0 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-00 |  | EASE_DAMPER COND | Damper Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-12-08 | CA copied from EW A0 Feb/2026
13329930 | OTA-WKM-C-0446-0447-Earthwire-C0 | OTA-WKM-C0446-0447 | OTA-WKM-C0446-0447-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 | CA copied from EW A0 Feb/2026
10046497 | OTA-WKM-C-0447-Tower | OTA-WKM-C0447 | OTA-WKM-C0447-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046497 | OTA-WKM-C-0447-Tower | OTA-WKM-C0447 | OTA-WKM-C0447-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046497 | OTA-WKM-C-0447-Tower | OTA-WKM-C0447 | OTA-WKM-C0447-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046497 | OTA-WKM-C-0447-Tower | OTA-WKM-C0447 | OTA-WKM-C0447-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046497 | OTA-WKM-C-0447-Tower | OTA-WKM-C0447 | OTA-WKM-C0447-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046497 | OTA-WKM-C-0447-Tower | OTA-WKM-C0447 | OTA-WKM-C0447-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12056622 | OTA-WKM-C-0447-Tower Foundation | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:25
12058864 | OTA-WKM-C-0447-Earthwire HW Set | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 15:59
12058864 | OTA-WKM-C-0447-Earthwire HW Set | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 15:59
13216926 | OTA-WKM-C-0447-Earthwire Attachment | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-16 15:32
13216926 | OTA-WKM-C-0447-Earthwire Attachment | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-16 15:32
13216926 | OTA-WKM-C-0447-Earthwire Attachment | OTA-WKM-C0447 | OTA-WKM-C0447-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-16 15:32
13285487 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285487 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285487 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285487 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285488 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-21 12:59
13285488 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 12:59
13285488 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 12:59
13285488 | OTA-WKM-C-0447-Insulator Set-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 12:59
13286406 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 19:18
13286406 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 19:18
13286406 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 19:18
13286406 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0447 | OTA-WKM-C0447-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 19:18
13286407 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Att Pt Project
13286407 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Att Pt Project
13286407 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Att Pt Project
13286407 | OTA-WKM-C-0447-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0447 | OTA-WKM-C0447-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 | Replaced during RSA2 24-25 Att Pt Project
10047145 | OTA-WKM-C-0447-0448-Conductor-OHW-OTA-2 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-16 15:04
10047145 | OTA-WKM-C-0447-0448-Conductor-OHW-OTA-2 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 15:04
10047145 | OTA-WKM-C-0447-0448-Conductor-OHW-OTA-2 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 15:04
10047146 | OTA-WKM-C-0447-0448-Conductor-OHW-OTA-1 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-16 15:03
10047146 | OTA-WKM-C-0447-0448-Conductor-OHW-OTA-1 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 15:03
10047146 | OTA-WKM-C-0447-0448-Conductor-OHW-OTA-1 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 15:03
10047147 | OTA-WKM-C-0447-0448-Earthwire-A0 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 15:48
10047147 | OTA-WKM-C-0447-0448-Earthwire-A0 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 15:48
13329931 | OTA-WKM-C-0447-0448-Earthwire-C0 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 | CA copied from EW A0 Feb/2026
13329931 | OTA-WKM-C-0447-0448-Earthwire-C0 | OTA-WKM-C0447-0448 | OTA-WKM-C0447-0448-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 | CA copied from EW A0 Feb/2026
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
10046502 | OTA-WKM-C-0448-Tower | OTA-WKM-C0448 | OTA-WKM-C0448-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-06
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12056623 | OTA-WKM-C-0448-Tower Foundation | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 12:31
12058865 | OTA-WKM-C-0448-Earthwire HW Set | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:27
12058865 | OTA-WKM-C-0448-Earthwire HW Set | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 13:27
13040181 | OTA-WKM-C-0448-Earthwire Attachment | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 13:30 | Has been replaced
13040181 | OTA-WKM-C-0448-Earthwire Attachment | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 13:30 | Has been replaced
13040181 | OTA-WKM-C-0448-Earthwire Attachment | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 13:30 | Has been replaced
13040181 | OTA-WKM-C-0448-Earthwire Attachment | OTA-WKM-C0448 | OTA-WKM-C0448-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 13:30 | Has been replaced
13073823 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:29 | Wind wear
13073823 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:29
13073823 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:29
13073823 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:29
13073824 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:28 | Wind wear
13073824 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:28
13073824 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:28 | Rust staining
13073824 | OTA-WKM-C-0448-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:28
13285489 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 18:43
13285489 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 18:43
13285489 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 18:43
13285489 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-1 | OTA-WKM-C0448 | OTA-WKM-C0448-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 18:43
13285490 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
13285490 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
13285490 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
13285490 | OTA-WKM-C-0448-Insulator Set-OHW-OTA-2 | OTA-WKM-C0448 | OTA-WKM-C0448-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 | Replaced during RSA2 24-25 Reins Project
10047148 | OTA-WKM-C-0448-0449-Conductor-OHW-OTA-2 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-16 13:26
10047148 | OTA-WKM-C-0448-0449-Conductor-OHW-OTA-2 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:26
10047148 | OTA-WKM-C-0448-0449-Conductor-OHW-OTA-2 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10047149 | OTA-WKM-C-0448-0449-Conductor-OHW-OTA-1 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-16 13:25
10047149 | OTA-WKM-C-0448-0449-Conductor-OHW-OTA-1 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:25
10047149 | OTA-WKM-C-0448-0449-Conductor-OHW-OTA-1 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10047150 | OTA-WKM-C-0448-0449-Earthwire-A0 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:48
10047150 | OTA-WKM-C-0448-0449-Earthwire-A0 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 13:48
13329932 | OTA-WKM-C-0448-0449-Earthwire-C0 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 | CA copied from EW A0 Feb/2026
13329932 | OTA-WKM-C-0448-0449-Earthwire-C0 | OTA-WKM-C0448-0449 | OTA-WKM-C0448-0449-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 | CA copied from EW A0 Feb/2026
10046507 | OTA-WKM-C-0449-Tower | OTA-WKM-C0449 | OTA-WKM-C0449-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046507 | OTA-WKM-C-0449-Tower | OTA-WKM-C0449 | OTA-WKM-C0449-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046507 | OTA-WKM-C-0449-Tower | OTA-WKM-C0449 | OTA-WKM-C0449-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046507 | OTA-WKM-C-0449-Tower | OTA-WKM-C0449 | OTA-WKM-C0449-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046507 | OTA-WKM-C-0449-Tower | OTA-WKM-C0449 | OTA-WKM-C0449-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046507 | OTA-WKM-C-0449-Tower | OTA-WKM-C0449 | OTA-WKM-C0449-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-21 17:14
10046507 | OTA-WKM-C-0449-Tower | OTA-WKM-C0449 | OTA-WKM-C0449-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12056624 | OTA-WKM-C-0449-Tower Foundation | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-16 11:37
12058866 | OTA-WKM-C-0449-Earthwire HW Set | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 11:56
12058866 | OTA-WKM-C-0449-Earthwire HW Set | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-16 11:56
13040182 | OTA-WKM-C-0449-Earthwire Attachment | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 06:06 | New attachment point installed
13040182 | OTA-WKM-C-0449-Earthwire Attachment | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 06:03 | Fitted with new M16X70 DN
13040182 | OTA-WKM-C-0449-Earthwire Attachment | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 06:01 | New attachment point installed
13040182 | OTA-WKM-C-0449-Earthwire Attachment | OTA-WKM-C0449 | OTA-WKM-C0449-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-16 06:08 | Fitted with M16X70 DN
13285491 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285491 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285491 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285491 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285492 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:11
13285492 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:10
13285492 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:10
13285492 | OTA-WKM-C-0449-Insulator Set-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:10
13286408 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286408 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286408 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286408 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0449 | OTA-WKM-C0449-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286409 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:12
13286409 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:12
13286409 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:12
13286409 | OTA-WKM-C-0449-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0449 | OTA-WKM-C0449-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-21 17:12
10047151 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-2 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-16 11:33
10047151 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-2 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 11:33
10047151 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-2 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10047151 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-2 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-20 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10047151 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-2 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 11:33 | Significant corrosion on u-bolt nut
10047152 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-1 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-16 11:33
10047152 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-1 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 11:33
10047152 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-1 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10047152 | OTA-WKM-C-0449-0450-Conductor-OHW-OTA-1 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 11:33 | Significant corrosion on u-bolt nut
10047153 | OTA-WKM-C-0449-0450-Earthwire-A0 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 12:13
10047153 | OTA-WKM-C-0449-0450-Earthwire-A0 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 12:13
13329933 | OTA-WKM-C-0449-0450-Earthwire-C0 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 | CA copied from EW A0 Feb/2026
13329933 | OTA-WKM-C-0449-0450-Earthwire-C0 | OTA-WKM-C0449-0450 | OTA-WKM-C0449-0450-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-16 | CA copied from EW A0 Feb/2026
10046512 | OTA-WKM-C-0450-Tower | OTA-WKM-C0450 | OTA-WKM-C0450-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates have metal loss. Insulator attachment steel rusty.
10046512 | OTA-WKM-C-0450-Tower | OTA-WKM-C0450 | OTA-WKM-C0450-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates have metal loss. Insulator attachment steel rusty.
10046512 | OTA-WKM-C-0450-Tower | OTA-WKM-C0450 | OTA-WKM-C0450-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates have metal loss. Insulator attachment steel rusty.
10046512 | OTA-WKM-C-0450-Tower | OTA-WKM-C0450 | OTA-WKM-C0450-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates have metal loss. Insulator attachment steel rusty.
10046512 | OTA-WKM-C-0450-Tower | OTA-WKM-C0450 | OTA-WKM-C0450-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates have metal loss. Insulator attachment steel rusty.
10046512 | OTA-WKM-C-0450-Tower | OTA-WKM-C0450 | OTA-WKM-C0450-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2025-03-22 10:41
10046512 | OTA-WKM-C-0450-Tower | OTA-WKM-C0450 | OTA-WKM-C0450-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates have metal loss. Insulator attachment steel rusty.
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10046513 | OTA-WKM-C-0450-Tower Foundation | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:04
10332827 | OTA-WKM-C-0450-Earthwire HW Set | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 10:47
10332827 | OTA-WKM-C-0450-Earthwire HW Set | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 10:47
13040183 | OTA-WKM-C-0450-Earthwire Attachment | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-22 08:00 | Updating to 4 Readings
13040183 | OTA-WKM-C-0450-Earthwire Attachment | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:08
13040183 | OTA-WKM-C-0450-Earthwire Attachment | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 10:08
13040183 | OTA-WKM-C-0450-Earthwire Attachment | OTA-WKM-C0450 | OTA-WKM-C0450-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-22 08:00 | Updating to 4 Readings
13204573 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:06
13204573 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:06
13204573 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:06
13204573 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:06
13204574 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:08
13204574 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:08
13204574 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:08
13204574 | OTA-WKM-C-0450-Insulator Set-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 10:08
13286410 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Att Pt Project
13286410 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Att Pt Project
13286410 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Att Pt Project
13286410 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0450 | OTA-WKM-C0450-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | Replaced during RSA2 24-25 Att Pt Project
13286411 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-22 10:44
13286411 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-22 10:44
13286411 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-22 10:44
13286411 | OTA-WKM-C-0450-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0450 | OTA-WKM-C0450-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-22 10:44
10047154 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-2 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 10:12
10047154 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-2 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-20 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 10:12
10047154 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-2 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10047154 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-2 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 10:12
10047155 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-1 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 10:12
10047155 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-1 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-10 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 10:12
10047155 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-1 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10047155 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-1 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-10 | 1965 | COSE_REPAIR SLEEVE COND | Repair Sleeve Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10047155 | OTA-WKM-C-0450-0451-Conductor-OHW-OTA-1 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 10:12
10047156 | OTA-WKM-C-0450-0451-Earthwire-A0 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 11:03
10047156 | OTA-WKM-C-0450-0451-Earthwire-A0 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 11:03
10047156 | OTA-WKM-C-0450-0451-Earthwire-A0 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-06-08 | CA
13329934 | OTA-WKM-C-0450-0451-Earthwire-C0 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 | CA copied from EW A0 Feb/2026
13329934 | OTA-WKM-C-0450-0451-Earthwire-C0 | OTA-WKM-C0450-0451 | OTA-WKM-C0450-0451-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 | CA copied from EW A0 Feb/2026
10046517 | OTA-WKM-C-0451-Tower | OTA-WKM-C0451 | OTA-WKM-C0451-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046517 | OTA-WKM-C-0451-Tower | OTA-WKM-C0451 | OTA-WKM-C0451-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046517 | OTA-WKM-C-0451-Tower | OTA-WKM-C0451 | OTA-WKM-C0451-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046517 | OTA-WKM-C-0451-Tower | OTA-WKM-C0451 | OTA-WKM-C0451-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046517 | OTA-WKM-C-0451-Tower | OTA-WKM-C0451 | OTA-WKM-C0451-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046517 | OTA-WKM-C-0451-Tower | OTA-WKM-C0451 | OTA-WKM-C0451-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36 | Rated as per TP specs
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36 | Rated as per TP specs
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36 | Rated as per TP specs
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36 | Rated as per TP specs
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36 | Rated as per TP specs
10046518 | OTA-WKM-C-0451-Tower Foundation | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 15:36 | Rated as per TP specs
10046521 | OTA-WKM-C-0451-Earthwire HW Set | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 16:00 | Rough surface
10046521 | OTA-WKM-C-0451-Earthwire HW Set | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 16:00 | Wind wear
13040184 | OTA-WKM-C-0451-Earthwire Attachment | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2014-03-13 08:00 | Updating to 4 Readings
13040184 | OTA-WKM-C-0451-Earthwire Attachment | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:55
13040184 | OTA-WKM-C-0451-Earthwire Attachment | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:55
13040184 | OTA-WKM-C-0451-Earthwire Attachment | OTA-WKM-C0451 | OTA-WKM-C0451-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2014-03-13 08:00 | Updating to 4 Readings
13073829 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:57
13073829 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:57
13073829 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:57
13073829 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:57
13073830 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:58
13073830 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:58
13073830 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:58
13073830 | OTA-WKM-C-0451-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 15:58
13285493 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-11 17:51
13285493 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-11 17:51
13285493 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-11 17:51
13285493 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-1 | OTA-WKM-C0451 | OTA-WKM-C0451-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-11 17:51
13285494 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during 24-25 REINS Project
13285494 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during 24-25 REINS Project
13285494 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during 24-25 REINS Project
13285494 | OTA-WKM-C-0451-Insulator Set-OHW-OTA-2 | OTA-WKM-C0451 | OTA-WKM-C0451-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during 24-25 REINS Project
10047157 | OTA-WKM-C-0451-0452-Conductor-OHW-OTA-2 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 16:00
10047157 | OTA-WKM-C-0451-0452-Conductor-OHW-OTA-2 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 16:00
10047157 | OTA-WKM-C-0451-0452-Conductor-OHW-OTA-2 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10047158 | OTA-WKM-C-0451-0452-Conductor-OHW-OTA-1 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 14:09
10047158 | OTA-WKM-C-0451-0452-Conductor-OHW-OTA-1 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 14:09
10047158 | OTA-WKM-C-0451-0452-Conductor-OHW-OTA-1 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10047159 | OTA-WKM-C-0451-0452-Earthwire-A0 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 16:02
10047159 | OTA-WKM-C-0451-0452-Earthwire-A0 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 16:02
13329935 | OTA-WKM-C-0451-0452-Earthwire-C0 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 | CA copied from EW A0 Feb/2026
13329935 | OTA-WKM-C-0451-0452-Earthwire-C0 | OTA-WKM-C0451-0452 | OTA-WKM-C0451-0452-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 | CA copied from EW A0 Feb/2026
10046522 | OTA-WKM-C-0452-Tower | OTA-WKM-C0452 | OTA-WKM-C0452-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046522 | OTA-WKM-C-0452-Tower | OTA-WKM-C0452 | OTA-WKM-C0452-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046522 | OTA-WKM-C-0452-Tower | OTA-WKM-C0452 | OTA-WKM-C0452-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046522 | OTA-WKM-C-0452-Tower | OTA-WKM-C0452 | OTA-WKM-C0452-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046522 | OTA-WKM-C-0452-Tower | OTA-WKM-C0452 | OTA-WKM-C0452-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046522 | OTA-WKM-C-0452-Tower | OTA-WKM-C0452 | OTA-WKM-C0452-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
10046523 | OTA-WKM-C-0452-Tower Foundation | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:49
12058867 | OTA-WKM-C-0452-Earthwire HW Set | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:18 | Roughing of surface strand
12058867 | OTA-WKM-C-0452-Earthwire HW Set | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-10 13:18
13040185 | OTA-WKM-C-0452-Earthwire Attachment | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2019-08-15 08:00 | Updating to 4 Readings
13040185 | OTA-WKM-C-0452-Earthwire Attachment | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-10 12:55
13040185 | OTA-WKM-C-0452-Earthwire Attachment | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:55
13040185 | OTA-WKM-C-0452-Earthwire Attachment | OTA-WKM-C0452 | OTA-WKM-C0452-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2019-08-15 08:00 | Updating to 4 Readings
13073831 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:14 | Wind wear
13073831 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:14
13073831 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:14
13073831 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:14 | Significant rust on through bolt nut
13073832 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:16 | Staining
13073832 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:16
13073832 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:16 | Staining
13073832 | OTA-WKM-C-0452-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:16 | Significant rust on through bolt and nut
13204575 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-10 13:10
13204575 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-10 13:10
13204575 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-10 13:10
13204575 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-1 | OTA-WKM-C0452 | OTA-WKM-C0452-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-10 13:10
13204576 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-10 13:10
13204576 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-10 13:10
13204576 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-10 13:10
13204576 | OTA-WKM-C-0452-Insulator Set-OHW-OTA-2 | OTA-WKM-C0452 | OTA-WKM-C0452-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-10 13:10
10047160 | OTA-WKM-C-0452-0453-Conductor-OHW-OTA-2 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:59
10047160 | OTA-WKM-C-0452-0453-Conductor-OHW-OTA-2 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 12:59
10047160 | OTA-WKM-C-0452-0453-Conductor-OHW-OTA-2 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 12:59
10047161 | OTA-WKM-C-0452-0453-Conductor-OHW-OTA-1 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-10 12:58
10047161 | OTA-WKM-C-0452-0453-Conductor-OHW-OTA-1 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 12:58
10047161 | OTA-WKM-C-0452-0453-Conductor-OHW-OTA-1 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 12:58
10047162 | OTA-WKM-C-0452-0453-Earthwire-A0 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:20
10047162 | OTA-WKM-C-0452-0453-Earthwire-A0 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 13:20
13329936 | OTA-WKM-C-0452-0453-Earthwire-C0 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 | CA copied from EW A0 Feb/2026
13329936 | OTA-WKM-C-0452-0453-Earthwire-C0 | OTA-WKM-C0452-0453 | OTA-WKM-C0452-0453-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-10 | CA copied from EW A0 Feb/2026
10046527 | OTA-WKM-C-0453-Tower | OTA-WKM-C0453 | OTA-WKM-C0453-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-10 | Fitted Climbing Deterrent to tower 7.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046527 | OTA-WKM-C-0453-Tower | OTA-WKM-C0453 | OTA-WKM-C0453-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-10 | Fitted Climbing Deterrent to tower 7.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046527 | OTA-WKM-C-0453-Tower | OTA-WKM-C0453 | OTA-WKM-C0453-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-10 | Fitted Climbing Deterrent to tower 7.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046527 | OTA-WKM-C-0453-Tower | OTA-WKM-C0453 | OTA-WKM-C0453-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-10 | Fitted Climbing Deterrent to tower 7.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046527 | OTA-WKM-C-0453-Tower | OTA-WKM-C0453 | OTA-WKM-C0453-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-10 | Fitted Climbing Deterrent to tower 7.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046527 | OTA-WKM-C-0453-Tower | OTA-WKM-C0453 | OTA-WKM-C0453-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-03-08 01:00 | CA
10046527 | OTA-WKM-C-0453-Tower | OTA-WKM-C0453 | OTA-WKM-C0453-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-10 | Fitted Climbing Deterrent to tower 7.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37 | Mortar crumbling
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37 | Mortar crumbling
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37 | Mortar crumbling
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37
10046528 | OTA-WKM-C-0453-Tower Foundation | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:37 | Mortar crumbling
10046531 | OTA-WKM-C-0453-Earthwire HW Set | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 14:57 | Severe degradation of coating
10046531 | OTA-WKM-C-0453-Earthwire HW Set | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-07 14:57
13073833 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:12 | Wind wear
13073833 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:12
13073833 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:12 | Surface rust
13073833 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:12
13073834 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:13 | Wind wear
13073834 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:13
13073834 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:13 | Surface rust
13073834 | OTA-WKM-C-0453-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:13
13245503 | OTA-WKM-C-0453-Earthwire Attachment | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-07 14:54
13245503 | OTA-WKM-C-0453-Earthwire Attachment | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-07 14:54
13245503 | OTA-WKM-C-0453-Earthwire Attachment | OTA-WKM-C0453 | OTA-WKM-C0453-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-07 14:54
13285495 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285495 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285495 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285495 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-1 | OTA-WKM-C0453 | OTA-WKM-C0453-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Replaced during RSA2 TL Insulators 24-25 project
13285496 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during RSA2 24-25 Reins Project
13285496 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during RSA2 24-25 Reins Project
13285496 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during RSA2 24-25 Reins Project
13285496 | OTA-WKM-C-0453-Insulator Set-OHW-OTA-2 | OTA-WKM-C0453 | OTA-WKM-C0453-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-30 | Replaced during RSA2 24-25 Reins Project
10047163 | OTA-WKM-C-0453-0454-Conductor-OHW-OTA-2 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 15:26
10047163 | OTA-WKM-C-0453-0454-Conductor-OHW-OTA-2 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:26
10047163 | OTA-WKM-C-0453-0454-Conductor-OHW-OTA-2 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:26 | Significant rust on U-bolt and nuts
10047164 | OTA-WKM-C-0453-0454-Conductor-OHW-OTA-1 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 15:26
10047164 | OTA-WKM-C-0453-0454-Conductor-OHW-OTA-1 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:26
10047164 | OTA-WKM-C-0453-0454-Conductor-OHW-OTA-1 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10047164 | OTA-WKM-C-0453-0454-Conductor-OHW-OTA-1 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:26 | Significant rust on U-bolt and nuts
10047165 | OTA-WKM-C-0453-0454-Earthwire-A0 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:30
10047165 | OTA-WKM-C-0453-0454-Earthwire-A0 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 15:30 | Cross-sectional metal loss
13329937 | OTA-WKM-C-0453-0454-Earthwire-C0 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 | CA copied from EW A0 Feb/2026
13329937 | OTA-WKM-C-0453-0454-Earthwire-C0 | OTA-WKM-C0453-0454 | OTA-WKM-C0453-0454-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 | Cross-sectional metal loss. CA copied from EW A0 Feb/2026
10046532 | OTA-WKM-C-0454-Tower | OTA-WKM-C0454 | OTA-WKM-C0454-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046532 | OTA-WKM-C-0454-Tower | OTA-WKM-C0454 | OTA-WKM-C0454-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046532 | OTA-WKM-C-0454-Tower | OTA-WKM-C0454 | OTA-WKM-C0454-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046532 | OTA-WKM-C-0454-Tower | OTA-WKM-C0454 | OTA-WKM-C0454-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046532 | OTA-WKM-C-0454-Tower | OTA-WKM-C0454 | OTA-WKM-C0454-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046532 | OTA-WKM-C-0454-Tower | OTA-WKM-C0454 | OTA-WKM-C0454-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-14
10046532 | OTA-WKM-C-0454-Tower | OTA-WKM-C0454 | OTA-WKM-C0454-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 12:09
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:09
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 12:09
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:09
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 12:09
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:09
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-14 12:09
10046533 | OTA-WKM-C-0454-Tower Foundation | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:09
10046536 | OTA-WKM-C-0454-Earthwire HW Set | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 12:26
10046536 | OTA-WKM-C-0454-Earthwire HW Set | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 12:26
13040187 | OTA-WKM-C-0454-Earthwire Attachment | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 12:13 | Replaced the attachment point
13040187 | OTA-WKM-C-0454-Earthwire Attachment | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 12:13 | Replaced the attachment point bolts
13040187 | OTA-WKM-C-0454-Earthwire Attachment | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 12:12 | Replaced the attachment point steel
13040187 | OTA-WKM-C-0454-Earthwire Attachment | OTA-WKM-C0454 | OTA-WKM-C0454-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-10 12:14 | Replaced the attachment point through bolts and nut
13073835 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:25
13073835 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:25
13073835 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:25
13073835 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:25
13073836 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:26
13073836 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:26
13073836 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:26
13073836 | OTA-WKM-C-0454-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:26
13186213 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:48
13186213 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:48
13186213 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:48
13186213 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-1 | OTA-WKM-C0454 | OTA-WKM-C0454-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:48
13204577 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:49
13204577 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:49
13204577 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:49
13204577 | OTA-WKM-C-0454-Insulator Set-OHW-OTA-2 | OTA-WKM-C0454 | OTA-WKM-C0454-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-11-14 11:49
10047166 | OTA-WKM-C-0454-0455-Conductor-OHW-OTA-2 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 11:53
10047166 | OTA-WKM-C-0454-0455-Conductor-OHW-OTA-2 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 11:53
10047166 | OTA-WKM-C-0454-0455-Conductor-OHW-OTA-2 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 11:53
10047167 | OTA-WKM-C-0454-0455-Conductor-OHW-OTA-1 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 11:52
10047167 | OTA-WKM-C-0454-0455-Conductor-OHW-OTA-1 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 11:52
10047167 | OTA-WKM-C-0454-0455-Conductor-OHW-OTA-1 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 11:52
10047168 | OTA-WKM-C-0454-0455-Earthwire-A0 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:44
10047168 | OTA-WKM-C-0454-0455-Earthwire-A0 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 12:44
10047168 | OTA-WKM-C-0454-0455-Earthwire-A0 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-30 | CA
13329938 | OTA-WKM-C-0454-0455-Earthwire-C0 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 | CA copied from EW A0 Feb/2026
13329938 | OTA-WKM-C-0454-0455-Earthwire-C0 | OTA-WKM-C0454-0455 | OTA-WKM-C0454-0455-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 | CA copied from EW A0 Feb/2026
10046537 | OTA-WKM-C-0455-Tower | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046537 | OTA-WKM-C-0455-Tower | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046537 | OTA-WKM-C-0455-Tower | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046537 | OTA-WKM-C-0455-Tower | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046537 | OTA-WKM-C-0455-Tower | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046537 | OTA-WKM-C-0455-Tower | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2025-06-09 10:37
10046537 | OTA-WKM-C-0455-Tower | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09 | Rust stain
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09 | Rust stain
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09 | Rust stain
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09
10046538 | OTA-WKM-C-0455-Tower Foundation | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:09 | Rust staining
10046539 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 15:25
10046539 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:25
10046539 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:25
10046539 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:25 | Significant rust on the ball and pins
10046540 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 15:24
10046540 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:24
10046540 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:24
10046540 | OTA-WKM-C-0455-Insulator Set-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:24 | Significant rust on ball and pins
12058868 | OTA-WKM-C-0455-Earthwire HW Set | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:11 | Rust on the strand
12058868 | OTA-WKM-C-0455-Earthwire HW Set | OTA-WKM-C0455 | OTA-WKM-C0455-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 16:11
13073838 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:20 | Wind wear
13073838 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:20 | Rust staining
13073838 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:20 | Wind wear
13073838 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0455 | OTA-WKM-C0455-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:20 | Minor metal loss
13286413 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-09 | Replaced during RSA2 24-25 Att Pt Project
13286413 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-09 | Replaced during RSA2 24-25 Att Pt Project
13286413 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-09 | Replaced during RSA2 24-25 Att Pt Project
13286413 | OTA-WKM-C-0455-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0455 | OTA-WKM-C0455-10 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-09 | Replaced during RSA2 24-25 Att Pt Project
13286470 | OTA-WKM-C-0455-Earthwire Attachment | OTA-WKM-C0455 | OTA-WKM-C0455-00 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-04-11 | Replaced during RSA2 24-25 Att Pt Project
10047169 | OTA-WKM-C-0455-0456-Conductor-OHW-OTA-2 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 15:27
10047169 | OTA-WKM-C-0455-0456-Conductor-OHW-OTA-2 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:27
10047169 | OTA-WKM-C-0455-0456-Conductor-OHW-OTA-2 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:27 | Significant rust on the ubolt and ring
10047170 | OTA-WKM-C-0455-0456-Conductor-OHW-OTA-1 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-14 15:27
10047170 | OTA-WKM-C-0455-0456-Conductor-OHW-OTA-1 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:27
10047170 | OTA-WKM-C-0455-0456-Conductor-OHW-OTA-1 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 15:27 | Significant rust ubolt nut and ring
10047171 | OTA-WKM-C-0455-0456-Earthwire-A0 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:05
10047171 | OTA-WKM-C-0455-0456-Earthwire-A0 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 16:05
13329939 | OTA-WKM-C-0455-0456-Earthwire-C0 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 | CA copied from EW A0 Feb/2026
13329939 | OTA-WKM-C-0455-0456-Earthwire-C0 | OTA-WKM-C0455-0456 | OTA-WKM-C0455-0456-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-14 | CA copied from EW A0 Feb/2026
10046542 | OTA-WKM-C-0456-Tower | OTA-WKM-C0456 | OTA-WKM-C0456-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046542 | OTA-WKM-C-0456-Tower | OTA-WKM-C0456 | OTA-WKM-C0456-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046542 | OTA-WKM-C-0456-Tower | OTA-WKM-C0456 | OTA-WKM-C0456-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046542 | OTA-WKM-C-0456-Tower | OTA-WKM-C0456 | OTA-WKM-C0456-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046542 | OTA-WKM-C-0456-Tower | OTA-WKM-C0456 | OTA-WKM-C0456-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046542 | OTA-WKM-C-0456-Tower | OTA-WKM-C0456 | OTA-WKM-C0456-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-24 18:11
10046542 | OTA-WKM-C-0456-Tower | OTA-WKM-C0456 | OTA-WKM-C0456-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 | Routine CA
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Rust beginning to pit steel below ground level.
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Loss of metal and pitting.
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Rust beginning to pit steel below ground level
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Loss of metal and pitting.
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Rust beginning to pit steel below ground level
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Loss of metal and pitting
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Rust beginning to pit steel below ground level
10046543 | OTA-WKM-C-0456-Tower Foundation | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 12:33 | Loss of metal and pitting
12058869 | OTA-WKM-C-0456-Earthwire HW Set | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 13:09
12058869 | OTA-WKM-C-0456-Earthwire HW Set | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-25 13:09
13040189 | OTA-WKM-C-0456-Earthwire Attachment | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-25 13:08 | Have been replaced
13040189 | OTA-WKM-C-0456-Earthwire Attachment | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-25 13:08 | Have been replaced
13040189 | OTA-WKM-C-0456-Earthwire Attachment | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-25 13:08 | Have been replaced
13040189 | OTA-WKM-C-0456-Earthwire Attachment | OTA-WKM-C0456 | OTA-WKM-C0456-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-25 13:08 | Have been replaced
13216927 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13216927 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13216927 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13216927 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13232478 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13232478 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13232478 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13232478 | OTA-WKM-C-0456-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-25 13:08
13285497 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285497 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285497 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285497 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-1 | OTA-WKM-C0456 | OTA-WKM-C0456-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-30 | Replaced during RSA2 TL Insulators 24-25 project
13285498 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 15:07
13285498 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 15:07
13285498 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 15:07
13285498 | OTA-WKM-C-0456-Insulator Set-OHW-OTA-2 | OTA-WKM-C0456 | OTA-WKM-C0456-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 15:07
10047172 | OTA-WKM-C-0456-0457-Conductor-OHW-OTA-2 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-25 18:09
10047172 | OTA-WKM-C-0456-0457-Conductor-OHW-OTA-2 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 18:09
10047172 | OTA-WKM-C-0456-0457-Conductor-OHW-OTA-2 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 18:09 | Significant corrosion on ring and nuts
10047173 | OTA-WKM-C-0456-0457-Conductor-OHW-OTA-1 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-25 18:08
10047173 | OTA-WKM-C-0456-0457-Conductor-OHW-OTA-1 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 18:08
10047173 | OTA-WKM-C-0456-0457-Conductor-OHW-OTA-1 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 18:08 | Significant corrosion on rings and nuts
10047174 | OTA-WKM-C-0456-0457-Earthwire-A0 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 13:10
10047174 | OTA-WKM-C-0456-0457-Earthwire-A0 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 13:10
13329940 | OTA-WKM-C-0456-0457-Earthwire-C0 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 | CA copied from EW A0 Feb/2026
13329940 | OTA-WKM-C-0456-0457-Earthwire-C0 | OTA-WKM-C0456-0457 | OTA-WKM-C0456-0457-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 | CA copied from EW A0 Feb/2026
10046547 | OTA-WKM-C-0457-Tower | OTA-WKM-C0457 | OTA-WKM-C0457-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046547 | OTA-WKM-C-0457-Tower | OTA-WKM-C0457 | OTA-WKM-C0457-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046547 | OTA-WKM-C-0457-Tower | OTA-WKM-C0457 | OTA-WKM-C0457-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046547 | OTA-WKM-C-0457-Tower | OTA-WKM-C0457 | OTA-WKM-C0457-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046547 | OTA-WKM-C-0457-Tower | OTA-WKM-C0457 | OTA-WKM-C0457-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046547 | OTA-WKM-C-0457-Tower | OTA-WKM-C0457 | OTA-WKM-C0457-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-01-08 01:00 | CA
10046547 | OTA-WKM-C-0457-Tower | OTA-WKM-C0457 | OTA-WKM-C0457-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-19 | Routine CA
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Metal loss on main leg
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Severe rust of steel.
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Metal loss on main leg
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Severe rust of steel.
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Metal loss on main leg
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Severe rust on steel
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Metal loss on main leg
10046548 | OTA-WKM-C-0457-Tower Foundation | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:01 | Severe rust on steel Dug leg D
10046549 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:18
10046549 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:18
10046549 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:18
10046549 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:18 | Loss of metal and build up corrosion.
10046550 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:33
10046550 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:33
10046550 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:33 | Loss of metal and corrosion on clamp nuts.
10046550 | OTA-WKM-C-0457-Insulator Set-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:33 | Loss of metal and build up corrosion.
10046551 | OTA-WKM-C-0457-Earthwire HW Set | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:07
10046551 | OTA-WKM-C-0457-Earthwire HW Set | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:07
13040190 | OTA-WKM-C-0457-Earthwire Attachment | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:20 | Minor loss of metal and corrosion.
13040190 | OTA-WKM-C-0457-Earthwire Attachment | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:20
13040190 | OTA-WKM-C-0457-Earthwire Attachment | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-01-09 08:00 | Updating to 4 Readings
13040190 | OTA-WKM-C-0457-Earthwire Attachment | OTA-WKM-C0457 | OTA-WKM-C0457-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-01-09 08:00 | Updating to 4 Readings
13073841 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
13073841 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
13073841 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
13073841 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0457 | OTA-WKM-C0457-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
13073842 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
13073842 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
13073842 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
13073842 | OTA-WKM-C-0457-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0457 | OTA-WKM-C0457-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:21
10047175 | OTA-WKM-C-0457-0458-Conductor-OHW-OTA-2 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-25 14:34
10047175 | OTA-WKM-C-0457-0458-Conductor-OHW-OTA-2 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:34
10047175 | OTA-WKM-C-0457-0458-Conductor-OHW-OTA-2 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:34 | Minor rust on bolts
10047176 | OTA-WKM-C-0457-0458-Conductor-OHW-OTA-1 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-25 14:34
10047176 | OTA-WKM-C-0457-0458-Conductor-OHW-OTA-1 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:34
10047176 | OTA-WKM-C-0457-0458-Conductor-OHW-OTA-1 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:34 | Minor rust on bolts
10047177 | OTA-WKM-C-0457-0458-Earthwire-A0 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-25 14:35
10047177 | OTA-WKM-C-0457-0458-Earthwire-A0 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 14:35 | Severe corrosion on earth wire strands
10047177 | OTA-WKM-C-0457-0458-Earthwire-A0 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-01-08 01:00 | CA
13329941 | OTA-WKM-C-0457-0458-Earthwire-C0 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-25 | CA copied from EW A0 Feb/2026
13329941 | OTA-WKM-C-0457-0458-Earthwire-C0 | OTA-WKM-C0457-0458 | OTA-WKM-C0457-0458-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-25 | Severe corrosion on earth wire strands. CA copied from EW A0 Feb/2026
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - Rust on all swivel bolts and attachments. Crossarm steel rusty.
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - Rust on all swivel bolts and attachments. Crossarm steel rusty.
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - Rust on all swivel bolts and attachments. Crossarm steel rusty.
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - Rust on all swivel bolts and attachments. Crossarm steel rusty.
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - Rust on all swivel bolts and attachments. Crossarm steel rusty.
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-01-08 01:00 | CA
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-01-08 01:00 | CA
10046552 | OTA-WKM-C-0458-Tower | OTA-WKM-C0458 | OTA-WKM-C0458-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - Rust on all swivel bolts and attachments. Crossarm steel rusty.
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046553 | OTA-WKM-C-0458-Tower Foundation | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:33
10046556 | OTA-WKM-C-0458-Earthwire HW Set | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W hardware rusty.
10046556 | OTA-WKM-C-0458-Earthwire HW Set | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 10:22
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:18
12006206 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2009 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:18
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:20
12006207 | OTA-WKM-C-0458-Insulator Set-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2008 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:20
13040191 | OTA-WKM-C-0458-Earthwire Attachment | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 10:21
13040191 | OTA-WKM-C-0458-Earthwire Attachment | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:21
13040191 | OTA-WKM-C-0458-Earthwire Attachment | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 10:21
13040191 | OTA-WKM-C-0458-Earthwire Attachment | OTA-WKM-C0458 | OTA-WKM-C0458-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 10:21
13171904 | OTA-WKM-C-0458-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2018 | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-08 10:20
13171904 | OTA-WKM-C-0458-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2018 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-08 10:20
13171904 | OTA-WKM-C-0458-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0458 | OTA-WKM-C0458-10 | 2018 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-08 10:20
13171905 | OTA-WKM-C-0458-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2018 | ATCA_POINT_CONDITION | Attachment Point Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-08 10:21
13171905 | OTA-WKM-C-0458-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2018 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-08 10:21
13171905 | OTA-WKM-C-0458-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0458 | OTA-WKM-C0458-20 | 2018 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-11-08 10:21
10047178 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-2 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 09:41
10047178 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-2 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:41
10047178 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-2 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1999-11-22 | <Not Specified>
10047178 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-2 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2011-05-05 | CA
10047178 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-2 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:41
10047179 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-1 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 09:41
10047179 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-1 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:41
10047179 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-1 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1999-11-22 | <Not Specified>
10047179 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-1 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2011-05-05 | CA
10047179 | OTA-WKM-C-0458-0459-Conductor-OHW-OTA-1 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 09:41
10047180 | OTA-WKM-C-0458-0459-Earthwire-A0 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 10:23
10047180 | OTA-WKM-C-0458-0459-Earthwire-A0 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 10:23
10047180 | OTA-WKM-C-0458-0459-Earthwire-A0 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-01-08 01:00 | CA
13329942 | OTA-WKM-C-0458-0459-Earthwire-C0 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 | CA copied from EW A0 Feb/2026
13329942 | OTA-WKM-C-0458-0459-Earthwire-C0 | OTA-WKM-C0458-0459 | OTA-WKM-C0458-0459-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 | CA copied from EW A0 Feb/2026
10046557 | OTA-WKM-C-0459-Tower | OTA-WKM-C0459 | OTA-WKM-C0459-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046557 | OTA-WKM-C-0459-Tower | OTA-WKM-C0459 | OTA-WKM-C0459-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046557 | OTA-WKM-C-0459-Tower | OTA-WKM-C0459 | OTA-WKM-C0459-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046557 | OTA-WKM-C-0459-Tower | OTA-WKM-C0459 | OTA-WKM-C0459-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046557 | OTA-WKM-C-0459-Tower | OTA-WKM-C0459 | OTA-WKM-C0459-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046557 | OTA-WKM-C-0459-Tower | OTA-WKM-C0459 | OTA-WKM-C0459-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2024-10-21 10:22
10046557 | OTA-WKM-C-0459-Tower | OTA-WKM-C0459 | OTA-WKM-C0459-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
10046558 | OTA-WKM-C-0459-Tower Foundation | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:03
12058870 | OTA-WKM-C-0459-Earthwire HW Set | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 12:01
12058870 | OTA-WKM-C-0459-Earthwire HW Set | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-08 12:01
13040192 | OTA-WKM-C-0459-Earthwire Attachment | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-19 12:02 | New attachment point
13040192 | OTA-WKM-C-0459-Earthwire Attachment | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-19 12:01 | Replaced the attachment point nuts and bolts
13040192 | OTA-WKM-C-0459-Earthwire Attachment | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-19 12:01 | Replaced the attachment point steel
13040192 | OTA-WKM-C-0459-Earthwire Attachment | OTA-WKM-C0459 | OTA-WKM-C0459-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2023-05-19 12:03 | Minor rust
13285499 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 TL Insulators 24-25
13285499 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 TL Insulators 24-25
13285499 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 TL Insulators 24-25
13285499 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 TL Insulators 24-25
13285500 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285500 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285500 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13285500 | OTA-WKM-C-0459-Insulator Set-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 | Replaced during RSA2 24-25 Reins Project
13286414 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 Attach Point Replacement 24-25
13286414 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 Attach Point Replacement 24-25
13286414 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 Attach Point Replacement 24-25
13286414 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0459 | OTA-WKM-C0459-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-17 | RSA2 Attach Point Replacement 24-25
13286415 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 15:32
13286415 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 15:32
13286415 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 15:32
13286415 | OTA-WKM-C-0459-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0459 | OTA-WKM-C0459-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 15:32
10047181 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-2 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 11:54
10047181 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-2 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 11:54
10047181 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-2 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | <Not Specified>
10047181 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-2 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 11:54
10047182 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-1 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-08 11:54
10047182 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-1 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 11:54
10047182 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-1 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | <Not Specified>
10047182 | OTA-WKM-C-0459-0460-Conductor-OHW-OTA-1 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 11:54
10047183 | OTA-WKM-C-0459-0460-Earthwire-A0 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:11
10047183 | OTA-WKM-C-0459-0460-Earthwire-A0 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 13:11
10047183 | OTA-WKM-C-0459-0460-Earthwire-A0 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-01-08 01:00 | CA
13329943 | OTA-WKM-C-0459-0460-Earthwire-C0 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 | CA copied from EW A0 Feb/2026
13329943 | OTA-WKM-C-0459-0460-Earthwire-C0 | OTA-WKM-C0459-0460 | OTA-WKM-C0459-0460-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-08 | CA copied from EW A0 Feb/2026
10046562 | OTA-WKM-C-0460-Tower | OTA-WKM-C0460 | OTA-WKM-C0460-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-04 | Fitted climbing deterrent to tower 6.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046562 | OTA-WKM-C-0460-Tower | OTA-WKM-C0460 | OTA-WKM-C0460-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-04 | Fitted climbing deterrent to tower 6.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046562 | OTA-WKM-C-0460-Tower | OTA-WKM-C0460 | OTA-WKM-C0460-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-04 | Fitted climbing deterrent to tower 6.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046562 | OTA-WKM-C-0460-Tower | OTA-WKM-C0460 | OTA-WKM-C0460-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-04 | Fitted climbing deterrent to tower 6.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046562 | OTA-WKM-C-0460-Tower | OTA-WKM-C0460 | OTA-WKM-C0460-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-04 | Fitted climbing deterrent to tower 6.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046562 | OTA-WKM-C-0460-Tower | OTA-WKM-C0460 | OTA-WKM-C0460-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-25 11:11
10046562 | OTA-WKM-C-0460-Tower | OTA-WKM-C0460 | OTA-WKM-C0460-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-04 | Fitted climbing deterrent to tower 6.5m above ground level. Tower not reassessed, ratings remain unchanged.
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Dug leg A
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Rust staining
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Dug leg A
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Rust staining
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Dug leg A
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Rust staining
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Dug leg A
10046563 | OTA-WKM-C-0460-Tower Foundation | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:18 | Rust staining
12058871 | OTA-WKM-C-0460-Earthwire HW Set | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:43 | Fretting on strands
12058871 | OTA-WKM-C-0460-Earthwire HW Set | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:43
13040193 | OTA-WKM-C-0460-Earthwire Attachment | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-05 19:36 | New attachment point installed
13040193 | OTA-WKM-C-0460-Earthwire Attachment | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-05 19:36 | Fitted New nuts and bolts
13040193 | OTA-WKM-C-0460-Earthwire Attachment | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-05 19:36 | New attachment point installed
13040193 | OTA-WKM-C-0460-Earthwire Attachment | OTA-WKM-C0460 | OTA-WKM-C0460-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-05 19:37 | Fitted with new nuts and bolts
13073847 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13073847 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13073847 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13073847 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13073848 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13073848 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13073848 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13073848 | OTA-WKM-C-0460-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 14:25
13285501 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285501 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285501 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285501 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-1 | OTA-WKM-C0460 | OTA-WKM-C0460-10 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 | Replaced during RSA2 24-25 Reins Project
13285502 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:30
13285502 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:29
13285502 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:29
13285502 | OTA-WKM-C-0460-Insulator Set-OHW-OTA-2 | OTA-WKM-C0460 | OTA-WKM-C0460-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:29
10047184 | OTA-WKM-C-0460-0461-Conductor-OHW-OTA-2 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-27 13:32
10047184 | OTA-WKM-C-0460-0461-Conductor-OHW-OTA-2 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 13:32
10047184 | OTA-WKM-C-0460-0461-Conductor-OHW-OTA-2 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 13:32 | Significant corrosion on bolts nut and ring
10047185 | OTA-WKM-C-0460-0461-Conductor-OHW-OTA-1 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-27 13:32
10047185 | OTA-WKM-C-0460-0461-Conductor-OHW-OTA-1 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 13:32
10047185 | OTA-WKM-C-0460-0461-Conductor-OHW-OTA-1 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 13:32 | Significant corrosion on bolts nut and ring
10047186 | OTA-WKM-C-0460-0461-Earthwire-A0 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:31
10047186 | OTA-WKM-C-0460-0461-Earthwire-A0 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 15:31 | Surface pitting
13329944 | OTA-WKM-C-0460-0461-Earthwire-C0 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 | CA copied from EW A0 Feb/2026
13329944 | OTA-WKM-C-0460-0461-Earthwire-C0 | OTA-WKM-C0460-0461 | OTA-WKM-C0460-0461-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 | Surface pitting. CA copied from EW A0 Feb/2026
10046567 | OTA-WKM-C-0461-Tower | OTA-WKM-C0461 | OTA-WKM-C0461-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046567 | OTA-WKM-C-0461-Tower | OTA-WKM-C0461 | OTA-WKM-C0461-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046567 | OTA-WKM-C-0461-Tower | OTA-WKM-C0461 | OTA-WKM-C0461-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046567 | OTA-WKM-C-0461-Tower | OTA-WKM-C0461 | OTA-WKM-C0461-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046567 | OTA-WKM-C-0461-Tower | OTA-WKM-C0461 | OTA-WKM-C0461-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046567 | OTA-WKM-C-0461-Tower | OTA-WKM-C0461 | OTA-WKM-C0461-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-26 13:30
10046567 | OTA-WKM-C-0461-Tower | OTA-WKM-C0461 | OTA-WKM-C0461-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10046568 | OTA-WKM-C-0461-Tower Foundation | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-27 10:01
10332828 | OTA-WKM-C-0461-Earthwire HW Set | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:27 | Corrosion
10332828 | OTA-WKM-C-0461-Earthwire HW Set | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-27 10:27
13040194 | OTA-WKM-C-0461-Earthwire Attachment | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:28
13040194 | OTA-WKM-C-0461-Earthwire Attachment | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:28
13040194 | OTA-WKM-C-0461-Earthwire Attachment | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:28
13040194 | OTA-WKM-C-0461-Earthwire Attachment | OTA-WKM-C0461 | OTA-WKM-C0461-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:28
13073849 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:30
13073849 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:30
13073849 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:30
13073849 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:30
13073850 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:31
13073850 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:31
13073850 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:31
13073850 | OTA-WKM-C-0461-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:31
13285503 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 | Replaced during RSA2 24-25 Reins Project
13285503 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 | Replaced during RSA2 24-25 Reins Project
13285503 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 | Replaced during RSA2 24-25 Reins Project
13285503 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-1 | OTA-WKM-C0461 | OTA-WKM-C0461-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-10 | Replaced during RSA2 24-25 Reins Project
13285504 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 11:51
13285504 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 11:50
13285504 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 11:51
13285504 | OTA-WKM-C-0461-Insulator Set-OHW-OTA-2 | OTA-WKM-C0461 | OTA-WKM-C0461-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-26 11:51
10047187 | OTA-WKM-C-0461-0462-Conductor-OHW-OTA-2 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-27 10:36
10047187 | OTA-WKM-C-0461-0462-Conductor-OHW-OTA-2 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:36
10047187 | OTA-WKM-C-0461-0462-Conductor-OHW-OTA-2 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:36 | Corrosion
10047188 | OTA-WKM-C-0461-0462-Conductor-OHW-OTA-1 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-27 10:36
10047188 | OTA-WKM-C-0461-0462-Conductor-OHW-OTA-1 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:36
10047188 | OTA-WKM-C-0461-0462-Conductor-OHW-OTA-1 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:36 | Corrosion
10047189 | OTA-WKM-C-0461-0462-Earthwire-A0 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:59
10047189 | OTA-WKM-C-0461-0462-Earthwire-A0 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 10:59
13329945 | OTA-WKM-C-0461-0462-Earthwire-C0 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 | CA copied from EW A0 Feb/2026
13329945 | OTA-WKM-C-0461-0462-Earthwire-C0 | OTA-WKM-C0461-0462 | OTA-WKM-C0461-0462-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-27 | CA copied from EW A0 Feb/2026
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-07-25 | CA
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-07-25 | CA
10046572 | OTA-WKM-C-0462-Tower | OTA-WKM-C0462 | OTA-WKM-C0462-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - E/W attachment plates R/C.
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10046573 | OTA-WKM-C-0462-Tower Foundation | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10332829 | OTA-WKM-C-0462-Earthwire HW Set | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:37 | Surface pitting
10332829 | OTA-WKM-C-0462-Earthwire HW Set | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-20 14:37
13040195 | OTA-WKM-C-0462-Earthwire Attachment | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-20 14:36
13040195 | OTA-WKM-C-0462-Earthwire Attachment | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-20 14:36
13040195 | OTA-WKM-C-0462-Earthwire Attachment | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-20 14:36
13040195 | OTA-WKM-C-0462-Earthwire Attachment | OTA-WKM-C0462 | OTA-WKM-C0462-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-20 14:36
13170131 | OTA-WKM-C-0462-Insulator Set-OHW-OTA-1 | OTA-WKM-C0462 | OTA-WKM-C0462-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-20 13:48
13170131 | OTA-WKM-C-0462-Insulator Set-OHW-OTA-1 | OTA-WKM-C0462 | OTA-WKM-C0462-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-20 13:48
13170131 | OTA-WKM-C-0462-Insulator Set-OHW-OTA-1 | OTA-WKM-C0462 | OTA-WKM-C0462-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-20 13:48
13170132 | OTA-WKM-C-0462-Insulator Set-OHW-OTA-2 | OTA-WKM-C0462 | OTA-WKM-C0462-20 | 2018 | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-20 13:48
13170132 | OTA-WKM-C-0462-Insulator Set-OHW-OTA-2 | OTA-WKM-C0462 | OTA-WKM-C0462-20 | 2018 | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-20 13:48
13170132 | OTA-WKM-C-0462-Insulator Set-OHW-OTA-2 | OTA-WKM-C0462 | OTA-WKM-C0462-20 | 2018 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-20 13:48
13216928 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0462 | OTA-WKM-C0462-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:49
13216928 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0462 | OTA-WKM-C0462-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:49
13216928 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0462 | OTA-WKM-C0462-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:49
13216928 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0462 | OTA-WKM-C0462-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:49
13216929 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0462 | OTA-WKM-C0462-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:50
13216929 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0462 | OTA-WKM-C0462-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:50
13216929 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0462 | OTA-WKM-C0462-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:50
13216929 | OTA-WKM-C-0462-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0462 | OTA-WKM-C0462-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-20 13:50
10047190 | OTA-WKM-C-0462-0463-Conductor-OHW-OTA-2 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-20 14:08
10047190 | OTA-WKM-C-0462-0463-Conductor-OHW-OTA-2 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:08
10047190 | OTA-WKM-C-0462-0463-Conductor-OHW-OTA-2 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - Subconctor spacers rusty.
10047191 | OTA-WKM-C-0462-0463-Conductor-OHW-OTA-1 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10047191 | OTA-WKM-C-0462-0463-Conductor-OHW-OTA-1 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:07
10047191 | OTA-WKM-C-0462-0463-Conductor-OHW-OTA-1 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-04 | CA - Subconctor spacers rusty.
10047192 | OTA-WKM-C-0462-0463-Earthwire-A0 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-00 |  | EASE_DAMPER COND | Damper Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:45 | Surface pitting
10047192 | OTA-WKM-C-0462-0463-Earthwire-A0 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 14:45
13329946 | OTA-WKM-C-0462-0463-Earthwire-C0 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-00 |  | EASE_DAMPER COND | Damper Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 | Surface pitting. CA copied from EW A0 Feb/2026
13329946 | OTA-WKM-C-0462-0463-Earthwire-C0 | OTA-WKM-C0462-0463 | OTA-WKM-C0462-0463-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 | CA copied from EW A0 Feb/2026
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-27 09:03
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-07-28 | CA
10046577 | OTA-WKM-C-0463-Tower | OTA-WKM-C0463 | OTA-WKM-C0463-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
10046578 | OTA-WKM-C-0463-Tower Foundation | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-07 11:27
12058872 | OTA-WKM-C-0463-Earthwire HW Set | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 15:18
12058872 | OTA-WKM-C-0463-Earthwire HW Set | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 15:18
13073853 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:45
13073853 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:45
13073853 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:45
13073853 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:45
13073854 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:46
13073854 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:46
13073854 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:46
13073854 | OTA-WKM-C-0463-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:46
13285505 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 08:30
13285505 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 08:30
13285505 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 08:30
13285505 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-1 | OTA-WKM-C0463 | OTA-WKM-C0463-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-09 08:30
13285506 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 12:56
13285506 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 12:55
13285506 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 12:55
13285506 | OTA-WKM-C-0463-Insulator Set-OHW-OTA-2 | OTA-WKM-C0463 | OTA-WKM-C0463-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-27 12:55
13300411 | OTA-WKM-C-0463-Earthwire Attachment | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 15:18
13300411 | OTA-WKM-C-0463-Earthwire Attachment | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 15:18
13300411 | OTA-WKM-C-0463-Earthwire Attachment | OTA-WKM-C0463 | OTA-WKM-C0463-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-08-13 15:18
10047193 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-2 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-07 11:47
10047193 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-2 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:47
10047193 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-2 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10047193 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-2 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:47 | Corrosion
10047194 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-1 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-07 11:46
10047194 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-1 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:46
10047194 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-1 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10047194 | OTA-WKM-C-0463-0464-Conductor-OHW-OTA-1 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 11:46 | Corrosion
10047195 | OTA-WKM-C-0463-0464-Earthwire-A0 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-00 |  | EASE_DAMPER COND | Damper Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-07 12:46
10047195 | OTA-WKM-C-0463-0464-Earthwire-A0 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 12:46
10047195 | OTA-WKM-C-0463-0464-Earthwire-A0 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-28 | CA
13329947 | OTA-WKM-C-0463-0464-Earthwire-C0 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-00 |  | EASE_DAMPER COND | Damper Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-07 | CA copied from EW A0 Feb/2026
13329947 | OTA-WKM-C-0463-0464-Earthwire-C0 | OTA-WKM-C0463-0464 | OTA-WKM-C0463-0464-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-07 | CA copied from EW A0 Feb/2026
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-27 12:52
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-07-28 | CA
10046582 | OTA-WKM-C-0464-Tower | OTA-WKM-C0464 | OTA-WKM-C0464-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
10046583 | OTA-WKM-C-0464-Tower Foundation | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:05
12058873 | OTA-WKM-C-0464-Earthwire HW Set | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-28 14:25
12058873 | OTA-WKM-C-0464-Earthwire HW Set | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-28 14:25
13073855 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13073855 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13073855 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13073855 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13073856 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13073856 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13073856 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13073856 | OTA-WKM-C-0464-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:15
13285507 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285507 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285507 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285507 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-1 | OTA-WKM-C0464 | OTA-WKM-C0464-10 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Reins Project
13285508 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 14:10
13285508 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 14:10
13285508 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 14:10
13285508 | OTA-WKM-C-0464-Insulator Set-OHW-OTA-2 | OTA-WKM-C0464 | OTA-WKM-C0464-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 14:10
13286473 | OTA-WKM-C-0464-Earthwire Attachment | OTA-WKM-C0464 | OTA-WKM-C0464-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-11 | Replaced during RSA2 24-25 Att Pt Project
10047196 | OTA-WKM-C-0464-0465-Conductor-OHW-OTA-2 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-28 14:16
10047196 | OTA-WKM-C-0464-0465-Conductor-OHW-OTA-2 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:16
10047196 | OTA-WKM-C-0464-0465-Conductor-OHW-OTA-2 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:16 | Corrosion
10047197 | OTA-WKM-C-0464-0465-Conductor-OHW-OTA-1 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-28 14:16
10047197 | OTA-WKM-C-0464-0465-Conductor-OHW-OTA-1 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:16
10047197 | OTA-WKM-C-0464-0465-Conductor-OHW-OTA-1 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 14:16 | Corrosion
10047198 | OTA-WKM-C-0464-0465-Earthwire-A0 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 15:07
10047198 | OTA-WKM-C-0464-0465-Earthwire-A0 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 15:07
13329948 | OTA-WKM-C-0464-0465-Earthwire-C0 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 | CA copied from EW A0 Feb/2026
13329948 | OTA-WKM-C-0464-0465-Earthwire-C0 | OTA-WKM-C0464-0465 | OTA-WKM-C0464-0465-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 | CA copied from EW A0 Feb/2026
10046587 | OTA-WKM-C-0465-Tower | OTA-WKM-C0465 | OTA-WKM-C0465-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046587 | OTA-WKM-C-0465-Tower | OTA-WKM-C0465 | OTA-WKM-C0465-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046587 | OTA-WKM-C-0465-Tower | OTA-WKM-C0465 | OTA-WKM-C0465-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046587 | OTA-WKM-C-0465-Tower | OTA-WKM-C0465 | OTA-WKM-C0465-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046587 | OTA-WKM-C-0465-Tower | OTA-WKM-C0465 | OTA-WKM-C0465-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046587 | OTA-WKM-C-0465-Tower | OTA-WKM-C0465 | OTA-WKM-C0465-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-07-29 | CA
10046587 | OTA-WKM-C-0465-Tower | OTA-WKM-C0465 | OTA-WKM-C0465-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35 | Dug leg c
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35
10046588 | OTA-WKM-C-0465-Tower Foundation | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:35
12058874 | OTA-WKM-C-0465-Earthwire HW Set | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:12 | Surface rust on strands
12058874 | OTA-WKM-C-0465-Earthwire HW Set | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:12
13040198 | OTA-WKM-C-0465-Earthwire Attachment | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:18 | replace ew attachment point type C and its hardware
13040198 | OTA-WKM-C-0465-Earthwire Attachment | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:11
13040198 | OTA-WKM-C-0465-Earthwire Attachment | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-18 08:00 | Updating to 4 Readings
13040198 | OTA-WKM-C-0465-Earthwire Attachment | OTA-WKM-C0465 | OTA-WKM-C0465-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:19 | replace bolts and its hardware
13218562 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13218562 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13218562 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13218562 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13243880 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13243880 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13243880 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13243880 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0465 | OTA-WKM-C0465-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:25
13245175 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:26
13245175 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:26
13245175 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:26
13245175 | OTA-WKM-C-0465-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:26
13247438 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:24
13247438 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:24
13247438 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:24
13247438 | OTA-WKM-C-0465-Insulator Set-OHW-OTA-2 | OTA-WKM-C0465 | OTA-WKM-C0465-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-28 11:24
10047199 | OTA-WKM-C-0465-0466-Conductor-OHW-OTA-2 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-28 11:37
10047199 | OTA-WKM-C-0465-0466-Conductor-OHW-OTA-2 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 11:37
10047199 | OTA-WKM-C-0465-0466-Conductor-OHW-OTA-2 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 11:37 | Significant corrosion on bolts nut
10047200 | OTA-WKM-C-0465-0466-Conductor-OHW-OTA-1 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-28 11:27
10047200 | OTA-WKM-C-0465-0466-Conductor-OHW-OTA-1 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 11:27
10047200 | OTA-WKM-C-0465-0466-Conductor-OHW-OTA-1 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 11:27 | Significant corrosion on bolts nut
10047201 | OTA-WKM-C-0465-0466-Earthwire-A0 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:14
10047201 | OTA-WKM-C-0465-0466-Earthwire-A0 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 12:14 | Metal loss on strands
13329949 | OTA-WKM-C-0465-0466-Earthwire-C0 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 | CA copied from EW A0 Feb/2026
13329949 | OTA-WKM-C-0465-0466-Earthwire-C0 | OTA-WKM-C0465-0466 | OTA-WKM-C0465-0466-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 | Metal loss on strands. CA copied from EW A0 Feb/2026
10046592 | OTA-WKM-C-0466-Tower | OTA-WKM-C0466 | OTA-WKM-C0466-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046592 | OTA-WKM-C-0466-Tower | OTA-WKM-C0466 | OTA-WKM-C0466-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046592 | OTA-WKM-C-0466-Tower | OTA-WKM-C0466 | OTA-WKM-C0466-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046592 | OTA-WKM-C-0466-Tower | OTA-WKM-C0466 | OTA-WKM-C0466-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046592 | OTA-WKM-C-0466-Tower | OTA-WKM-C0466 | OTA-WKM-C0466-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046592 | OTA-WKM-C-0466-Tower | OTA-WKM-C0466 | OTA-WKM-C0466-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2025-03-24 18:02
10046592 | OTA-WKM-C-0466-Tower | OTA-WKM-C0466 | OTA-WKM-C0466-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046593 | OTA-WKM-C-0466-Tower Foundation | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:36
10046596 | OTA-WKM-C-0466-Earthwire HW Set | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:24
10046596 | OTA-WKM-C-0466-Earthwire HW Set | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:24
13040199 | OTA-WKM-C-0466-Earthwire Attachment | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 | Reeplaced EW attachment
13040199 | OTA-WKM-C-0466-Earthwire Attachment | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:30 | Nuts and bolts also replace
13040199 | OTA-WKM-C-0466-Earthwire Attachment | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-13 19:29 | replace EW attachment point both side
13040199 | OTA-WKM-C-0466-Earthwire Attachment | OTA-WKM-C0466 | OTA-WKM-C0466-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 10:34
13073859 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 21 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-05-09 14:39 | Hanger bracket showing signs of corrosion
13073859 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-05-09 14:43 | Bolt head showing signs of corrosion
13073859 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 21 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-05-09 14:37 | ZCP layer has significant erosion and starting to corrode
13073859 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-05-09 14:32 | Through bolt head has heavy corrosion on all phases
13073860 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:43
13073860 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:43
13073860 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:43
13073860 | OTA-WKM-C-0466-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:43
13285509 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285509 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285509 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285509 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-1 | OTA-WKM-C0466 | OTA-WKM-C0466-10 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-07 | Replaced during RSA2 24-25 Reins Project
13285510 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 18:04
13285510 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 18:04
13285510 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 18:04
13285510 | OTA-WKM-C-0466-Insulator Set-OHW-OTA-2 | OTA-WKM-C0466 | OTA-WKM-C0466-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-24 18:04
10047202 | OTA-WKM-C-0466-0467-Conductor-OHW-OTA-2 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-28 09:50
10047202 | OTA-WKM-C-0466-0467-Conductor-OHW-OTA-2 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:50
10047202 | OTA-WKM-C-0466-0467-Conductor-OHW-OTA-2 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10047203 | OTA-WKM-C-0466-0467-Conductor-OHW-OTA-1 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-28 | CA
10047203 | OTA-WKM-C-0466-0467-Conductor-OHW-OTA-1 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 09:49
10047203 | OTA-WKM-C-0466-0467-Conductor-OHW-OTA-1 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2007-07-17 | Routine CA
10047204 | OTA-WKM-C-0466-0467-Earthwire-A0 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 10:37
10047204 | OTA-WKM-C-0466-0467-Earthwire-A0 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 10:37
10047204 | OTA-WKM-C-0466-0467-Earthwire-A0 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-28 | CA
13329950 | OTA-WKM-C-0466-0467-Earthwire-C0 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 | CA copied from EW A0 Feb/2026
13329950 | OTA-WKM-C-0466-0467-Earthwire-C0 | OTA-WKM-C0466-0467 | OTA-WKM-C0466-0467-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-28 | CA copied from EW A0 Feb/2026
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-14
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-07-25 | CA
10046597 | OTA-WKM-C-0467-Tower | OTA-WKM-C0467 | OTA-WKM-C0467-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachments rusty. Insulator attachments on OHW_OTA_2 rusty.
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
10046598 | OTA-WKM-C-0467-Tower Foundation | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:34
12058875 | OTA-WKM-C-0467-Earthwire HW Set | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:45
12058875 | OTA-WKM-C-0467-Earthwire HW Set | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-11-15 13:45
13040200 | OTA-WKM-C-0467-Earthwire Attachment | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:42
13040200 | OTA-WKM-C-0467-Earthwire Attachment | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-15 13:42
13040200 | OTA-WKM-C-0467-Earthwire Attachment | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:42
13040200 | OTA-WKM-C-0467-Earthwire Attachment | OTA-WKM-C0467 | OTA-WKM-C0467-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2019-08-15 08:00 | Updating to 4 Readings
13073861 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13073861 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13073861 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13073861 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13073862 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13073862 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13073862 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13073862 | OTA-WKM-C-0467-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:44
13285511 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-20 07:27
13285511 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-20 07:27
13285511 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-20 07:27
13285511 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-1 | OTA-WKM-C0467 | OTA-WKM-C0467-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-20 07:27
13285512 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-22 11:30
13285512 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-22 11:30
13285512 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-22 11:30
13285512 | OTA-WKM-C-0467-Insulator Set-OHW-OTA-2 | OTA-WKM-C0467 | OTA-WKM-C0467-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-09-22 11:30
10047205 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-2 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-15 13:46
10047205 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-2 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:46
10047205 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-2 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10047205 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-2 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:46
10047206 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-1 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-11-15 13:46
10047206 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-1 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:46
10047206 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-1 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10047206 | OTA-WKM-C-0467-0468-Conductor-OHW-OTA-1 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:46
10047207 | OTA-WKM-C-0467-0468-Earthwire-A0 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:49
10047207 | OTA-WKM-C-0467-0468-Earthwire-A0 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 13:49
13329951 | OTA-WKM-C-0467-0468-Earthwire-C0 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 | CA copied from EW A0 Feb/2026
13329951 | OTA-WKM-C-0467-0468-Earthwire-C0 | OTA-WKM-C0467-0468 | OTA-WKM-C0467-0468-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-11-15 | CA copied from EW A0 Feb/2026
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-10-20 01:00 | CA
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046602 | OTA-WKM-C-0468-Tower | OTA-WKM-C0468 | OTA-WKM-C0468-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA - E/W attachment plates R/C.
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046603 | OTA-WKM-C-0468-Tower Foundation | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:42
10046604 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-21 10:51
10046604 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:51
10046604 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:51 | Corrosion
10046604 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:51 | Rust flaking
10046605 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-21 10:53 | Replaced
10046605 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:53
10046605 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-21 10:53 | Replaced
10046605 | OTA-WKM-C-0468-Insulator Set-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:53
10332830 | OTA-WKM-C-0468-Earthwire HW Set | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:56 | Corrosion
10332830 | OTA-WKM-C-0468-Earthwire HW Set | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-21 10:56
13040201 | OTA-WKM-C-0468-Earthwire Attachment | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13040201 | OTA-WKM-C-0468-Earthwire Attachment | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-21 10:55
13040201 | OTA-WKM-C-0468-Earthwire Attachment | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13040201 | OTA-WKM-C-0468-Earthwire Attachment | OTA-WKM-C0468 | OTA-WKM-C0468-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073863 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073863 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073863 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073863 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0468 | OTA-WKM-C0468-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073864 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073864 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073864 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
13073864 | OTA-WKM-C-0468-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0468 | OTA-WKM-C0468-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:55
10047208 | OTA-WKM-C-0468-0469-Conductor-OHW-OTA-2 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-21 10:47
10047208 | OTA-WKM-C-0468-0469-Conductor-OHW-OTA-2 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:47
10047208 | OTA-WKM-C-0468-0469-Conductor-OHW-OTA-2 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:47 | Nuts and bolts rusty
10047209 | OTA-WKM-C-0468-0469-Conductor-OHW-OTA-1 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-21 10:46
10047209 | OTA-WKM-C-0468-0469-Conductor-OHW-OTA-1 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:46
10047209 | OTA-WKM-C-0468-0469-Conductor-OHW-OTA-1 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:46 | Nuts and bolts rusty
10047210 | OTA-WKM-C-0468-0469-Earthwire-A0 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:58
10047210 | OTA-WKM-C-0468-0469-Earthwire-A0 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 10:58
13329952 | OTA-WKM-C-0468-0469-Earthwire-C0 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 | CA copied from EW A0 Feb/2026
13329952 | OTA-WKM-C-0468-0469-Earthwire-C0 | OTA-WKM-C0468-0469 | OTA-WKM-C0468-0469-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-21 | CA copied from EW A0 Feb/2026
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-28 13:54
10046607 | OTA-WKM-C-0469-Tower | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2009-09-18 | Fitted climbing deterrent to tower 5m above ground. Tower not reassessed, ratings remain unchanged.
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
10046608 | OTA-WKM-C-0469-Tower Foundation | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:00
12058876 | OTA-WKM-C-0469-Earthwire HW Set | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:50 | Corrosion
12058876 | OTA-WKM-C-0469-Earthwire HW Set | OTA-WKM-C0469 | OTA-WKM-C0469-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-20 10:50
13073865 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:22
13073865 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:22
13073865 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:22 | Corrosion
13073865 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:22
13073866 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:21
13073866 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:21
13073866 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-08-20 | Updating to 4 Readings
13073866 | OTA-WKM-C-0469-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:21
13285513 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285513 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285513 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285513 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-1 | OTA-WKM-C0469 | OTA-WKM-C0469-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Reins Project
13285514 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 13:57
13285514 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 13:57
13285514 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 13:57
13285514 | OTA-WKM-C-0469-Insulator Set-OHW-OTA-2 | OTA-WKM-C0469 | OTA-WKM-C0469-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-28 13:57
13286475 | OTA-WKM-C-0469-Earthwire Attachment | OTA-WKM-C0469 | OTA-WKM-C0469-00 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-01 | Replaced during RSA2 24-25 Att Pt Project
10047211 | OTA-WKM-C-0469-0470-Conductor-OHW-OTA-2 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-20 10:20
10047211 | OTA-WKM-C-0469-0470-Conductor-OHW-OTA-2 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:20
10047211 | OTA-WKM-C-0469-0470-Conductor-OHW-OTA-2 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:20 | Corrosion
10047212 | OTA-WKM-C-0469-0470-Conductor-OHW-OTA-1 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-20 10:19
10047212 | OTA-WKM-C-0469-0470-Conductor-OHW-OTA-1 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:19
10047212 | OTA-WKM-C-0469-0470-Conductor-OHW-OTA-1 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:19 | Corrosion
10047213 | OTA-WKM-C-0469-0470-Earthwire-A0 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-00 |  | EASE_DAMPER COND | Damper Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:51
10047213 | OTA-WKM-C-0469-0470-Earthwire-A0 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 10:51
13329953 | OTA-WKM-C-0469-0470-Earthwire-C0 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-00 |  | EASE_DAMPER COND | Damper Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 | CA copied from EW A0 Feb/2026
13329953 | OTA-WKM-C-0469-0470-Earthwire-C0 | OTA-WKM-C0469-0470 | OTA-WKM-C0469-0470-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-20 | CA copied from EW A0 Feb/2026
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2025-06-05 07:38
10046612 | OTA-WKM-C-0470-Tower | OTA-WKM-C0470 | OTA-WKM-C0470-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-05 | CA
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046613 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:24 | Rust flaking
10046616 | OTA-WKM-C-0470-Earthwire HW Set | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:45 | Heavy corrosion
10046616 | OTA-WKM-C-0470-Earthwire HW Set | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:45
13040203 | OTA-WKM-C-0470-Earthwire Attachment | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-19 15:44
13040203 | OTA-WKM-C-0470-Earthwire Attachment | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-19 15:44
13040203 | OTA-WKM-C-0470-Earthwire Attachment | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-19 15:44
13040203 | OTA-WKM-C-0470-Earthwire Attachment | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-19 15:44
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285034 | OTA-WKM-C-0470-Tower Foundation | OTA-WKM-C0470 | OTA-WKM-C0470-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-08 | RSA2 24-25 Grillage Refurbishment
13285515 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285515 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285515 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285515 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Reins Project
13285516 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Reins Project
13285516 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Reins Project
13285516 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Reins Project
13285516 | OTA-WKM-C-0470-Insulator Set-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Reins Project
13286416 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2024 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286416 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2024 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286416 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2024 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286416 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0470 | OTA-WKM-C0470-10 | 2024 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-12 | Replaced during RSA2 24-25 Att Pt Project
13286417 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Att Pt Project
13286417 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Att Pt Project
13286417 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Att Pt Project
13286417 | OTA-WKM-C-0470-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0470 | OTA-WKM-C0470-20 | 2024 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-04 | Replaced during RSA2 24-25 Att Pt Project
10047214 | OTA-WKM-C-0470-0471-Conductor-OHW-OTA-2 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-19 15:25
10047214 | OTA-WKM-C-0470-0471-Conductor-OHW-OTA-2 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:25
10047214 | OTA-WKM-C-0470-0471-Conductor-OHW-OTA-2 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:25 | Nuts and bolts rusty
10047215 | OTA-WKM-C-0470-0471-Conductor-OHW-OTA-1 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-19 15:25
10047215 | OTA-WKM-C-0470-0471-Conductor-OHW-OTA-1 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:25
10047215 | OTA-WKM-C-0470-0471-Conductor-OHW-OTA-1 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 15:25 | Nuts and bolts rusty
10047216 | OTA-WKM-C-0470-0471-Earthwire-A0 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 16:17
10047216 | OTA-WKM-C-0470-0471-Earthwire-A0 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 16:17
13329954 | OTA-WKM-C-0470-0471-Earthwire-C0 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 | CA copied from EW A0 Feb/2026
13329954 | OTA-WKM-C-0470-0471-Earthwire-C0 | OTA-WKM-C0470-0471 | OTA-WKM-C0470-0471-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-19 | CA copied from EW A0 Feb/2026
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-19
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-08-19 | Attachment point plates rusty on Y and R phase cct 1 and Y phase cct2. paint on Ins attachment point plates is RC
10046617 | OTA-WKM-C-0471-Tower | OTA-WKM-C0471 | OTA-WKM-C0471-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
10046618 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:39
12058877 | OTA-WKM-C-0471-Earthwire HW Set | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 11:36 | Heavy corrosion
12058877 | OTA-WKM-C-0471-Earthwire HW Set | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:36
13040204 | OTA-WKM-C-0471-Earthwire Attachment | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 11:38
13040204 | OTA-WKM-C-0471-Earthwire Attachment | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 11:38
13040204 | OTA-WKM-C-0471-Earthwire Attachment | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 11:38
13040204 | OTA-WKM-C-0471-Earthwire Attachment | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 11:38
13253197 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 TL Insulators 22-23
13253197 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 TL Insulators 22-23
13253197 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 TL Insulators 22-23
13253197 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 TL Insulators 22-23
13262429 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 Attachment Point Replacement 23-24
13262429 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 Attachment Point Replacement 23-24
13262429 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 Attachment Point Replacement 23-24
13262429 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0471 | OTA-WKM-C0471-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-12-08 | RSA2 Attachment Point Replacement 23-24
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285035 | OTA-WKM-C-0471-Tower Foundation | OTA-WKM-C0471 | OTA-WKM-C0471-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-19 | RSA2 24-25 Grillage Refurbishment
13285517 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13285517 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13285517 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13285517 | OTA-WKM-C-0471-Insulator Set-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Reins Project
13286418 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
13286418 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
13286418 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
13286418 | OTA-WKM-C-0471-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0471 | OTA-WKM-C0471-20 | 2025 | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-06-17 | Replaced during RSA2 24-25 Att Pt Project
10047217 | OTA-WKM-C-0471-0472-Conductor-OHW-OTA-2 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-18 12:09
10047217 | OTA-WKM-C-0471-0472-Conductor-OHW-OTA-2 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 12:09
10047217 | OTA-WKM-C-0471-0472-Conductor-OHW-OTA-2 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 12:09 | Corrosion on Nuts and bolts
10047218 | OTA-WKM-C-0471-0472-Conductor-OHW-OTA-1 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-18 12:08
10047218 | OTA-WKM-C-0471-0472-Conductor-OHW-OTA-1 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 12:08
10047218 | OTA-WKM-C-0471-0472-Conductor-OHW-OTA-1 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-20 | Routine CA
10047218 | OTA-WKM-C-0471-0472-Conductor-OHW-OTA-1 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 12:08 | Corrosion on Nuts and bolts
10047219 | OTA-WKM-C-0471-0472-Earthwire-A0 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 12:07
10047219 | OTA-WKM-C-0471-0472-Earthwire-A0 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 12:07
10047219 | OTA-WKM-C-0471-0472-Earthwire-A0 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-19 | CA
13329955 | OTA-WKM-C-0471-0472-Earthwire-C0 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 | CA copied from EW A0 Feb/2026
13329955 | OTA-WKM-C-0471-0472-Earthwire-C0 | OTA-WKM-C0471-0472 | OTA-WKM-C0471-0472-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 | CA copied from EW A0 Feb/2026
10046622 | OTA-WKM-C-0472-Tower | OTA-WKM-C0472 | OTA-WKM-C0472-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA
10046622 | OTA-WKM-C-0472-Tower | OTA-WKM-C0472 | OTA-WKM-C0472-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA
10046622 | OTA-WKM-C-0472-Tower | OTA-WKM-C0472 | OTA-WKM-C0472-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA
10046622 | OTA-WKM-C-0472-Tower | OTA-WKM-C0472 | OTA-WKM-C0472-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA
10046622 | OTA-WKM-C-0472-Tower | OTA-WKM-C0472 | OTA-WKM-C0472-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA
10046622 | OTA-WKM-C-0472-Tower | OTA-WKM-C0472 | OTA-WKM-C0472-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-10-20 01:00 | CA
10046622 | OTA-WKM-C-0472-Tower | OTA-WKM-C0472 | OTA-WKM-C0472-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54 | Dug leg A
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54
10046623 | OTA-WKM-C-0472-Tower Foundation | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 13:54
10046624 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:18
10046624 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 13:55
10046624 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 13:57 | Significant corrosion on u-bolts and nuts
10046624 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 14:00 | Severe corrosion on pins
10046625 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 14:40
10046625 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:40
10046625 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:40 | Frozen bolts and nuts on clamp
10046625 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:40 | Rust flaking on caps and pins
10046626 | OTA-WKM-C-0472-Earthwire HW Set | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:25 | Surface pitting
10046626 | OTA-WKM-C-0472-Earthwire HW Set | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:25
13040205 | OTA-WKM-C-0472-Earthwire Attachment | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 16:03
13040205 | OTA-WKM-C-0472-Earthwire Attachment | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 16:03
13040205 | OTA-WKM-C-0472-Earthwire Attachment | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 16:03 | Wind wear.
13040205 | OTA-WKM-C-0472-Earthwire Attachment | OTA-WKM-C0472 | OTA-WKM-C0472-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 16:03
13073871 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 15:58
13073871 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 15:58
13073871 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 15:58 | Significant corrosion on steel plate
13073871 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0472 | OTA-WKM-C0472-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 15:58 | Significant corrosion on through bolt
13073872 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:17
13073872 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:17
13073872 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:17
13073872 | OTA-WKM-C-0472-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:17
13317471 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-11 15:34
13317471 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-11 15:34
13317471 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-11 15:34
13317471 | OTA-WKM-C-0472-Insulator Set-OHW-OTA-2 | OTA-WKM-C0472 | OTA-WKM-C0472-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-11 15:34
10047220 | OTA-WKM-C-0472-0473-Conductor-OHW-OTA-2 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 14:31
10047220 | OTA-WKM-C-0472-0473-Conductor-OHW-OTA-2 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:31
10047220 | OTA-WKM-C-0472-0473-Conductor-OHW-OTA-2 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:31 | Significant corrosion on bolts and ring
10047221 | OTA-WKM-C-0472-0473-Conductor-OHW-OTA-1 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-18 14:31
10047221 | OTA-WKM-C-0472-0473-Conductor-OHW-OTA-1 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:31
10047221 | OTA-WKM-C-0472-0473-Conductor-OHW-OTA-1 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:31 | Significant corrosion on bolts and ring
10047222 | OTA-WKM-C-0472-0473-Earthwire-A0 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:28
10047222 | OTA-WKM-C-0472-0473-Earthwire-A0 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 14:28
13329956 | OTA-WKM-C-0472-0473-Earthwire-C0 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 | CA copied from EW A0 Feb/2026
13329956 | OTA-WKM-C-0472-0473-Earthwire-C0 | OTA-WKM-C0472-0473 | OTA-WKM-C0472-0473-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-18 | CA copied from EW A0 Feb/2026
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-07-21 | CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-07-21 | CA
10046627 | OTA-WKM-C-0473-Tower | OTA-WKM-C0473 | OTA-WKM-C0473-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046628 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:51
10046629 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-21 | CA
10046629 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 14:09
10046629 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 14:12 | Significant corrosion on u-bolts and nuts
10046629 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 14:12 | Severe corrosion on pins
10046630 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 14:56
10046630 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:56
10046630 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:56 | U bolt nuts possible frozen
10046630 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:56 | Rusty pins
10046631 | OTA-WKM-C-0473-Earthwire HW Set | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:49 | Heavy corrosion
10046631 | OTA-WKM-C-0473-Earthwire HW Set | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:49
13040206 | OTA-WKM-C-0473-Earthwire Attachment | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:43 | Rust flaking
13040206 | OTA-WKM-C-0473-Earthwire Attachment | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:43
13040206 | OTA-WKM-C-0473-Earthwire Attachment | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:43
13040206 | OTA-WKM-C-0473-Earthwire Attachment | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:43
13073873 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:15
13073873 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:15
13073873 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:15 | Oyster rust
13073873 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0473 | OTA-WKM-C0473-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:15
13073874 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:03
13073874 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:03
13073874 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:03
13073874 | OTA-WKM-C-0473-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:03
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13313422 | OTA-WKM-C-0473-Tower Foundation | OTA-WKM-C0473 | OTA-WKM-C0473-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-28 | RSA2 24-25 Grillage Refurbishment
13317472 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:29
13317472 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:29
13317472 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:29
13317472 | OTA-WKM-C-0473-Insulator Set-OHW-OTA-2 | OTA-WKM-C0473 | OTA-WKM-C0473-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:29
10047223 | OTA-WKM-C-0473-0474-Conductor-OHW-OTA-2 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-17 14:58
10047223 | OTA-WKM-C-0473-0474-Conductor-OHW-OTA-2 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:58
10047223 | OTA-WKM-C-0473-0474-Conductor-OHW-OTA-2 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:58 | Nuts and bolts rusty
10047224 | OTA-WKM-C-0473-0474-Conductor-OHW-OTA-1 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-17 14:58
10047224 | OTA-WKM-C-0473-0474-Conductor-OHW-OTA-1 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:58
10047224 | OTA-WKM-C-0473-0474-Conductor-OHW-OTA-1 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 14:58 | Corrosion nuts bolts
10047225 | OTA-WKM-C-0473-0474-Earthwire-A0 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 15:45
10047225 | OTA-WKM-C-0473-0474-Earthwire-A0 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 15:45
13329957 | OTA-WKM-C-0473-0474-Earthwire-C0 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 | CA copied from EW A0 Feb/2026
13329957 | OTA-WKM-C-0473-0474-Earthwire-C0 | OTA-WKM-C0473-0474 | OTA-WKM-C0473-0474-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 | CA copied from EW A0 Feb/2026
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-10-20 01:00 | CA
10046632 | OTA-WKM-C-0474-Tower | OTA-WKM-C0474 | OTA-WKM-C0474-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rust staining
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rated as per TP specs
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rust staining
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rated as per TP specs
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rust staining
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rated as per TP specs
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rust staining Dug leg D
10046633 | OTA-WKM-C-0474-Tower Foundation | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 12:29 | Rated as per TP specs
10046635 | OTA-WKM-C-0474-Insulator Set-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:04
10046635 | OTA-WKM-C-0474-Insulator Set-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:04
10046635 | OTA-WKM-C-0474-Insulator Set-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:04 | Significant corrosion on caps and pins
10046635 | OTA-WKM-C-0474-Insulator Set-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:04 | Significant corrosion on caps and pins
12058878 | OTA-WKM-C-0474-Earthwire HW Set | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:06 | Degradation of coating
12058878 | OTA-WKM-C-0474-Earthwire HW Set | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:06
13040207 | OTA-WKM-C-0474-Earthwire Attachment | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:50
13040207 | OTA-WKM-C-0474-Earthwire Attachment | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:50
13040207 | OTA-WKM-C-0474-Earthwire Attachment | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:50
13040207 | OTA-WKM-C-0474-Earthwire Attachment | OTA-WKM-C0474 | OTA-WKM-C0474-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:50
13073875 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:00
13073875 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:00
13073875 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:00
13073875 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0474 | OTA-WKM-C0474-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:00
13073876 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0474 | OTA-WKM-C0474-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:49
13073876 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0474 | OTA-WKM-C0474-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:49
13073876 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0474 | OTA-WKM-C0474-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:49 | Significant corrosion
13073876 | OTA-WKM-C-0474-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0474 | OTA-WKM-C0474-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 11:49
13253882 | OTA-WKM-C-0474-Insulator Set-OHW-OTA-2 | OTA-WKM-C0474 | OTA-WKM-C0474-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 | RSA2 TL Insulators 22-23
13253882 | OTA-WKM-C-0474-Insulator Set-OHW-OTA-2 | OTA-WKM-C0474 | OTA-WKM-C0474-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 | RSA2 TL Insulators 22-23
13253882 | OTA-WKM-C-0474-Insulator Set-OHW-OTA-2 | OTA-WKM-C0474 | OTA-WKM-C0474-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-05-11 | RSA2 TL Insulators 22-23
10047226 | OTA-WKM-C-0474-0475-Conductor-OHW-OTA-2 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 12:08
10047226 | OTA-WKM-C-0474-0475-Conductor-OHW-OTA-2 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:08
10047226 | OTA-WKM-C-0474-0475-Conductor-OHW-OTA-2 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:08 | Significant corrosion on bolts and rings
10047227 | OTA-WKM-C-0474-0475-Conductor-OHW-OTA-1 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 12:07
10047227 | OTA-WKM-C-0474-0475-Conductor-OHW-OTA-1 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:07
10047227 | OTA-WKM-C-0474-0475-Conductor-OHW-OTA-1 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:07 | Significant corrosion on bolts and rings
10047228 | OTA-WKM-C-0474-0475-Earthwire-A0 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:10
10047228 | OTA-WKM-C-0474-0475-Earthwire-A0 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 12:10 | Surface pitting
13329958 | OTA-WKM-C-0474-0475-Earthwire-C0 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 | CA copied from EW A0 Feb/2026
13329958 | OTA-WKM-C-0474-0475-Earthwire-C0 | OTA-WKM-C0474-0475 | OTA-WKM-C0474-0475-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 | Surface pitting. CA copied from EW A0 Feb/2026
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-13
10046637 | OTA-WKM-C-0475-Tower | OTA-WKM-C0475 | OTA-WKM-C0475-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
12058879 | OTA-WKM-C-0475-Earthwire HW Set | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:18 | Heavy corrosion
12058879 | OTA-WKM-C-0475-Earthwire HW Set | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:18
13040208 | OTA-WKM-C-0475-Earthwire Attachment | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16 | Wind wear
13040208 | OTA-WKM-C-0475-Earthwire Attachment | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16
13040208 | OTA-WKM-C-0475-Earthwire Attachment | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16
13040208 | OTA-WKM-C-0475-Earthwire Attachment | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16 | Wind wear
13073877 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:14
13073877 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:14
13073877 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:14
13073877 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:14
13073878 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16
13073878 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16
13073878 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16
13073878 | OTA-WKM-C-0475-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:16
13186214 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:17
13186214 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:17
13186214 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:17
13186214 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-2 | OTA-WKM-C0475 | OTA-WKM-C0475-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:17
13204578 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13204578 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13204578 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13204578 | OTA-WKM-C-0475-Insulator Set-OHW-OTA-1 | OTA-WKM-C0475 | OTA-WKM-C0475-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
13232366 | OTA-WKM-C-0475-Tower Foundation | OTA-WKM-C0475 | OTA-WKM-C0475-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-17 10:10
10047229 | OTA-WKM-C-0475-0476-Conductor-OHW-OTA-2 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-17 10:20
10047229 | OTA-WKM-C-0475-0476-Conductor-OHW-OTA-2 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-20 | 1965 | COSE_DAMPER COND | Damper Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:20
10047229 | OTA-WKM-C-0475-0476-Conductor-OHW-OTA-2 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:20 | Corrosion on nuts bolts
10047230 | OTA-WKM-C-0475-0476-Conductor-OHW-OTA-1 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-17 10:20
10047230 | OTA-WKM-C-0475-0476-Conductor-OHW-OTA-1 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-10 | 1965 | COSE_DAMPER COND | Damper Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:20
10047230 | OTA-WKM-C-0475-0476-Conductor-OHW-OTA-1 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:20 | Corrosion on nuts bolts
10047231 | OTA-WKM-C-0475-0476-Earthwire-A0 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 10:29
10047231 | OTA-WKM-C-0475-0476-Earthwire-A0 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 10:29
13329959 | OTA-WKM-C-0475-0476-Earthwire-C0 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-17 | CA copied from EW A0 Feb/2026
13329959 | OTA-WKM-C-0475-0476-Earthwire-C0 | OTA-WKM-C0475-0476 | OTA-WKM-C0475-0476-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-17 | CA copied from EW A0 Feb/2026
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 12:59
10046642 | OTA-WKM-C-0476-Tower | OTA-WKM-C0476 | OTA-WKM-C0476-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-02 | Routine CA
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
10046643 | OTA-WKM-C-0476-Tower Foundation | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 14:33
12058880 | OTA-WKM-C-0476-Earthwire HW Set | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 14:33 | Severe corrosion
12058880 | OTA-WKM-C-0476-Earthwire HW Set | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 14:33
13216930 | OTA-WKM-C-0476-Earthwire Attachment | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 14:32
13216930 | OTA-WKM-C-0476-Earthwire Attachment | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 14:32
13216930 | OTA-WKM-C-0476-Earthwire Attachment | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 14:32
13216930 | OTA-WKM-C-0476-Earthwire Attachment | OTA-WKM-C0476 | OTA-WKM-C0476-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 14:32
13216931 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13216931 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13216931 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13216931 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13216932 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13216932 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13216932 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13216932 | OTA-WKM-C-0476-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:26
13285518 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 17:51
13285518 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 17:51
13285518 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 17:51
13285518 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-1 | OTA-WKM-C0476 | OTA-WKM-C0476-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-05 17:51
13285519 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:02
13285519 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:02
13285519 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:02
13285519 | OTA-WKM-C-0476-Insulator Set-OHW-OTA-2 | OTA-WKM-C0476 | OTA-WKM-C0476-20 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-25 13:02
10047232 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-2 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 14:27
10047232 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-2 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 14:27
10047232 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-2 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-02 | The mandatory replacement item is 7 Alcan Spring Spacers on Y phase & 7 Andre GEGB Spacers on B phase.
10047232 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-2 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:27
10047233 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-1 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 14:27
10047233 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-1 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 14:27
10047233 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-1 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-02 | The mandatory replacement item is 7 Alcan Spring Spacers on Y phase & 7 Andre GEGB Spacers on R phase.
10047233 | OTA-WKM-C-0476-0477-Conductor-OHW-OTA-1 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-14 14:27
10047234 | OTA-WKM-C-0476-0477-Earthwire-A0 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 15:14
10047234 | OTA-WKM-C-0476-0477-Earthwire-A0 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 15:14
10047234 | OTA-WKM-C-0476-0477-Earthwire-A0 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-08-20 | CA
13329960 | OTA-WKM-C-0476-0477-Earthwire-C0 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 | CA copied from EW A0 Feb/2026
13329960 | OTA-WKM-C-0476-0477-Earthwire-C0 | OTA-WKM-C0476-0477 | OTA-WKM-C0476-0477-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 | CA copied from EW A0 Feb/2026
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-29 12:24
10046647 | OTA-WKM-C-0477-Tower | OTA-WKM-C0477 | OTA-WKM-C0477-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
10046648 | OTA-WKM-C-0477-Tower Foundation | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 11:27
12058881 | OTA-WKM-C-0477-Earthwire HW Set | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2017-02-13 01:00
13040210 | OTA-WKM-C-0477-Earthwire Attachment | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:20 | Replced
13040210 | OTA-WKM-C-0477-Earthwire Attachment | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 12:20 | Replaced
13040210 | OTA-WKM-C-0477-Earthwire Attachment | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 12:20 | Replaced
13040210 | OTA-WKM-C-0477-Earthwire Attachment | OTA-WKM-C0477 | OTA-WKM-C0477-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-14 12:20 | Replaced
13073881 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:24
13073881 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:24
13073881 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:24
13073881 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:24 | Rust flaking
13073882 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:25
13073882 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:25
13073882 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:25
13073882 | OTA-WKM-C-0477-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:25 | Rust flaking
13285520 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 14:05
13285520 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 14:04
13285520 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 14:05
13285520 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-1 | OTA-WKM-C0477 | OTA-WKM-C0477-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-05-06 14:05
13285521 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:28
13285521 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:28
13285521 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:28
13285521 | OTA-WKM-C-0477-Insulator Set-OHW-OTA-2 | OTA-WKM-C0477 | OTA-WKM-C0477-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-29 12:28
10047235 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-2 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 12:21
10047235 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-2 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:21
10047235 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-2 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-20 | 1965 | COSE_INTERPHASE SPACER CO | Interphase Spcr Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10047235 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-2 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:21 | Nuts bolts rusty
10047236 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-1 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-14 12:22
10047236 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-1 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:22
10047236 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-1 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-10 | 1965 | COSE_INTERPHASE SPACER CO | Interphase Spcr Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10047236 | OTA-WKM-C-0477-0478-Conductor-OHW-OTA-1 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 12:22 | Nuts bolts rusty
10047237 | OTA-WKM-C-0477-0478-Earthwire-A0 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 13:17
10047237 | OTA-WKM-C-0477-0478-Earthwire-A0 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 13:17
13329961 | OTA-WKM-C-0477-0478-Earthwire-C0 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 | CA copied from EW A0 Feb/2026
13329961 | OTA-WKM-C-0477-0478-Earthwire-C0 | OTA-WKM-C0477-0478 | OTA-WKM-C0477-0478-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-14 | CA copied from EW A0 Feb/2026
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-07-21 | OHW-WKM-1 has exploded bolts on outside of HSH.
10046652 | OTA-WKM-C-0478-Tower | OTA-WKM-C0478 | OTA-WKM-C0478-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates rusty.
10046656 | OTA-WKM-C-0478-Earthwire HW Set | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:04 | Heavily corroded
10046656 | OTA-WKM-C-0478-Earthwire HW Set | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:04
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
12006164 | OTA-WKM-C-0478-Tower Foundation | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-13 12:56
13040211 | OTA-WKM-C-0478-Earthwire Attachment | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 12:58
13040211 | OTA-WKM-C-0478-Earthwire Attachment | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 12:58
13040211 | OTA-WKM-C-0478-Earthwire Attachment | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 12:58
13040211 | OTA-WKM-C-0478-Earthwire Attachment | OTA-WKM-C0478 | OTA-WKM-C0478-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 12:58
13170134 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 | 2018 | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:03
13170134 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 | 2018 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:03
13170134 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 | 2018 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:03
13170134 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 | 2018 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:03
13216933 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 12:59
13216933 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 12:59
13216933 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 12:59
13216933 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 12:59
13216934 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 12:59
13216934 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 12:59
13216934 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-09-05
13216934 | OTA-WKM-C-0478-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0478 | OTA-WKM-C0478-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 12:59
13227067 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:01
13227067 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:01
13227067 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:01
13227067 | OTA-WKM-C-0478-Insulator Set-OHW-OTA-1 | OTA-WKM-C0478 | OTA-WKM-C0478-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-13 13:01
10047238 | OTA-WKM-C-0478-0479-Conductor-OHW-OTA-2 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-13 13:07
10047238 | OTA-WKM-C-0478-0479-Conductor-OHW-OTA-2 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:07
10047238 | OTA-WKM-C-0478-0479-Conductor-OHW-OTA-2 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:07 | Heavy corrosion on nutsbolts
10047239 | OTA-WKM-C-0478-0479-Conductor-OHW-OTA-1 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-13 13:05
10047239 | OTA-WKM-C-0478-0479-Conductor-OHW-OTA-1 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:05
10047239 | OTA-WKM-C-0478-0479-Conductor-OHW-OTA-1 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:05 | Nuts bolts heavy corrosion
10047240 | OTA-WKM-C-0478-0479-Earthwire-A0 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:44
10047240 | OTA-WKM-C-0478-0479-Earthwire-A0 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 13:44
13329962 | OTA-WKM-C-0478-0479-Earthwire-C0 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 | CA copied from EW A0 Feb/2026
13329962 | OTA-WKM-C-0478-0479-Earthwire-C0 | OTA-WKM-C0478-0479 | OTA-WKM-C0478-0479-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-13 | CA copied from EW A0 Feb/2026
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046657 | OTA-WKM-C-0479-Tower | OTA-WKM-C0479 | OTA-WKM-C0479-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:31
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 14:31
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:31 | Dug leg B
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 14:31
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:31
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 14:31
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:31
10046658 | OTA-WKM-C-0479-Tower Foundation | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 14:31
10332831 | OTA-WKM-C-0479-Earthwire HW Set | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:26
10332831 | OTA-WKM-C-0479-Earthwire HW Set | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:26
13040212 | OTA-WKM-C-0479-Earthwire Attachment | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:25
13040212 | OTA-WKM-C-0479-Earthwire Attachment | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:25
13040212 | OTA-WKM-C-0479-Earthwire Attachment | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:25
13040212 | OTA-WKM-C-0479-Earthwire Attachment | OTA-WKM-C0479 | OTA-WKM-C0479-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:25
13073885 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:12
13073885 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:12
13073885 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:12
13073885 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:12
13073886 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:13
13073886 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:13
13073886 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:13
13073886 | OTA-WKM-C-0479-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:13
13186215 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:11
13186215 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:11
13186215 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:11
13186215 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-1 | OTA-WKM-C0479 | OTA-WKM-C0479-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:11
13186216 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:12
13186216 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:12
13186216 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:12
13186216 | OTA-WKM-C-0479-Insulator Set-OHW-OTA-2 | OTA-WKM-C0479 | OTA-WKM-C0479-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 14:12
10047241 | OTA-WKM-C-0479-0480-Conductor-OHW-OTA-2 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-05 14:16
10047241 | OTA-WKM-C-0479-0480-Conductor-OHW-OTA-2 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:16
10047241 | OTA-WKM-C-0479-0480-Conductor-OHW-OTA-2 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-07-21 | CA
10047242 | OTA-WKM-C-0479-0480-Conductor-OHW-OTA-1 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-05 14:16
10047242 | OTA-WKM-C-0479-0480-Conductor-OHW-OTA-1 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:16
10047242 | OTA-WKM-C-0479-0480-Conductor-OHW-OTA-1 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:16 | Significant corrosion on bolts and ring
10047242 | OTA-WKM-C-0479-0480-Conductor-OHW-OTA-1 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-10 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2015-07-21 | CA
10047243 | OTA-WKM-C-0479-0480-Earthwire-A0 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-00 |  | EASE_DAMPER COND | Damper Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:25 | Corrosion on messenger wire
10047243 | OTA-WKM-C-0479-0480-Earthwire-A0 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 14:25
13329963 | OTA-WKM-C-0479-0480-Earthwire-C0 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-00 |  | EASE_DAMPER COND | Damper Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 | Corrosion on messenger drooping. CA copied from EW A0 Feb/2026
13329963 | OTA-WKM-C-0479-0480-Earthwire-C0 | OTA-WKM-C0479-0480 | OTA-WKM-C0479-0480-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 | CA copied from EW A0 Feb/2026
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-11 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046662 | OTA-WKM-C-0480-Tower | OTA-WKM-C0480 | OTA-WKM-C0480-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-13 | Routine CA
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046663 | OTA-WKM-C-0480-Tower Foundation | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 11:55
10046664 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 | 2002 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:49
10046664 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 | 2002 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 12:49
10046664 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 | 2002 | INSE_SUSP HOT END COND | Susp Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:49
10046664 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 | 2002 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 12:49
10046665 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 | 2002 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:00
10046665 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 | 2002 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 12:00
10046665 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 | 2002 | INSE_SUSP HOT END COND | Susp Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:00
10046665 | OTA-WKM-C-0480-Insulator Set-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 | 2002 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 12:00
12058882 | OTA-WKM-C-0480-Earthwire HW Set | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:10 | Severe corrosion
12058882 | OTA-WKM-C-0480-Earthwire HW Set | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:10
13040213 | OTA-WKM-C-0480-Earthwire Attachment | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:09 | Replaced
13040213 | OTA-WKM-C-0480-Earthwire Attachment | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:09 | Replaced
13040213 | OTA-WKM-C-0480-Earthwire Attachment | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:09 | Replaced
13040213 | OTA-WKM-C-0480-Earthwire Attachment | OTA-WKM-C0480 | OTA-WKM-C0480-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:09 | Replaced
13073887 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:02
13073887 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:02
13073887 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:02
13073887 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0480 | OTA-WKM-C0480-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:02
13073888 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:04
13073888 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:04
13073888 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:04
13073888 | OTA-WKM-C-0480-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0480 | OTA-WKM-C0480-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:04
10047244 | OTA-WKM-C-0480-0481-Conductor-OHW-OTA-2 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:08
10047244 | OTA-WKM-C-0480-0481-Conductor-OHW-OTA-2 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-20 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-12 12:08
10047244 | OTA-WKM-C-0480-0481-Conductor-OHW-OTA-2 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:08 | Severe corrosion on bolts
10047245 | OTA-WKM-C-0480-0481-Conductor-OHW-OTA-1 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-12 12:05
10047245 | OTA-WKM-C-0480-0481-Conductor-OHW-OTA-1 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:05
10047245 | OTA-WKM-C-0480-0481-Conductor-OHW-OTA-1 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:05 | Nuts bolts severe corrosion
10047246 | OTA-WKM-C-0480-0481-Earthwire-A0 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:51
10047246 | OTA-WKM-C-0480-0481-Earthwire-A0 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 12:51
13329964 | OTA-WKM-C-0480-0481-Earthwire-C0 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 | CA copied from EW A0 Feb/2026
13329964 | OTA-WKM-C-0480-0481-Earthwire-C0 | OTA-WKM-C0480-0481 | OTA-WKM-C0480-0481-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-12 | CA copied from EW A0 Feb/2026
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-10-29 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046667 | OTA-WKM-C-0481-Tower | OTA-WKM-C0481 | OTA-WKM-C0481-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10046668 | OTA-WKM-C-0481-Tower Foundation | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-06 10:30
10261296 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:35
10261296 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:35
10261296 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:35
10261296 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:35
10261304 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:36
10261304 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:36
10261304 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:36
10261304 | OTA-WKM-C-0481-Insulator Set-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:36
12019093 | OTA-WKM-C-0481-Earthwire HW Set | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:42
12019093 | OTA-WKM-C-0481-Earthwire HW Set | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:42
13040214 | OTA-WKM-C-0481-Earthwire Attachment | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 20:20 | changed
13040214 | OTA-WKM-C-0481-Earthwire Attachment | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 20:23 | change all bolts and nuts
13040214 | OTA-WKM-C-0481-Earthwire Attachment | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 20:21 | change EW attachment point hardware and bolts
13040214 | OTA-WKM-C-0481-Earthwire Attachment | OTA-WKM-C0481 | OTA-WKM-C0481-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-01-11 20:20 | changed
13073889 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
13073889 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
13073889 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
13073889 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0481 | OTA-WKM-C0481-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
13073890 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
13073890 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
13073890 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
13073890 | OTA-WKM-C-0481-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0481 | OTA-WKM-C0481-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 09:17
10047247 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-2 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:43
10047247 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-2 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-20 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:43
10047247 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-2 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10047247 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-2 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:43 | Heavy corrosion
10047248 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-1 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-06 10:43
10047248 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-1 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:43
10047248 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-1 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10047248 | OTA-WKM-C-0481-0482-Conductor-OHW-OTA-1 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:43 | Nuts and bolts heavy corrosion
10047249 | OTA-WKM-C-0481-0482-Earthwire-A0 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-00 |  | EASE_DAMPER COND | Damper Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:44
10047249 | OTA-WKM-C-0481-0482-Earthwire-A0 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 10:44
10047249 | OTA-WKM-C-0481-0482-Earthwire-A0 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-04-09 | CA
13329965 | OTA-WKM-C-0481-0482-Earthwire-C0 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-00 |  | EASE_DAMPER COND | Damper Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 | CA copied from EW A0 Feb/2026
13329965 | OTA-WKM-C-0481-0482-Earthwire-C0 | OTA-WKM-C0481-0482 | OTA-WKM-C0481-0482-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-06 | CA copied from EW A0 Feb/2026
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-29 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046672 | OTA-WKM-C-0482-Tower | OTA-WKM-C0482 | OTA-WKM-C0482-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C.
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:05
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:05
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:05
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:05
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:06
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:06
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:06
10046673 | OTA-WKM-C-0482-Tower Foundation | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:06
10261297 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-11 13:12
10261297 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:12
10261297 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:12
10261297 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:12
10261305 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-11 13:11
10261305 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:11
10261305 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:11
10261305 | OTA-WKM-C-0482-Insulator Set-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:11
10332832 | OTA-WKM-C-0482-Earthwire HW Set | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:25
10332832 | OTA-WKM-C-0482-Earthwire HW Set | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:25
13040215 | OTA-WKM-C-0482-Earthwire Attachment | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:22
13040215 | OTA-WKM-C-0482-Earthwire Attachment | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:22
13040215 | OTA-WKM-C-0482-Earthwire Attachment | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:22
13040215 | OTA-WKM-C-0482-Earthwire Attachment | OTA-WKM-C0482 | OTA-WKM-C0482-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:22
13073891 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
13073891 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
13073891 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
13073891 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0482 | OTA-WKM-C0482-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
13073892 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
13073892 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
13073892 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
13073892 | OTA-WKM-C-0482-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0482 | OTA-WKM-C0482-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:13
10047250 | OTA-WKM-C-0482-0483-Conductor-OHW-OTA-2 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-11 13:07
10047250 | OTA-WKM-C-0482-0483-Conductor-OHW-OTA-2 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:07
10047250 | OTA-WKM-C-0482-0483-Conductor-OHW-OTA-2 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:07 | Nuts bolts heavy corrosion
10047251 | OTA-WKM-C-0482-0483-Conductor-OHW-OTA-1 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-11 13:06
10047251 | OTA-WKM-C-0482-0483-Conductor-OHW-OTA-1 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:06
10047251 | OTA-WKM-C-0482-0483-Conductor-OHW-OTA-1 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:06 | Nutsbolts heavy corrosion
10047252 | OTA-WKM-C-0482-0483-Earthwire-A0 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 13:28
10047252 | OTA-WKM-C-0482-0483-Earthwire-A0 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 13:28
13329966 | OTA-WKM-C-0482-0483-Earthwire-C0 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-11 | CA copied from EW A0 Feb/2026
13329966 | OTA-WKM-C-0482-0483-Earthwire-C0 | OTA-WKM-C0482-0483 | OTA-WKM-C0482-0483-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-11 | CA copied from EW A0 Feb/2026
10046677 | OTA-WKM-C-0483-Tower | OTA-WKM-C0483 | OTA-WKM-C0483-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C. Various steel work R/C throughout tower.
10046677 | OTA-WKM-C-0483-Tower | OTA-WKM-C0483 | OTA-WKM-C0483-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C. Various steel work R/C throughout tower.
10046677 | OTA-WKM-C-0483-Tower | OTA-WKM-C0483 | OTA-WKM-C0483-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C. Various steel work R/C throughout tower.
10046677 | OTA-WKM-C-0483-Tower | OTA-WKM-C0483 | OTA-WKM-C0483-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C. Various steel work R/C throughout tower.
10046677 | OTA-WKM-C-0483-Tower | OTA-WKM-C0483 | OTA-WKM-C0483-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C. Various steel work R/C throughout tower.
10046677 | OTA-WKM-C-0483-Tower | OTA-WKM-C0483 | OTA-WKM-C0483-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-29 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046677 | OTA-WKM-C-0483-Tower | OTA-WKM-C0483 | OTA-WKM-C0483-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-05-20 | CA - E/W attachment plates R/C. Various steel work R/C throughout tower.
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10046678 | OTA-WKM-C-0483-Tower Foundation | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:34
10332833 | OTA-WKM-C-0483-Earthwire HW Set | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-05 09:46
10332833 | OTA-WKM-C-0483-Earthwire HW Set | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2019-08-13 12:03
13040216 | OTA-WKM-C-0483-Earthwire Attachment | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-05 10:28
13040216 | OTA-WKM-C-0483-Earthwire Attachment | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 10:28 | New
13040216 | OTA-WKM-C-0483-Earthwire Attachment | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-05 10:28 | New
13040216 | OTA-WKM-C-0483-Earthwire Attachment | OTA-WKM-C0483 | OTA-WKM-C0483-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 10:28 | New
13073893 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:19
13073893 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:19
13073893 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:19
13073893 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:19
13073894 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:20
13073894 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:20
13073894 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:20
13073894 | OTA-WKM-C-0483-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:20
13186217 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-05 09:44
13186217 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 09:44
13186217 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 09:44
13186217 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-1 | OTA-WKM-C0483 | OTA-WKM-C0483-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 09:44
13186218 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-05 09:44
13186218 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 09:44
13186218 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 09:44
13186218 | OTA-WKM-C-0483-Insulator Set-OHW-OTA-2 | OTA-WKM-C0483 | OTA-WKM-C0483-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-05 09:44
10047253 | OTA-WKM-C-0483-0484-Conductor-OHW-OTA-2 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-05 10:17
10047253 | OTA-WKM-C-0483-0484-Conductor-OHW-OTA-2 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:17
10047253 | OTA-WKM-C-0483-0484-Conductor-OHW-OTA-2 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:17 | Heavy corrosion on nuts bots
10047254 | OTA-WKM-C-0483-0484-Conductor-OHW-OTA-1 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-05 10:13
10047254 | OTA-WKM-C-0483-0484-Conductor-OHW-OTA-1 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:13
10047254 | OTA-WKM-C-0483-0484-Conductor-OHW-OTA-1 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:13 | Nuts bolts heavy corrosion
10047255 | OTA-WKM-C-0483-0484-Earthwire-A0 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 10:29
10047255 | OTA-WKM-C-0483-0484-Earthwire-A0 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 10:29
13329967 | OTA-WKM-C-0483-0484-Earthwire-C0 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-05 | CA copied from EW A0 Feb/2026
13329967 | OTA-WKM-C-0483-0484-Earthwire-C0 | OTA-WKM-C0483-0484 | OTA-WKM-C0483-0484-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-05 | CA copied from EW A0 Feb/2026
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-29 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046682 | OTA-WKM-C-0484-Tower | OTA-WKM-C0484 | OTA-WKM-C0484-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046683 | OTA-WKM-C-0484-Tower Foundation | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:36
10046684 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-04 15:07
10046684 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 14:28
10046684 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 14:29
10046684 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 14:29 | Severe corrosion on pins
12058883 | OTA-WKM-C-0484-Earthwire HW Set | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:33 | Heavy corrosion on armour rods
12058883 | OTA-WKM-C-0484-Earthwire HW Set | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-10-04 14:33
13073895 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:26
13073895 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:26
13073895 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:26
13073895 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:26
13073896 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:38
13073896 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:38
13073896 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:38
13073896 | OTA-WKM-C-0484-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:38
13216935 | OTA-WKM-C-0484-Earthwire Attachment | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 14:38
13216935 | OTA-WKM-C-0484-Earthwire Attachment | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 14:38
13216935 | OTA-WKM-C-0484-Earthwire Attachment | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 14:38
13216935 | OTA-WKM-C-0484-Earthwire Attachment | OTA-WKM-C0484 | OTA-WKM-C0484-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 14:38
13317473 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 | 2025 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2025-10-14 | Replaced during RSA2 25-26 Reins Project
13317473 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 | 2025 | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-14 | Replaced during RSA2 25-26 Reins Project
13317473 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 | 2025 | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-14 | Replaced during RSA2 25-26 Reins Project
13317473 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-1 | OTA-WKM-C0484 | OTA-WKM-C0484-10 | 2025 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-14 | Replaced during RSA2 25-26 Reins Project
13317474 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:26
13317474 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:26
13317474 | OTA-WKM-C-0484-Insulator Set-OHW-OTA-2 | OTA-WKM-C0484 | OTA-WKM-C0484-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:26
10047256 | OTA-WKM-C-0484-0485-Conductor-OHW-OTA-2 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:41
10047256 | OTA-WKM-C-0484-0485-Conductor-OHW-OTA-2 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-20 | 1965 | COSE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-04 14:41
10047256 | OTA-WKM-C-0484-0485-Conductor-OHW-OTA-2 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:41 | Corrosion
10047257 | OTA-WKM-C-0484-0485-Conductor-OHW-OTA-1 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 14:40
10047257 | OTA-WKM-C-0484-0485-Conductor-OHW-OTA-1 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-10 | 1965 | COSE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-04 14:40
10047257 | OTA-WKM-C-0484-0485-Conductor-OHW-OTA-1 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 14:40 | Corrosion
10047258 | OTA-WKM-C-0484-0485-Earthwire-A0 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-04 15:09
10047258 | OTA-WKM-C-0484-0485-Earthwire-A0 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 15:09
13329968 | OTA-WKM-C-0484-0485-Earthwire-C0 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-00 |  | EASE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-04 | CA copied from EW A0 Feb/2026
13329968 | OTA-WKM-C-0484-0485-Earthwire-C0 | OTA-WKM-C0484-0485 | OTA-WKM-C0484-0485-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 | CA copied from EW A0 Feb/2026
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-15 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-02-09 01:00 | CA
10046687 | OTA-WKM-C-0485-Tower | OTA-WKM-C0485 | OTA-WKM-C0485-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2016-09-05
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046688 | OTA-WKM-C-0485-Tower Foundation | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 11:53
10046689 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-10-04 12:46
10046689 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 15:03
10046689 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 15:08
10046689 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 15:04 | Severe corrosion on caps and pins
10046691 | OTA-WKM-C-0485-Earthwire HW Set | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:24 | Significant corrosion on strand
10046691 | OTA-WKM-C-0485-Earthwire HW Set | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 12:24 | Rated as per TP service specs
13073897 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0485 | OTA-WKM-C0485-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:47
13073897 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0485 | OTA-WKM-C0485-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:47
13073897 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0485 | OTA-WKM-C0485-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:47
13073897 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0485 | OTA-WKM-C0485-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:47
13073898 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:13
13073898 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:13
13073898 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:13
13073898 | OTA-WKM-C-0485-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:13
13245176 | OTA-WKM-C-0485-Earthwire Attachment | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 12:24
13245176 | OTA-WKM-C-0485-Earthwire Attachment | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 12:24
13245176 | OTA-WKM-C-0485-Earthwire Attachment | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 12:24
13245176 | OTA-WKM-C-0485-Earthwire Attachment | OTA-WKM-C0485 | OTA-WKM-C0485-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-10-04 12:24
13317475 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-1 | OTA-WKM-C0485 | OTA-WKM-C0485-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-17 06:26
13317475 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-1 | OTA-WKM-C0485 | OTA-WKM-C0485-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-17 06:26
13317475 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-1 | OTA-WKM-C0485 | OTA-WKM-C0485-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-17 06:26
13317476 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-12 16:20
13317476 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-12 16:20
13317476 | OTA-WKM-C-0485-Insulator Set-OHW-OTA-2 | OTA-WKM-C0485 | OTA-WKM-C0485-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-12 16:20
10047259 | OTA-WKM-C-0485-0486-Conductor-OHW-OTA-2 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-04 12:19
10047259 | OTA-WKM-C-0485-0486-Conductor-OHW-OTA-2 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:19
10047259 | OTA-WKM-C-0485-0486-Conductor-OHW-OTA-2 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:19 | Significant corrosion on bolts and rings
10047260 | OTA-WKM-C-0485-0486-Conductor-OHW-OTA-1 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-10-04 12:20
10047260 | OTA-WKM-C-0485-0486-Conductor-OHW-OTA-1 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:20
10047260 | OTA-WKM-C-0485-0486-Conductor-OHW-OTA-1 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 12:20 | Significant corrosion on bolts and rings
10047261 | OTA-WKM-C-0485-0486-Earthwire-A0 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-00 |  | EASE_DAMPER COND | Damper Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 13:13 | Rust staining on messenger wire on both circuits
10047261 | OTA-WKM-C-0485-0486-Earthwire-A0 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 13:13 | RC earth wire on both circuits
13329969 | OTA-WKM-C-0485-0486-Earthwire-C0 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-00 |  | EASE_DAMPER COND | Damper Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 | Rust staining on messenger wire on both circuits. CA copied from EW A0 Feb/2026
13329969 | OTA-WKM-C-0485-0486-Earthwire-C0 | OTA-WKM-C0485-0486 | OTA-WKM-C0485-0486-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-10-04 | RC earth wire on both circuits. CA copied from EW A0 Feb/2026
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-11 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2015-07-15 | Rust coming through paint on Ins and EW attachments.
10046692 | OTA-WKM-C-0486-Tower | OTA-WKM-C0486 | OTA-WKM-C0486-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Leg interface is visible
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Significant corrosion
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Leg interface is visible
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Significant corrosion
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Leg interface is visible
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Significant corrosion
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Leg interface is visible
10046693 | OTA-WKM-C-0486-Tower Foundation | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-08 19:33 | Significant corrosion on interface
10046694 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-16 15:28
10046694 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 15:31
10046694 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 15:32 | Significant corrosion on clevis
10046694 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2025-07-31 15:31 | Severe corrosion on caps and pins
10046696 | OTA-WKM-C-0486-Earthwire HW Set | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 30 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:22 | Surface pitting wrong overlay
10046696 | OTA-WKM-C-0486-Earthwire HW Set | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-16 15:22
13040219 | OTA-WKM-C-0486-Earthwire Attachment | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2020-07-10 | Replaced earthwire att point plate WO 1612693
13040219 | OTA-WKM-C-0486-Earthwire Attachment | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-16 15:23
13040219 | OTA-WKM-C-0486-Earthwire Attachment | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-16 15:23 | Been replaced since last ca
13040219 | OTA-WKM-C-0486-Earthwire Attachment | OTA-WKM-C0486 | OTA-WKM-C0486-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2019-08-14 08:00 | Updating to 4 Readings
13073899 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0486 | OTA-WKM-C0486-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:20 | Significant corrosion
13073899 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0486 | OTA-WKM-C0486-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:20
13073899 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0486 | OTA-WKM-C0486-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:20
13073899 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0486 | OTA-WKM-C0486-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:20 | Significant corrosion
13073900 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:25 | Wind wear
13073900 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:25 | Significant corrosion
13073900 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:25
13073900 | OTA-WKM-C-0486-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:25 | Significant corrosion
13317477 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-1 | OTA-WKM-C0486 | OTA-WKM-C0486-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-15 09:56
13317477 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-1 | OTA-WKM-C0486 | OTA-WKM-C0486-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-15 09:57
13317477 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-1 | OTA-WKM-C0486 | OTA-WKM-C0486-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-10-15 09:57
13317478 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:20
13317478 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:20
13317478 | OTA-WKM-C-0486-Insulator Set-OHW-OTA-2 | OTA-WKM-C0486 | OTA-WKM-C0486-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2026-03-10 22:20
10047262 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-2 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-16 15:29
10047262 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-2 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-20 | 1965 | COSE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-16 15:29
10047262 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-2 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-20 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10047262 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-2 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:29
10047263 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-1 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-16 15:29
10047263 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-1 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-10 | 1965 | COSE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-16 15:29
10047263 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-1 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
10047263 | OTA-WKM-C-0486-0487-Conductor-OHW-OTA-1 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:29
10047264 | OTA-WKM-C-0486-0487-Earthwire-A0 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:21
10047264 | OTA-WKM-C-0486-0487-Earthwire-A0 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 15:21
10047264 | OTA-WKM-C-0486-0487-Earthwire-A0 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-07-11 | Routine CA
13329970 | OTA-WKM-C-0486-0487-Earthwire-C0 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 | CA copied from EW A0 Feb/2026
13329970 | OTA-WKM-C-0486-0487-Earthwire-C0 | OTA-WKM-C0486-0487 | OTA-WKM-C0486-0487-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-16 | CA copied from EW A0 Feb/2026
10046697 | OTA-WKM-C-0487-Tower | OTA-WKM-C0487 | OTA-WKM-C0487-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046697 | OTA-WKM-C-0487-Tower | OTA-WKM-C0487 | OTA-WKM-C0487-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046697 | OTA-WKM-C-0487-Tower | OTA-WKM-C0487 | OTA-WKM-C0487-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046697 | OTA-WKM-C-0487-Tower | OTA-WKM-C0487 | OTA-WKM-C0487-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046697 | OTA-WKM-C-0487-Tower | OTA-WKM-C0487 | OTA-WKM-C0487-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046697 | OTA-WKM-C-0487-Tower | OTA-WKM-C0487 | OTA-WKM-C0487-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-15 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046697 | OTA-WKM-C-0487-Tower | OTA-WKM-C0487 | OTA-WKM-C0487-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-06 | CA - E/W attachment plates R/C.
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10046698 | OTA-WKM-C-0487-Tower Foundation | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:23
10261298 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:56
10261298 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:56
10261298 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:56
10261298 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:56
10261306 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:54
10261306 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 | 2004 | INSE_SUSP COLD END COND | Susp Cold End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:54
10261306 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 | 2004 | INSE_SUSP HOT END COND | Susp Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:54
10261306 | OTA-WKM-C-0487-Insulator Set-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 | 2004 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:54
10332834 | OTA-WKM-C-0487-Earthwire HW Set | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-05 15:34 | Fretting loss of galv
10332834 | OTA-WKM-C-0487-Earthwire HW Set | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:34
13040220 | OTA-WKM-C-0487-Earthwire Attachment | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:36
13040220 | OTA-WKM-C-0487-Earthwire Attachment | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:36
13040220 | OTA-WKM-C-0487-Earthwire Attachment | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:36
13040220 | OTA-WKM-C-0487-Earthwire Attachment | OTA-WKM-C0487 | OTA-WKM-C0487-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:36
13073901 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:55
13073901 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:55
13073901 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:55
13073901 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0487 | OTA-WKM-C0487-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:55
13073902 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:57
13073902 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:57
13073902 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:57
13073902 | OTA-WKM-C-0487-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0487 | OTA-WKM-C0487-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:57
10047265 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-2 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:47
10047265 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-2 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-05 15:47
10047265 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-2 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-06 | CA
10047265 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-2 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-05 15:47
10047266 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-1 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-05 15:43
10047266 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-1 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-10 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-05 15:43
10047266 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-1 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-06 | CA
10047266 | OTA-WKM-C-0487-0488-Conductor-OHW-OTA-1 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-05 15:43
10047267 | OTA-WKM-C-0487-0488-Earthwire-A0 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-05 15:41
10047267 | OTA-WKM-C-0487-0488-Earthwire-A0 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-05 15:41
13329971 | OTA-WKM-C-0487-0488-Earthwire-C0 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-00 |  | EASE_DAMPER COND | Damper Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-05 | CA copied from EW A0 Feb/2026
13329971 | OTA-WKM-C-0487-0488-Earthwire-C0 | OTA-WKM-C0487-0488 | OTA-WKM-C0487-0488-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-05 | CA copied from EW A0 Feb/2026
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2025-03-11 09:43
10046702 | OTA-WKM-C-0488-Tower | OTA-WKM-C0488 | OTA-WKM-C0488-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | Routine CA
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27 | Significant corrosion
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27
10046703 | OTA-WKM-C-0488-Tower Foundation | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:27
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046704 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 | 2004 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:02
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046705 | OTA-WKM-C-0488-Insulator Set-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 | 2004 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:51
10046706 | OTA-WKM-C-0488-Earthwire HW Set | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:23
13040221 | OTA-WKM-C-0488-Earthwire Attachment | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:24
13040221 | OTA-WKM-C-0488-Earthwire Attachment | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:24
13040221 | OTA-WKM-C-0488-Earthwire Attachment | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:24
13040221 | OTA-WKM-C-0488-Earthwire Attachment | OTA-WKM-C0488 | OTA-WKM-C0488-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:24
13073903 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:25
13073903 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:25
13073903 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-09-23 19:34 | Rating wasn’t changed after Att project updated to CA60 due to rust spots
13073903 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0488 | OTA-WKM-C0488-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:25
13073904 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:22
13073904 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:22
13073904 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-09-23 19:36 | Rating wasn’t changed after Att project updated to CA60 due to rust spots
13073904 | OTA-WKM-C-0488-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0488 | OTA-WKM-C0488-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 20:22
10047268 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-2 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 19:40
10047268 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-2 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-20 | 1965 | COSE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:40
10047268 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-2 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-20 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | 3x SAD term joints (65%) & 3x ERD term joints (85%)
10047268 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-2 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 19:40
10047268 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-2 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-20 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2025-03-10 12:03
10047269 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-1 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 19:35
10047269 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-1 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-10 | 1965 | COSE_DAMPER COND | Damper Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 19:35
10047269 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-1 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2007-06-14 | 3x SAD term joints (65%) & 3x ERD term joints (85%)
10047269 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-1 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2007-06-14 | 3x SAD term joints (65%) & 3x ERD term joints (85%)
10047269 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-1 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 19:35
10047269 | OTA-WKM-C-0488-0489-Conductor-OHW-OTA-1 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-10 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2024-08-07 11:04
10047270 | OTA-WKM-C-0488-0489-Earthwire-A0 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:28
10047270 | OTA-WKM-C-0488-0489-Earthwire-A0 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 19:28 | Surface pitting both CCT
13329972 | OTA-WKM-C-0488-0489-Earthwire-C0 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-00 |  | EASE_DAMPER COND | Damper Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 | CA copied from EW A0 Feb/2026
13329972 | OTA-WKM-C-0488-0489-Earthwire-C0 | OTA-WKM-C0488-0489 | OTA-WKM-C0488-0489-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 | Surface pitting both CCT. CA copied from EW A0 Feb/2026
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-08-29 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046707 | OTA-WKM-C-0489-Tower | OTA-WKM-C0489 | OTA-WKM-C0489-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - E/W attachment plates rusty. Vegetation overgrowing around tower base.
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046708 | OTA-WKM-C-0489-Tower Foundation | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:37
10046709 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 07:39
10046709 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:39
10046709 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:39
10046709 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:39
10046710 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 | 1971 | INSE_ARMOUR ROD COND | Armour Rod Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 07:38
10046710 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 | 1971 | INSE_SUSP COLD END COND | Susp Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:38
10046710 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 | 1971 | INSE_SUSP HOT END COND | Susp Hot End Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:38
10046710 | OTA-WKM-C-0489-Insulator Set-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 | 1971 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 45 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:38
10332835 | OTA-WKM-C-0489-Earthwire HW Set | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:43 | Armour rod mostly red/brown in colourslight pitting.
10332835 | OTA-WKM-C-0489-Earthwire HW Set | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:43
13040222 | OTA-WKM-C-0489-Earthwire Attachment | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:40
13040222 | OTA-WKM-C-0489-Earthwire Attachment | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:40
13040222 | OTA-WKM-C-0489-Earthwire Attachment | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:40
13040222 | OTA-WKM-C-0489-Earthwire Attachment | OTA-WKM-C0489 | OTA-WKM-C0489-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-22 07:40
13073905 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
13073905 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
13073905 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
13073905 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0489 | OTA-WKM-C0489-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
13073906 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
13073906 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
13073906 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
13073906 | OTA-WKM-C-0489-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0489 | OTA-WKM-C0489-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:41
10047271 | OTA-WKM-C-0489-0490-Conductor-OHW-OTA-2 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 07:47
10047271 | OTA-WKM-C-0489-0490-Conductor-OHW-OTA-2 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-20 | 1965 | COSE_DAMPER COND | Damper Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 07:47
10047271 | OTA-WKM-C-0489-0490-Conductor-OHW-OTA-2 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-09-22 07:47
10047272 | OTA-WKM-C-0489-0490-Conductor-OHW-OTA-1 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 10:03
10047272 | OTA-WKM-C-0489-0490-Conductor-OHW-OTA-1 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-10 | 1965 | COSE_DAMPER COND | Damper Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 10:03
10047272 | OTA-WKM-C-0489-0490-Conductor-OHW-OTA-1 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2022-09-22 10:03
10047273 | OTA-WKM-C-0489-0490-Earthwire-A0 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-00 |  | EASE_DAMPER COND | Damper Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 07:50
10047273 | OTA-WKM-C-0489-0490-Earthwire-A0 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 07:50 | Conductor mostly brown in colour slight pitting observed red.
13329973 | OTA-WKM-C-0489-0490-Earthwire-C0 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-00 |  | EASE_DAMPER COND | Damper Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-22 | CA copied from EW A0 Feb/2026
13329973 | OTA-WKM-C-0489-0490-Earthwire-C0 | OTA-WKM-C0489-0490 | OTA-WKM-C0489-0490-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-22 | Conductor mostly brown in colour slight pitting observed red. CA copied from EW A0 Feb/2026
10046712 | OTA-WKM-C-0490-Tower | OTA-WKM-C0490 | OTA-WKM-C0490-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - Soil/debries/moisture covering foundation.
10046712 | OTA-WKM-C-0490-Tower | OTA-WKM-C0490 | OTA-WKM-C0490-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - Soil/debries/moisture covering foundation.
10046712 | OTA-WKM-C-0490-Tower | OTA-WKM-C0490 | OTA-WKM-C0490-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - Soil/debries/moisture covering foundation.
10046712 | OTA-WKM-C-0490-Tower | OTA-WKM-C0490 | OTA-WKM-C0490-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - Soil/debries/moisture covering foundation.
10046712 | OTA-WKM-C-0490-Tower | OTA-WKM-C0490 | OTA-WKM-C0490-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - Soil/debries/moisture covering foundation.
10046712 | OTA-WKM-C-0490-Tower | OTA-WKM-C0490 | OTA-WKM-C0490-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-11 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046712 | OTA-WKM-C-0490-Tower | OTA-WKM-C0490 | OTA-WKM-C0490-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA - Soil/debries/moisture covering foundation.
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 12:39
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 12:39
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 12:39
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 12:39
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 12:39
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 12:39
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 12:39
10046713 | OTA-WKM-C-0490-Tower Foundation | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 12:39
10046716 | OTA-WKM-C-0490-Earthwire HW Set | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:09 | Heavy corrosion on E/W armour rod
10046716 | OTA-WKM-C-0490-Earthwire HW Set | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:09
12009509 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:51
12009509 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:51
12009509 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 14:51
12009509 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:51
12009510 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | INSE_ARMOUR ROD COND | Armour Rod Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:51
12009510 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | INSE_SUSP COLD END COND | Susp Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:51
12009510 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | INSE_SUSP HOT END COND | Susp Hot End Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 14:51
12009510 | OTA-WKM-C-0490-Insulator Set-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | INSE_SUSP INSULATOR COND | Susp Ins Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:51
13040223 | OTA-WKM-C-0490-Earthwire Attachment | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:58
13040223 | OTA-WKM-C-0490-Earthwire Attachment | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:58 | Wind wear on attachment steel
13040223 | OTA-WKM-C-0490-Earthwire Attachment | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 14:58 | Wind wear on steel
13040223 | OTA-WKM-C-0490-Earthwire Attachment | OTA-WKM-C0490 | OTA-WKM-C0490-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 14:58
13073907 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:03
13073907 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:03 | New attachment installed
13073907 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:03 | New attachment installed
13073907 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0490 | OTA-WKM-C0490-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:03
13073908 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:04
13073908 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:04
13073908 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:04
13073908 | OTA-WKM-C-0490-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0490 | OTA-WKM-C0490-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:04
10047274 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-2 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-20 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 15:12
10047274 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-2 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-20 | 1965 | COSE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-15 15:12
10047274 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-2 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-20 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 15:12
10047274 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-2 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-20 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:12
10047275 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-1 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-15 15:10
10047275 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-1 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-10 | 1965 | COSE_DAMPER COND | Damper Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-15 15:10
10047275 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-1 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-05-10 | CA
10047275 | OTA-WKM-C-0490-0491-Conductor-OHW-OTA-1 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-15 15:10
10047276 | OTA-WKM-C-0490-0491-Earthwire-A0 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-00 |  | EASE_DAMPER COND | Damper Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 15:12
10047276 | OTA-WKM-C-0490-0491-Earthwire-A0 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 15:12
10047276 | OTA-WKM-C-0490-0491-Earthwire-A0 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-00 |  | EASE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-05-10 | CA
13329974 | OTA-WKM-C-0490-0491-Earthwire-C0 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-00 |  | EASE_DAMPER COND | Damper Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 | CA copied from EW A0 Feb/2026
13329974 | OTA-WKM-C-0490-0491-Earthwire-C0 | OTA-WKM-C0490-0491 | OTA-WKM-C0490-0491-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 | CA copied from EW A0 Feb/2026
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_BODY MAJOR PAINT CON | Body Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_BODY MAJOR STEEL CON | Body Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_BODY MINOR PAINT CON | Body Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_BODY MINOR STEEL CON | Body Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_XARM BOLT CONDITION | Crossarm Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_XARM MAJOR PAINT CON | Crossarm Major Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_XARM MAJOR STEEL CON | Crossarm Major Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_XARM MINOR PAINT CON | Crossarm Minor Paint Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_XARM MINOR STEEL CON | Crossarm Minor Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_EARTHING PLATE COND | Earthing Plate Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2023-09-11 | Full Tower refurbishment including both CCTS outage (2 coat MAD system)
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_EWATTACH PNT COND | Earthwire Attach Paint Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-02-09 01:00 | CA
10046717 | OTA-WKM-C-0491-Tower | OTA-WKM-C0491 | OTA-WKM-C0491-00 | 1961 | TOWE_TOWER BOLT CONDITION | Tower Bolt Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA - Insulator attachments rusty. Soil/debries/moisture covering foundation.
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_A_CONDITION | Leg A Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 11:16
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_A_CONNEC_COND | Leg A Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 11:16 | Tower leg paintedno corrosion evident.
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_B_CONDITION | Leg B Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 11:16 | Significant corrosion
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_B_CONNEC_COND | Leg B Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 11:16
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_C_CONDITION | Leg C Condition | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 11:16 | Significant corrosion on steeldug the leg c.
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_C_CONNEC_COND | Leg C Connect Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-15 11:16
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_D_CONDITION | Leg D Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 11:16
10046718 | OTA-WKM-C-0491-Tower Foundation | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | TOFO_LEG_D_CONNEC_COND | Leg D Connect Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-15 11:16 | Tower leg paintedno corrosion evident.
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046719 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 | 2004 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:49
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_ARMOUR ROD COND | Armour Rod Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2011-06-20 | CA - Extra jumper insulators with weights on R phase.
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-14 14:46
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:46
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:46
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2019-08-30
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:46
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2019-08-30
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:46
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:46
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:46
10046720 | OTA-WKM-C-0491-Insulator Set-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 | 2004 | INSE_WEIGHT COND | Weight Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:46
10046721 | OTA-WKM-C-0491-Earthwire HW Set | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 40 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA
10046721 | OTA-WKM-C-0491-Earthwire HW Set | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 16:51 | PRD coded at 40
13040224 | OTA-WKM-C-0491-Earthwire Attachment | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:52
13040224 | OTA-WKM-C-0491-Earthwire Attachment | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:52
13040224 | OTA-WKM-C-0491-Earthwire Attachment | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:52
13040224 | OTA-WKM-C-0491-Earthwire Attachment | OTA-WKM-C0491 | OTA-WKM-C0491-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:52
13073909 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:53
13073909 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:53
13073909 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:53
13073909 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-1 | OTA-WKM-C0491 | OTA-WKM-C0491-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:53
13073910 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:54
13073910 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 14:54
13073910 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-14 14:54
13073910 | OTA-WKM-C-0491-Insulator Attachment-OHW-OTA-2 | OTA-WKM-C0491 | OTA-WKM-C0491-20 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-09-14 14:54
10047281 | OTA-WKM-C-0491-OTAG128-Conductor-OHW-OTA-1 | OTA-WKM-C0491-OTAG128 | OTA-WKM-C0491-OTAG128-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-02-09 01:00 | CA
10047281 | OTA-WKM-C-0491-OTAG128-Conductor-OHW-OTA-1 | OTA-WKM-C0491-OTAG128 | OTA-WKM-C0491-OTAG128-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1999-11-24 | <Not Specified>
10047281 | OTA-WKM-C-0491-OTAG128-Conductor-OHW-OTA-1 | OTA-WKM-C0491-OTAG128 | OTA-WKM-C0491-OTAG128-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2012-10-26 | Birdcaging on B ph at gantry. Special CA for MMS updates following OTA-DIV project., SCDx2 and ERDX1 on gantry CA code 95.
10047281 | OTA-WKM-C-0491-OTAG128-Conductor-OHW-OTA-1 | OTA-WKM-C0491-OTAG128 | OTA-WKM-C0491-OTAG128-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-14 13:51
10047281 | OTA-WKM-C-0491-OTAG128-Conductor-OHW-OTA-1 | OTA-WKM-C0491-OTAG128 | OTA-WKM-C0491-OTAG128-10 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 13:51
10047280 | OTA-WKM-C-0491-OTAG200-Conductor-OHW-OTA-2 | OTA-WKM-C0491-OTAG200 | OTA-WKM-C0491-OTAG200-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-14 13:50
10047280 | OTA-WKM-C-0491-OTAG200-Conductor-OHW-OTA-2 | OTA-WKM-C0491-OTAG200 | OTA-WKM-C0491-OTAG200-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1999-11-24 | <Not Specified>
10047280 | OTA-WKM-C-0491-OTAG200-Conductor-OHW-OTA-2 | OTA-WKM-C0491-OTAG200 | OTA-WKM-C0491-OTAG200-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2011-06-20 | CA
10047280 | OTA-WKM-C-0491-OTAG200-Conductor-OHW-OTA-2 | OTA-WKM-C0491-OTAG200 | OTA-WKM-C0491-OTAG200-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-09-14 13:50
10047280 | OTA-WKM-C-0491-OTAG200-Conductor-OHW-OTA-2 | OTA-WKM-C0491-OTAG200 | OTA-WKM-C0491-OTAG200-10 | 1965 | COSE_SPACER JUMPER COND | Subcond Spcr (Jumper) Condition | 55 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-09-14 13:50
10332759 | OTA-WKM-C-0491-OTAS135-Earthwire | OTA-WKM-C0491-OTAS135 | OTA-WKM-C0491-OTAS135-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-14 14:29
10332759 | OTA-WKM-C-0491-OTAS135-Earthwire | OTA-WKM-C0491-OTAS135 | OTA-WKM-C0491-OTAS135-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-02-09 01:00 | CA
10332764 | OTA-WKM-C-0491-OTAS201-Earthwire | OTA-WKM-C0491-OTAS201 | OTA-WKM-C0491-OTAS201-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-09-14 14:29
10332764 | OTA-WKM-C-0491-OTAS201-Earthwire | OTA-WKM-C0491-OTAS201 | OTA-WKM-C0491-OTAS201-00 |  | EASE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-02-09 01:00 | CA
10281379 | OTA-WKM-C-OHWG17-Insulator Set-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 | 2008 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:57
10281379 | OTA-WKM-C-OHWG17-Insulator Set-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 | 2008 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:57
10281379 | OTA-WKM-C-OHWG17-Insulator Set-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 | 2008 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:57
10281379 | OTA-WKM-C-OHWG17-Insulator Set-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 | 2008 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-26 | New fitted for OHW substation by ELX
10281379 | OTA-WKM-C-OHWG17-Insulator Set-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 | 2008 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-26 | New fitted for OHW substation by ELX
10281379 | OTA-WKM-C-OHWG17-Insulator Set-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 | 2008 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-26 | New fitted for OHW substation by ELX
13031577 | OTA-WKM-C-OHWG17-Insulator Attachment-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:59
13031577 | OTA-WKM-C-OHWG17-Insulator Attachment-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:59
13031577 | OTA-WKM-C-OHWG17-Insulator Attachment-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:59
13031577 | OTA-WKM-C-OHWG17-Insulator Attachment-OHW-WKM-1 | OTA-WKM-COHWG17 | OTA-WKM-COHWG17-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:59
10281381 | OTA-WKM-C-OHWG2-Insulator Set-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 | 2008 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-26 | New fitted for OHW sub by ELX
10281381 | OTA-WKM-C-OHWG2-Insulator Set-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 | 2008 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-26 | New fitted for OHW sub by ELX
10281381 | OTA-WKM-C-OHWG2-Insulator Set-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 | 2008 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-26 | New fitted for OHW sub by ELX
10281381 | OTA-WKM-C-OHWG2-Insulator Set-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 | 2008 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:38
10281381 | OTA-WKM-C-OHWG2-Insulator Set-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 | 2008 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:38
10281381 | OTA-WKM-C-OHWG2-Insulator Set-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 | 2008 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:38
13031578 | OTA-WKM-C-OHWG2-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:37
13031578 | OTA-WKM-C-OHWG2-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:37
13031578 | OTA-WKM-C-OHWG2-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:37
13031578 | OTA-WKM-C-OHWG2-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COHWG2 | OTA-WKM-COHWG2-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:37
10281407 | OTA-WKM-C-OHWG2-0305A-Conductor-OHW-OTA-1 | OTA-WKM-COHWG2-0305A | OTA-WKM-COHWG2-0305A-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:36
10281407 | OTA-WKM-C-OHWG2-0305A-Conductor-OHW-OTA-1 | OTA-WKM-COHWG2-0305A | OTA-WKM-COHWG2-0305A-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-26 | Wired the existing conductor into OHW sub - ELX
10281407 | OTA-WKM-C-OHWG2-0305A-Conductor-OHW-OTA-1 | OTA-WKM-COHWG2-0305A | OTA-WKM-COHWG2-0305A-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:36
10281380 | OTA-WKM-C-OHWG3-Insulator Set-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 | 2008 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-14 | New insulators fitted to new gantry at sub by ELX on 13/11/08
10281380 | OTA-WKM-C-OHWG3-Insulator Set-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 | 2008 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-14 | New insulators fitted to new gantry at sub by ELX on 13/11/08
10281380 | OTA-WKM-C-OHWG3-Insulator Set-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 | 2008 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-14 | New insulators fitted to new gantry at sub by ELX on 13/11/08
10281380 | OTA-WKM-C-OHWG3-Insulator Set-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 | 2008 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:29
10281380 | OTA-WKM-C-OHWG3-Insulator Set-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 | 2008 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:29
10281380 | OTA-WKM-C-OHWG3-Insulator Set-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 | 2008 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:29
13031579 | OTA-WKM-C-OHWG3-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:27
13031579 | OTA-WKM-C-OHWG3-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:27
13031579 | OTA-WKM-C-OHWG3-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:27
13031579 | OTA-WKM-C-OHWG3-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COHWG3 | OTA-WKM-COHWG3-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:27
10281408 | OTA-WKM-C-OHWG3-0305A-Conductor-OHW-OTA-2 | OTA-WKM-COHWG3-0305A | OTA-WKM-COHWG3-0305A-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:27
10281408 | OTA-WKM-C-OHWG3-0305A-Conductor-OHW-OTA-2 | OTA-WKM-COHWG3-0305A | OTA-WKM-COHWG3-0305A-10 | 1965 | COSE_JOINT (IN SPAN) COND | Joint (In Span) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-14 | Span wired into the OHW substation by ELX 13/06/08
10281408 | OTA-WKM-C-OHWG3-0305A-Conductor-OHW-OTA-2 | OTA-WKM-COHWG3-0305A | OTA-WKM-COHWG3-0305A-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-14 | Span wired into the OHW substation by ELX 13/06/08
10281408 | OTA-WKM-C-OHWG3-0305A-Conductor-OHW-OTA-2 | OTA-WKM-COHWG3-0305A | OTA-WKM-COHWG3-0305A-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:27
10281385 | OTA-WKM-C-OHWS17-Earthwire HW Set | OTA-WKM-COHWS17 | OTA-WKM-COHWS17-00 | 2008 | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 16:55
13030956 | OTA-WKM-C-OHWS17-Earthwire Attachment | OTA-WKM-COHWS17 | OTA-WKM-COHWS17-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:55
13030956 | OTA-WKM-C-OHWS17-Earthwire Attachment | OTA-WKM-COHWS17 | OTA-WKM-COHWS17-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:55
13030956 | OTA-WKM-C-OHWS17-Earthwire Attachment | OTA-WKM-COHWS17 | OTA-WKM-COHWS17-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:55
13030956 | OTA-WKM-C-OHWS17-Earthwire Attachment | OTA-WKM-COHWS17 | OTA-WKM-COHWS17-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:55
10307559 | OTA-WKM-C-OHWS18-Earthwire HW Set | OTA-WKM-COHWS18 | OTA-WKM-COHWS18-00 | 2008 | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:41
13030957 | OTA-WKM-C-OHWS18-Earthwire Attachment | OTA-WKM-COHWS18 | OTA-WKM-COHWS18-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:41
13030957 | OTA-WKM-C-OHWS18-Earthwire Attachment | OTA-WKM-COHWS18 | OTA-WKM-COHWS18-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:41
13030957 | OTA-WKM-C-OHWS18-Earthwire Attachment | OTA-WKM-COHWS18 | OTA-WKM-COHWS18-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:41
13030957 | OTA-WKM-C-OHWS18-Earthwire Attachment | OTA-WKM-COHWS18 | OTA-WKM-COHWS18-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:41
10307560 | OTA-WKM-C-OHWS2-Earthwire HW Set | OTA-WKM-COHWS2 | OTA-WKM-COHWS2-00 | 2008 | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:11
13030958 | OTA-WKM-C-OHWS2-Earthwire Attachment | OTA-WKM-COHWS2 | OTA-WKM-COHWS2-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:16
13030958 | OTA-WKM-C-OHWS2-Earthwire Attachment | OTA-WKM-COHWS2 | OTA-WKM-COHWS2-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:16
13030958 | OTA-WKM-C-OHWS2-Earthwire Attachment | OTA-WKM-COHWS2 | OTA-WKM-COHWS2-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:16
13030958 | OTA-WKM-C-OHWS2-Earthwire Attachment | OTA-WKM-COHWS2 | OTA-WKM-COHWS2-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:16
10281444 | OTA-WKM-C-OHWS2-0305A-Earthwire | OTA-WKM-COHWS2-0305A | OTA-WKM-COHWS2-0305A-00 | 2008 | EASE_DAMPER COND | Damper Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-14 | Data added
10281444 | OTA-WKM-C-OHWS2-0305A-Earthwire | OTA-WKM-COHWS2-0305A | OTA-WKM-COHWS2-0305A-00 | 2008 | EASE_EARTHWIRE CONDITION | Earthwire Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-09 14:51
10281444 | OTA-WKM-C-OHWS2-0305A-Earthwire | OTA-WKM-COHWS2-0305A | OTA-WKM-COHWS2-0305A-00 | 2008 | EASE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-10-19 01:00 | CA
10307561 | OTA-WKM-C-OHWS4-Earthwire HW Set | OTA-WKM-COHWS4 | OTA-WKM-COHWS4-00 | 2008 | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:18
13030959 | OTA-WKM-C-OHWS4-Earthwire Attachment | OTA-WKM-COHWS4 | OTA-WKM-COHWS4-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:18
13030959 | OTA-WKM-C-OHWS4-Earthwire Attachment | OTA-WKM-COHWS4 | OTA-WKM-COHWS4-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:18
13030959 | OTA-WKM-C-OHWS4-Earthwire Attachment | OTA-WKM-COHWS4 | OTA-WKM-COHWS4-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 16:18
13030959 | OTA-WKM-C-OHWS4-Earthwire Attachment | OTA-WKM-COHWS4 | OTA-WKM-COHWS4-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:18
10307553 | OTA-WKM-C-OHWS4-0305A-Earthwire | OTA-WKM-COHWS4-0305A | OTA-WKM-COHWS4-0305A-00 | 2008 | EASE_DAMPER COND | Damper Condition | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2008-06-14 | New data added
10307553 | OTA-WKM-C-OHWS4-0305A-Earthwire | OTA-WKM-COHWS4-0305A | OTA-WKM-COHWS4-0305A-00 | 2008 | EASE_EARTHWIRE CONDITION | Earthwire Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 16:19
10307553 | OTA-WKM-C-OHWS4-0305A-Earthwire | OTA-WKM-COHWS4-0305A | OTA-WKM-COHWS4-0305A-00 | 2008 | EASE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2015-10-19 01:00 | CA
10332756 | OTA-WKM-C-OTAG128-Insulator Set-OHW-OTA-1 | OTA-WKM-COTAG128 | OTA-WKM-COTAG128-10 | 2007 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 09:44
10332756 | OTA-WKM-C-OTAG128-Insulator Set-OHW-OTA-1 | OTA-WKM-COTAG128 | OTA-WKM-COTAG128-10 | 2007 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2022-12-07 09:44
10332756 | OTA-WKM-C-OTAG128-Insulator Set-OHW-OTA-1 | OTA-WKM-COTAG128 | OTA-WKM-COTAG128-10 | 2007 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 09:44
13031580 | OTA-WKM-C-OTAG128-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COTAG128 | OTA-WKM-COTAG128-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 09:46
13031580 | OTA-WKM-C-OTAG128-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COTAG128 | OTA-WKM-COTAG128-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 09:46
13031580 | OTA-WKM-C-OTAG128-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COTAG128 | OTA-WKM-COTAG128-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2022-12-07 09:46
13031580 | OTA-WKM-C-OTAG128-Insulator Attachment-OHW-OTA-1 | OTA-WKM-COTAG128 | OTA-WKM-COTAG128-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2015-07-18 | Updating to 4 Readings
10332761 | OTA-WKM-C-OTAG200-Insulator Set-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 | 1965 | INSE_JUMPER COLD END COND | Jumper Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:13
10332761 | OTA-WKM-C-OTAG200-Insulator Set-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 | 1965 | INSE_JUMPER HOT END COND | Jumper Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:13
10332761 | OTA-WKM-C-OTAG200-Insulator Set-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 | 1965 | INSE_JUMPER INSULATOR CON | Jumper Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:13
10332761 | OTA-WKM-C-OTAG200-Insulator Set-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 | 1965 | INSE_STRAIN BACK COLD END | Strain Back Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:13
10332761 | OTA-WKM-C-OTAG200-Insulator Set-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 | 1965 | INSE_STRAIN BACK HOT END | Strain Back Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:13
10332761 | OTA-WKM-C-OTAG200-Insulator Set-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 | 1965 | INSE_STRAIN BACK INSULATO | Strain Back Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:13
13031581 | OTA-WKM-C-OTAG200-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 09:09
13031581 | OTA-WKM-C-OTAG200-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-07-18 | Updating to 4 Readings
13031581 | OTA-WKM-C-OTAG200-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 09:09
13031581 | OTA-WKM-C-OTAG200-Insulator Attachment-OHW-OTA-2 | OTA-WKM-COTAG200 | OTA-WKM-COTAG200-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 09:09
10332758 | OTA-WKM-C-OTAS135-Earthwire HW Set | OTA-WKM-COTAS135 | OTA-WKM-COTAS135-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:29
13030960 | OTA-WKM-C-OTAS135-Earthwire Attachment | OTA-WKM-COTAS135 | OTA-WKM-COTAS135-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:28
13030960 | OTA-WKM-C-OTAS135-Earthwire Attachment | OTA-WKM-COTAS135 | OTA-WKM-COTAS135-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:28
13030960 | OTA-WKM-C-OTAS135-Earthwire Attachment | OTA-WKM-COTAS135 | OTA-WKM-COTAS135-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:28
13030960 | OTA-WKM-C-OTAS135-Earthwire Attachment | OTA-WKM-COTAS135 | OTA-WKM-COTAS135-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2015-07-18 | Updating to 4 Readings
10332763 | OTA-WKM-C-OTAS201-Earthwire HW Set | OTA-WKM-COTAS201 | OTA-WKM-COTAS201-00 |  | EHWC_ARMOUR ROD COND | Armour Rod Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:02 | Rating is for preform dead end grip
10332763 | OTA-WKM-C-OTAS201-Earthwire HW Set | OTA-WKM-COTAS201 | OTA-WKM-COTAS201-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 09:02
13030961 | OTA-WKM-C-OTAS201-Earthwire Attachment | OTA-WKM-COTAS201 | OTA-WKM-COTAS201-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:00
13030961 | OTA-WKM-C-OTAS201-Earthwire Attachment | OTA-WKM-COTAS201 | OTA-WKM-COTAS201-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2015-07-18 | Updating to 4 Readings
13030961 | OTA-WKM-C-OTAS201-Earthwire Attachment | OTA-WKM-COTAS201 | OTA-WKM-COTAS201-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2022-12-07 09:00
13030961 | OTA-WKM-C-OTAS201-Earthwire Attachment | OTA-WKM-COTAS201 | OTA-WKM-COTAS201-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2022-12-07 09:00
10043347 | OTA-WKM-C-WKMG5-Insulator Set-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 | 1965 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 08:49
10043347 | OTA-WKM-C-WKMG5-Insulator Set-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 | 1965 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 08:49
10043347 | OTA-WKM-C-WKMG5-Insulator Set-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 | 1965 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 08:49
10043347 | OTA-WKM-C-WKMG5-Insulator Set-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 | 1965 | INSE_SUSP COLD END COND | Susp Cold End Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2006-06-20 | CA-Special Substation Condition Assessment JUN 06. Yphase 5th unit missing.
10043347 | OTA-WKM-C-WKMG5-Insulator Set-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 | 1965 | INSE_SUSP HOT END COND | Susp Hot End Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2006-06-20 | CA-Special Substation Condition Assessment JUN 06. Yphase 5th unit missing.
10043347 | OTA-WKM-C-WKMG5-Insulator Set-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 | 1965 | INSE_SUSP INSULATOR COND | Susp Ins Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2006-06-20 | CA-Special Substation Condition Assessment JUN 06. Yphase 5th unit missing.
13031582 | OTA-WKM-C-WKMG5-Insulator Attachment-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 08:56
13031582 | OTA-WKM-C-WKMG5-Insulator Attachment-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 08:56
13031582 | OTA-WKM-C-WKMG5-Insulator Attachment-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 08:56
13031582 | OTA-WKM-C-WKMG5-Insulator Attachment-HAM-WKM-1 | OTA-WKM-CWKMG5 | OTA-WKM-CWKMG5-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 08:56
10043350 | OTA-WKM-C-WKMG5-0001-Conductor-HAM-WKM-1 | OTA-WKM-CWKMG5-0001 | OTA-WKM-CWKMG5-0001-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2024-06-05 08:57
10043350 | OTA-WKM-C-WKMG5-0001-Conductor-HAM-WKM-1 | OTA-WKM-CWKMG5-0001 | OTA-WKM-CWKMG5-0001-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2011-03-27 | WKM WMOF joint replaced and all jumper palms refurbished
10043350 | OTA-WKM-C-WKMG5-0001-Conductor-HAM-WKM-1 | OTA-WKM-CWKMG5-0001 | OTA-WKM-CWKMG5-0001-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 08:57
10043346 | OTA-WKM-C-WKMG57-Insulator Set-OHW-WKM-1 | OTA-WKM-CWKMG57 | OTA-WKM-CWKMG57-10 | 1965 | INSE_STRAIN FORWARD COLD | Strain Fwd Cold End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 09:01
10043346 | OTA-WKM-C-WKMG57-Insulator Set-OHW-WKM-1 | OTA-WKM-CWKMG57 | OTA-WKM-CWKMG57-10 | 1965 | INSE_STRAIN FORWARD HOT | Strain Fwd Hot End Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 09:01
10043346 | OTA-WKM-C-WKMG57-Insulator Set-OHW-WKM-1 | OTA-WKM-CWKMG57 | OTA-WKM-CWKMG57-10 | 1965 | INSE_STRAIN FORWARD INSUL | Strain Fwd Ins Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:01
13031583 | OTA-WKM-C-WKMG57-Insulator Attachment-OHW-WKM-1 | OTA-WKM-CWKMG57 | OTA-WKM-CWKMG57-10 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 09:02
13031583 | OTA-WKM-C-WKMG57-Insulator Attachment-OHW-WKM-1 | OTA-WKM-CWKMG57 | OTA-WKM-CWKMG57-10 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 09:02
13031583 | OTA-WKM-C-WKMG57-Insulator Attachment-OHW-WKM-1 | OTA-WKM-CWKMG57 | OTA-WKM-CWKMG57-10 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 09:02
13031583 | OTA-WKM-C-WKMG57-Insulator Attachment-OHW-WKM-1 | OTA-WKM-CWKMG57 | OTA-WKM-CWKMG57-10 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 09:02
10043349 | OTA-WKM-C-WKMG57-0001-Conductor-OHW-WKM-1 | OTA-WKM-CWKMG57-0001 | OTA-WKM-CWKMG57-0001-10 | 1965 | COSE_CONDUCTOR CONDITION | Conductor Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:06
10043349 | OTA-WKM-C-WKMG57-0001-Conductor-OHW-WKM-1 | OTA-WKM-CWKMG57-0001 | OTA-WKM-CWKMG57-0001-10 | 1965 | COSE_JOINT (TERM) COND | Joint (Term) Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2010-10-09 | WKM ELIF, WKM ELOF joints replaced and all jumper palms replaced.
10043349 | OTA-WKM-C-WKMG57-0001-Conductor-OHW-WKM-1 | OTA-WKM-CWKMG57-0001 | OTA-WKM-CWKMG57-0001-10 | 1965 | COSE_SUB COND SPACER | Subcond Spacer Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:06
10304395 | OTA-WKM-C-WKMS10-Earthwire HW Set | OTA-WKM-CWKMS10 | OTA-WKM-CWKMS10-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:11
13030962 | OTA-WKM-C-WKMS10-Earthwire Attachment | OTA-WKM-CWKMS10 | OTA-WKM-CWKMS10-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:08
13030962 | OTA-WKM-C-WKMS10-Earthwire Attachment | OTA-WKM-CWKMS10 | OTA-WKM-CWKMS10-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:08
13030962 | OTA-WKM-C-WKMS10-Earthwire Attachment | OTA-WKM-CWKMS10 | OTA-WKM-CWKMS10-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:08
13030962 | OTA-WKM-C-WKMS10-Earthwire Attachment | OTA-WKM-CWKMS10 | OTA-WKM-CWKMS10-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:08
10304398 | OTA-WKM-C-WKMS10-0001-Earthwire | OTA-WKM-CWKMS10-0001 | OTA-WKM-CWKMS10-0001-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:11
10304396 | OTA-WKM-C-WKMS58-Earthwire HW Set | OTA-WKM-CWKMS58 | OTA-WKM-CWKMS58-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:20 | Surface roughening is ca70
13030963 | OTA-WKM-C-WKMS58-Earthwire Attachment | OTA-WKM-CWKMS58 | OTA-WKM-CWKMS58-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:18
13030963 | OTA-WKM-C-WKMS58-Earthwire Attachment | OTA-WKM-CWKMS58 | OTA-WKM-CWKMS58-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:18
13030963 | OTA-WKM-C-WKMS58-Earthwire Attachment | OTA-WKM-CWKMS58 | OTA-WKM-CWKMS58-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:18
13030963 | OTA-WKM-C-WKMS58-Earthwire Attachment | OTA-WKM-CWKMS58 | OTA-WKM-CWKMS58-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:18
10304399 | OTA-WKM-C-WKMS58-0001-Earthwire | OTA-WKM-CWKMS58-0001 | OTA-WKM-CWKMS58-0001-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:20
10304397 | OTA-WKM-C-WKMS59-Earthwire HW Set | OTA-WKM-CWKMS59 | OTA-WKM-CWKMS59-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:24 | Surface roughning
13247448 | OTA-WKM-C-WKMS59-Earthwire Attachment | OTA-WKM-CWKMS59 | OTA-WKM-CWKMS59-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:23
13247448 | OTA-WKM-C-WKMS59-Earthwire Attachment | OTA-WKM-CWKMS59 | OTA-WKM-CWKMS59-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 60 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 2024-06-05 09:23
13247448 | OTA-WKM-C-WKMS59-Earthwire Attachment | OTA-WKM-CWKMS59 | OTA-WKM-CWKMS59-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:23
13247448 | OTA-WKM-C-WKMS59-Earthwire Attachment | OTA-WKM-CWKMS59 | OTA-WKM-CWKMS59-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:23
10304400 | OTA-WKM-C-WKMS59-0001-Earthwire | OTA-WKM-CWKMS59-0001 | OTA-WKM-CWKMS59-0001-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:24
10043348 | OTA-WKM-C-WKMS9-Earthwire HW Set | OTA-WKM-CWKMS9 | OTA-WKM-CWKMS9-00 |  | EHWC_HARDWARE CONDITION | Earthwire Hardware Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:31
13226999 | OTA-WKM-C-WKMS9-Earthwire Attachment | OTA-WKM-CWKMS9 | OTA-WKM-CWKMS9-00 |  | ATCA_POINT_CONDITION | Attachment Point Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:31
13226999 | OTA-WKM-C-WKMS9-Earthwire Attachment | OTA-WKM-CWKMS9 | OTA-WKM-CWKMS9-00 |  | ATCA_NUT_BOLT_CONDITION | Attachment Point Nuts and Bolt Condition | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:31
13226999 | OTA-WKM-C-WKMS9-Earthwire Attachment | OTA-WKM-CWKMS9 | OTA-WKM-CWKMS9-00 |  | ATCA_STEEL_CONDITION | Attachment Point Steel Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:31
13226999 | OTA-WKM-C-WKMS9-Earthwire Attachment | OTA-WKM-CWKMS9 | OTA-WKM-CWKMS9-00 |  | ATCA_THROUGH_CONDITION | Attachment Point Through Bolt and Nut Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:31
10043351 | OTA-WKM-C-WKMS9-0001-Earthwire | OTA-WKM-CWKMS9-0001 | OTA-WKM-CWKMS9-0001-00 |  | EASE_EARTHWIRE CONDITION | Earthwire Condition | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 2024-06-05 09:33
Applied filters: Current Reading is Y Meter Name is TOWE_EARTHING PLATE COND, TOWE_XARM BOLT CONDITION, TOWE_XARM MAJOR PAINT CON, TOWE_XARM MAJOR STEEL CON, TOWE_XARM MINOR PAINT CON, TOWE_XARM MINOR STEEL CON, ATCA_NUT_BOLT_CONDITION, ATCA_POINT_CONDITION, ATCA_STEEL_CONDITION, TOWE_BODY MAJOR PAINT CON, TOWE_BODY MAJOR STEEL CON, TOWE_BODY MINOR PAINT CON, TOWE_BODY MINOR STEEL CON, TOWE_EWATTACH PNT COND, TOWE_TOWER BOLT CONDITION, TOFO_LEG_A_CONDITION, TOFO_LEG_A_CONNEC_COND, TOFO_LEG_B_CONDITION, TOFO_LEG_B_CONNEC_COND, TOFO_LEG_C_CONDITION, TOFO_LEG_C_CONNEC_COND, TOFO_LEG_D_CONDITION, POST_ACC_ATTACH_COND1, POST_COND_ATTACHMENT_COND, POST_CROSSARM_CONDITION, POST_EARTH_PEAK_COND, POST_EARTHING_CONDITION, POST_EARTHWIRE ATTACH CON, POST_EXTERNAL_GUY_COND, POST_INTERNAL_GUY_COND, POST_LEFT_POLE_COND, POST_LEFT_POLE_GL_DIA, POST_LIGHTNING_ARRES_COND, POST_MIDDLE_POLE_COND, POST_MIDDLE_POLE_GL_DIA, POST_RIGHT_POLE_COND, COSE_CONDUCTOR CONDITION, COSE_DAMPER COND, COSE_INTERPHASE SPACER CO, COSE_JOINT (IN SPAN) COND, COSE_JOINT (TERM) COND, COSE_MAR_BAL_COND, COSE_REPAIR ROD COND, COSE_REPAIR SLEEVE COND, COSE_SPACER JUMPER COND, COSE_SUB COND SPACER, EASE_DAMPER COND, EASE_EARTHWIRE CONDITION, EASE_JOINT (IN SPAN) COND, EASE_JOINT (TERM) COND, EASE_MAR_BAL_COND, EHWC_ARMOUR ROD COND, EHWC_HARDWARE CONDITION, INSE_ARMOUR ROD COND, INSE_ARRESTOR COND, INSE_JUMPER COLD END COND, INSE_JUMPER HOT END COND, INSE_JUMPER INSULATOR CON, INSE_STRAIN BACK COLD END, INSE_STRAIN BACK HOT END, INSE_STRAIN BACK INSULATO, INSE_STRAIN FORWARD COLD, INSE_STRAIN FORWARD HOT, INSE_STRAIN FORWARD INSUL, INSE_SUSP COLD END COND, INSE_SUSP HOT END COND, INSE_SUSP INSULATOR COND, INSE_WEIGHT COND, FOSE_DAMPER COND, FOSE_MAR_BAL_COND, FOSE_OPTIC WIRE CONDITION, POST_RIGHT_POLE_GL_DIA, TOFO_LEG_D_CONNEC_COND, or ATCA_THROUGH_CONDITION Asset Status is COMMISSIONED, INSTALLED, or NOT READY SITE_DESC is Otahuhu - Whakamaru C SITE is OTA-WKM-C

## Sheet1
Armour Rod Condition
Attachment Point Condition
Attachment Point Nuts and Bolt Condition
Attachment Point Steel Condition
Attachment Point Through Bolt and Nut Condition
Body Major Paint Condition
Body Major Steel Condition
Body Minor Paint Condition
Body Minor Steel Condition
Conductor Condition
Crossarm Bolt Condition
Crossarm Major Paint Condition
Crossarm Major Steel Condition
Crossarm Minor Paint Condition
Crossarm Minor Steel Condition
Damper Condition
Earthing Plate Condition
Earthwire Attach Paint Condition
Earthwire Condition
Earthwire Hardware Condition
Interphase Spcr Condition
Joint (In Span) Condition
Joint (Term) Condition
Jumper Cold End Condition
Jumper Hot End Condition
Jumper Ins Condition
Leg A Condition
Leg A Connect Condition
Leg B Condition
Leg B Connect Condition
Leg C Condition
Leg C Connect Condition
Leg D Condition
Leg D Connect Condition
Meter Description
Repair Rod Condition
Repair Sleeve Condition
Strain Back Cold End Condition
Strain Back Hot End Condition
Strain Back Ins Condition
Strain Fwd Cold End Condition
Strain Fwd Hot End Condition
Strain Fwd Ins Condition
Subcond Spacer Condition
Subcond Spcr (Jumper) Condition
Susp Cold End Condition
Susp Hot End Condition
Susp Ins Condition
Tower Bolt Condition
Weight Condition
0