## Index
User: | Igor.Bertyaev
Project: | f1818b_bri-bun_red-bun
Date: | 8/07/2025
Tabs Index:
Tab_1 | Structure Locations and Usage Report
Tab_2 | Multiple Structure Suspension Insulator Swing Angles and V-String Load Angles
Tab_3 | Multiple Structure Minimum Vertical Load (Uplift) Summary
Tab_4 | Summary of Maximum Usages by Load Case for Structure Range
Tab_5 | Summary of Tip Deflections For All Load Cases for Structure Range
Tab_6 | Foundation Design Forces For All Load Cases for Structure Range
Tab_7 | Summary of Joint Support Reactions For All Load Cases for Structure Range
Tab_8 | Loads At Insulator Attachments For All Load Cases for Structure Range
Tab_9 | Summary of Maximum Element Usages for Structure Range

## Tab_1
rowtext | structure_number | structure_name | station | x | y | z | line_angle | constraints_prohib_zone | constraints_req_pos | constraints_extra_cost | structure_strength_usage | insulator_swing_usage | minimum_required_vertical_load_uplift | pole_tip_deflection_usage | analysis_type | ok_or_ng
1 | 281A | 724.350 _197_310_118.700.#281a-UI | 0.00 | 246180.19 | 6290477.37 | 103.64 | 0.00 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
2 | 282 | 76.8.20.#282 | 210.99 | 246124.84 | 6290680.97 | 102.42 | -0.02 |  |  | 0 | 200.0 | 50.6 | OK | 0.0 |  | NG
3 | 283 | r75.12.25 EW Mod | 479.39 | 246054.32 | 6290939.94 | 102.48 | -0.05 |  |  | 0 | 200.0 | 53.0 | OK | 0.0 |  | NG
4 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 762.85 | 245979.63 | 6291213.38 | 102.82 | 0.00 |  |  | 0 | 64.8 | 49.2 | OK | 0.0 | Nonlinear | OK
5 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 1063.35 | 245900.59 | 6291503.30 | 103.88 | 0.00 |  |  | 0 | 65.6 | 49.3 | OK | 0.0 | Nonlinear | OK
6 | 286 | 75.8.20 EW Mod | 1337.49 | 245828.29 | 6291767.74 | 105.21 | 0.05 |  |  | 0 | 200.0 | 51.6 | OK | 0.0 |  | NG
7 | 287 | 76.8.20.#287 | 1632.69 | 245750.68 | 6292052.55 | 105.65 | -0.01 |  |  | 0 | 200.0 | 45.8 | OK | 0.0 |  | NG
8 | 287A | wa1860 EW Mod | 1779.63 | 245712.03 | 6292194.32 | 106.23 | 0.02 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
9 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 1990.98 | 245656.50 | 6292398.24 | 106.72 | 0.00 |  |  | 0 | 59.0 | 47.9 | OK | 0.0 | Nonlinear | OK
10 | 289 | r75.12.25 EW Mod1 | 2237.10 | 245591.79 | 6292635.70 | 108.72 | 0.00 |  |  | 0 | 200.0 | 52.0 | OK | 0.0 |  | NG
11 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 2498.32 | 245523.12 | 6292887.73 | 108.11 | 0.00 |  |  | 0 | 69.0 | 54.5 | OK | 0.0 | Nonlinear | OK
12 | 291 | 76.8.20 EW Mod | 2768.67 | 245446.22 | 6293146.91 | 109.36 | -0.03 |  |  | 0 | 200.0 | 52.8 | OK | 0.0 |  | NG
13 | 292 | 76.8.20.#292 | 3013.21 | 245375.75 | 6293381.07 | 110.35 | 0.02 |  |  | 0 | 200.0 | 48.8 | OK | 0.0 |  | NG
14 | 293 | 76.8.20.#293-UI | 3253.55 | 245306.56 | 6293611.24 | 109.55 | -0.03 |  |  | 0 | 200.0 | 48.3 | OK | 0.0 |  | NG
15 | 294 | wa2340.#294-UI | 3525.50 | 245228.13 | 6293871.63 | 107.45 | -5.94 |  |  | 0 | 200.0 | 67.1 | OK | 0.0 |  | NG
16 | 295 | 75.9.24.#295-UI | 3707.58 | 245157.87 | 6294039.61 | 107.43 | -1.01 |  |  | 0 | 200.0 | 50.8 | OK | 0.0 |  | NG
17 | 296 | 75.8.20.#296 | 3974.71 | 245050.45 | 6294284.19 | 106.66 | 0.03 |  |  | 0 | 200.0 | 54.1 | OK | 0.0 |  | NG
18 | 297 | 75.8.20_mod.#297 | 4240.22 | 244943.81 | 6294527.35 | 106.86 | 2.32 |  |  | 0 | 200.0 | 56.6 | OK | 0.0 |  | NG
19 | 298 | 75.8.20.#298 | 4495.93 | 244850.67 | 6294765.49 | 106.69 | -0.03 |  |  | 0 | 200.0 | 52.9 | OK | 0.0 |  | NG
20 | 299 | 75.8.20.#299 | 4751.38 | 244757.50 | 6295003.34 | 105.17 | -0.04 |  |  | 0 | 200.0 | 51.4 | OK | 0.0 |  | NG
21 | 300 | 75.8.24.#300 | 5012.28 | 244662.19 | 6295246.21 | 104.88 | -10.27 |  |  | 0 | 200.0 | 70.5 | OK | 0.0 |  | NG
22 | 301 | r75.12.25.#301 | 5269.72 | 244526.91 | 6295465.24 | 103.06 | -0.01 |  |  | 0 | 200.0 | 46.1 | OK | 0.0 |  | NG
23 | 301A | wa1860.#301a-UI | 5418.48 | 244448.72 | 6295591.80 | 102.20 | 0.05 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
24 | 302 | 75.8.20 EW Mod 5 | 5565.47 | 244371.57 | 6295716.91 | 101.77 | -0.00 |  |  | 0 | 200.0 | 46.7 | OK | 0.0 |  | NG
25 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5851.06 | 244221.65 | 6295959.99 | 100.69 | 0.00 |  |  | 0 | 70.6 | 51.1 | OK | 0.0 | Nonlinear | OK
26 | 304A | WB8025 Updated Crossarm NO EP.POL | 6151.77 | 244063.87 | 6296215.98 | 101.22 | 0.00 |  |  | 0 | 63.7 | 46.7 | OK | 0.0 | Nonlinear | OK
27 | 305 | 75.8.20 EW Mod3 | 6452.20 | 243906.08 | 6296471.63 | 100.98 | 0.03 |  |  | 0 | 200.0 | 53.0 | OK | 0.0 |  | NG
28 | 306 | 75.8.20.#306 | 6747.64 | 243751.02 | 6296723.11 | 101.22 | -0.00 |  |  | 0 | 200.0 | 50.9 | OK | 0.0 |  | NG
29 | 307 | 75.8.20.#307 | 7043.09 | 243595.94 | 6296974.59 | 101.51 | 0.02 |  |  | 0 | 200.0 | 50.9 | OK | 0.0 |  | NG
30 | 308 | r75.12.25.#308 | 7341.29 | 243439.50 | 6297228.46 | 100.85 | -0.02 |  |  | 0 | 200.0 | 50.7 | OK | 0.0 |  | NG
31 | 309 | 75.8.20.#309 | 7637.27 | 243284.15 | 6297480.39 | 100.66 | -0.29 |  |  | 0 | 200.0 | 53.0 | OK | 0.0 |  | NG
32 | 310 | 75.8.20.#310 | 7852.39 | 243170.30 | 6297662.92 | 101.00 | 0.01 |  |  | 0 | 200.0 | 49.2 | OK | 0.0 |  | NG
33 | 311 | 75.8.20.#311 | 8067.04 | 243056.73 | 6297845.06 | 100.09 | -0.03 |  |  | 0 | 200.0 | 48.8 | OK | 0.0 |  | NG
34 | 312 | 75.8.20.#312 | 8281.78 | 242943.02 | 6298027.22 | 98.18 | -0.87 |  |  | 0 | 200.0 | 53.3 | OK | 0.0 |  | NG
35 | 313 | 75.8.20.#313 | 8577.26 | 242782.78 | 6298275.48 | 95.67 | 0.04 |  |  | 0 | 200.0 | 50.3 | OK | 0.0 |  | NG
36 | 314 | 75.8.20.#314 | 8873.00 | 242622.59 | 6298524.08 | 93.57 | -0.03 |  |  | 0 | 200.0 | 50.4 | OK | 0.0 |  | NG
37 | 315 | 75.8.20.#315 | 9168.70 | 242462.28 | 6298772.55 | 91.40 | 0.03 |  |  | 0 | 200.0 | 51.8 | OK | 0.0 |  | NG
38 | 316 | r75.12.25.#316 | 9449.17 | 242310.36 | 6299008.32 | 91.45 | -0.03 |  |  | 0 | 200.0 | 49.3 | OK | 0.0 |  | NG
39 | 317 | 75.8.20.#317 | 9745.04 | 242149.99 | 6299256.95 | 90.16 | 0.06 |  |  | 0 | 200.0 | 50.0 | OK | 0.0 |  | NG
40 | 318 | 75.8.20.#318 | 10041.31 | 241989.66 | 6299506.09 | 88.34 | -0.06 |  |  | 0 | 200.0 | 50.9 | OK | 0.0 |  | NG
41 | 319 | 75.8.20.#319 | 10338.38 | 241828.64 | 6299755.74 | 87.44 | 0.05 |  |  | 0 | 200.0 | 51.4 | OK | 0.0 |  | NG
42 | 320 | 75.8.20.#320 | 10633.80 | 241668.73 | 6300004.14 | 88.24 | -0.01 |  |  | 0 | 200.0 | 49.6 | OK | 0.0 |  | NG
43 | 321 | r75.12.25.#321 | 10929.35 | 241508.69 | 6300252.60 | 88.18 | 0.05 |  |  | 0 | 200.0 | 45.9 | OK | 0.0 |  | NG
44 | 321A | wa1860.#321a-UI | 11077.13 | 241428.78 | 6300376.92 | 88.38 | -0.01 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
45 | 322 | 75.8.20.#322 | 11225.07 | 241348.76 | 6300501.35 | 87.29 | -0.08 |  |  | 0 | 200.0 | 47.7 | OK | 0.0 |  | NG
46 | 323 | 75.8.20.#323 | 11521.36 | 241188.15 | 6300750.33 | 87.44 | 0.04 |  |  | 0 | 200.0 | 50.6 | OK | 0.0 |  | NG
47 | 323A | wa2327.#323a | 11686.51 | 241098.71 | 6300889.17 | 88.07 | 0.11 |  |  | 0 | 200.0 | 46.4 | OK | 0.0 |  | NG
48 | 324 | 75.8.20.#324 | 11841.87 | 241014.82 | 6301019.93 | 86.93 | -0.12 |  |  | 0 | 200.0 | 52.7 | OK | 0.0 |  | NG
49 | 325 | 75.8.20.#325 | 12060.29 | 240896.49 | 6301203.52 | 87.19 | 0.05 |  |  | 0 | 200.0 | 49.2 | OK | 0.0 |  | NG
50 | 326 | 75.8.20.#326 | 12351.74 | 240738.83 | 6301448.64 | 86.26 | -0.03 |  |  | 0 | 200.0 | 51.6 | OK | 0.0 |  | NG
51 | 327 | r75.12.25.#327 | 12647.13 | 240578.89 | 6301696.99 | 86.08 | 0.00 |  |  | 0 | 200.0 | 50.4 | OK | 0.0 |  | NG
52 | 328 | 75.8.20.#328 | 12929.38 | 240426.07 | 6301934.29 | 85.27 | 0.02 |  |  | 0 | 200.0 | 51.3 | OK | 0.0 |  | NG
53 | 329 | 75.8.20.#329 | 13214.21 | 240271.93 | 6302173.81 | 84.64 | 0.01 |  |  | 0 | 200.0 | 50.5 | OK | 0.0 |  | NG
54 | 330 | 75.8.20.#330 | 13484.03 | 240125.95 | 6302400.72 | 84.49 | 0.00 |  |  | 0 | 200.0 | 50.7 | OK | 0.0 |  | NG
55 | 331 | 75.8.20.#331 | 13753.37 | 239980.23 | 6302627.24 | 84.67 | -0.03 |  |  | 0 | 200.0 | 50.9 | OK | 0.0 |  | NG
56 | 332 | 75.8.20.#332 | 14049.14 | 239820.08 | 6302875.90 | 86.28 | 0.03 |  |  | 0 | 200.0 | 49.4 | OK | 0.0 |  | NG
57 | 333 | r75.12.25.#333 | 14344.66 | 239660.20 | 6303124.44 | 86.34 | 0.01 |  |  | 0 | 200.0 | 51.0 | OK | 0.0 |  | NG
58 | 334 | 75.9.24.#334-UI | 14634.22 | 239503.58 | 6303367.98 | 87.32 | -1.38 |  |  | 0 | 200.0 | 53.5 | OK | 0.0 |  | NG
59 | 335 | 75.8.20.#335 | 14936.36 | 239334.10 | 6303618.11 | 89.09 | -0.04 |  |  | 0 | 200.0 | 50.4 | OK | 0.0 |  | NG
60 | 336 | 75.8.20.#336 | 15232.35 | 239167.89 | 6303863.03 | 89.86 | 0.02 |  |  | 0 | 200.0 | 50.5 | OK | 0.0 |  | NG
61 | 337 | 75.8.20.#337 | 15527.43 | 239002.27 | 6304107.25 | 91.44 | 0.04 |  |  | 0 | 200.0 | 48.5 | OK | 0.0 |  | NG
62 | 337A | wa1862.#337a-UI | 15748.95 | 238878.06 | 6304290.67 | 93.66 | -0.02 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
63 | 338 | wa1862.#338-UI | 15822.08 | 238837.03 | 6304351.21 | 93.72 | 1.39 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
64 | 339 | r75.12.25.#339 | 16094.35 | 238689.80 | 6304580.23 | 93.93 | 0.06 |  |  | 0 | 200.0 | 49.2 | OK | 0.0 |  | NG
65 | 340 | 75.8.20.#340 | 16377.27 | 238537.05 | 6304818.38 | 95.37 | -0.01 |  |  | 0 | 200.0 | 48.8 | OK | 0.0 |  | NG
66 | 341 | 75.8.20.#341 | 16660.79 | 238383.93 | 6305056.99 | 94.97 | 0.04 |  |  | 0 | 200.0 | 50.4 | OK | 0.0 |  | NG
67 | 342 | 75.8.20.#342 | 16957.71 | 238223.73 | 6305306.99 | 95.17 | -0.08 |  |  | 0 | 200.0 | 51.1 | OK | 0.0 |  | NG
68 | 343 | 75.8.20.#343 | 17253.84 | 238063.63 | 6305556.11 | 96.21 | 0.02 |  |  | 0 | 200.0 | 45.7 | OK | 0.0 |  | NG
69 | 343A | wa1860.#343a-UI | 17416.60 | 237975.69 | 6305693.06 | 96.10 | 0.08 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
70 | 344 | r75.12.25.#344 | 17564.93 | 237895.71 | 6305817.98 | 95.75 | 0.03 |  |  | 0 | 200.0 | 50.0 | OK | 0.0 |  | NG
71 | 345 | r75.12.25_mod.#345-UI | 17851.39 | 237741.39 | 6306059.32 | 95.54 | 2.26 |  |  | 0 | 200.0 | 55.0 | OK | 0.0 |  | NG
72 | 346 | 75.8.20.#346 | 18103.52 | 237614.03 | 6306276.92 | 93.52 | -0.10 |  |  | 0 | 200.0 | 51.6 | OK | 0.0 |  | NG
73 | 346A | 75.8.20.#346a | 18270.08 | 237529.64 | 6306420.52 | 93.70 | 0.03 |  |  | 0 | 200.0 | 72.1 | OK | 0.0 |  | NG
74 | 347 | 75.8.20.#347 | 18412.91 | 237457.33 | 6306543.69 | 92.86 | -0.06 |  |  | 0 | 200.0 | 45.6 | OK | 0.0 |  | NG
75 | 348 | 75.8.20.#348 | 18628.03 | 237348.24 | 6306729.10 | 93.10 | 0.01 |  |  | 0 | 200.0 | 49.7 | OK | 0.0 |  | NG
76 | 349 | 75.8.20.#349 | 18930.62 | 237194.83 | 6306989.92 | 93.45 | -0.13 |  |  | 0 | 200.0 | 53.6 | OK | 0.0 |  | NG
77 | 350 | 75.8.24.#350 | 19241.59 | 237036.58 | 6307257.61 | 97.64 | -2.66 |  |  | 0 | 200.0 | 55.4 | OK | 0.0 |  | NG
78 | 351 | r75.12.25.#351 | 19525.52 | 236880.92 | 6307495.07 | 96.78 | 0.01 |  |  | 0 | 200.0 | 52.1 | OK | 0.0 |  | NG
79 | 352 | 75.8.20.#352 | 19821.49 | 236718.70 | 6307742.63 | 96.15 | -0.00 |  |  | 0 | 200.0 | 53.2 | OK | 0.0 |  | NG
80 | 353A | 2 _ 12.203_46.610 a4-08397.#353a | 20120.73 | 236554.68 | 6307992.91 | 98.50 | -0.04 |  |  | 0 | 200.0 | 38.0 | OK | 0.0 |  | NG
81 | 353 | 76.8.20_mod_strain.#353-UI | 20247.25 | 236485.26 | 6308098.68 | 97.24 | 0.06 |  |  | 0 | 200.0 | 0.0 | NG | 0.0 |  | NG
82 | 354 | 76.8.20 EW Mod1 | 20416.87 | 236392.33 | 6308240.58 | 95.69 | 0.01 |  |  | 0 | 200.0 | 46.4 | OK | 0.0 |  | NG
83 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 20717.29 | 236227.77 | 6308491.92 | 97.36 | 0.00 |  |  | 0 | 70.5 | 45.9 | OK | 0.0 | Nonlinear | OK
84 | 356 | r75.12.25 EW Mod2 | 20986.30 | 236080.30 | 6308716.91 | 95.80 | -0.02 |  |  | 0 | 200.0 | 54.0 | OK | 0.0 |  | NG
85 | 357 | 76.8.20.#357 | 21282.44 | 235917.87 | 6308964.53 | 95.92 | 0.02 |  |  | 0 | 200.0 | 49.8 | OK | 0.0 |  | NG
86 | 358 | 76.8.20.#358 | 21495.16 | 235801.26 | 6309142.44 | 95.79 | -0.04 |  |  | 0 | 200.0 | 55.1 | OK | 0.0 |  | NG
87 | 359A | 75.8.20_mod.#359a | 21792.51 | 235638.10 | 6309391.03 | 98.66 | 1.21 |  |  | 0 | 200.0 | 56.9 | OK | 0.0 |  | NG
88 | 359 | 75.8.20.#359 | 21886.77 | 235588.06 | 6309470.90 | 98.34 | 0.05 |  |  | 0 | 200.0 | 58.4 | OK | 0.0 |  | NG
89 | 360 | 76.8.20.#360 | 22004.05 | 235525.88 | 6309570.34 | 94.59 | -0.09 |  |  | 0 | 200.0 | 55.0 | OK | 0.0 |  | NG
90 | 361 | 75.8.20.#361 | 22293.76 | 235371.91 | 6309815.75 | 90.91 | -0.03 |  |  | 0 | 200.0 | 52.1 | OK | 0.0 |  | NG
91 | 362 | r75.12.25.#362 | 22604.88 | 235206.44 | 6310079.22 | 89.20 | -0.02 |  |  | 0 | 200.0 | 51.2 | OK | 0.0 |  | NG
92 | 363 | 76.8.20.#363 | 22901.05 | 235048.82 | 6310329.96 | 88.60 | 0.05 |  |  | 0 | 200.0 | 50.8 | OK | 0.0 |  | NG
93 | 363A | wa1860.#363a-UI | 23050.76 | 234969.25 | 6310456.78 | 91.33 | -0.12 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
94 | 364 | 76.8.20 EW Mod2 | 23196.23 | 234891.67 | 6310579.84 | 92.38 | 0.08 |  |  | 0 | 200.0 | 40.8 | OK | 0.0 |  | NG
95 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 23448.44 | 234757.47 | 6310793.37 | 87.16 | 0.00 |  |  | 0 | 69.0 | 49.4 | OK | 0.0 | Nonlinear | OK
96 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 23771.13 | 234585.71 | 6311066.56 | 81.53 | 0.00 |  |  | 0 | 68.8 | 59.8 | OK | 0.0 | Nonlinear | OK
97 | 367 | 75.8.20 EW Mod | 24058.25 | 234432.84 | 6311309.60 | 88.93 | -0.05 |  |  | 0 | 200.0 | 40.6 | OK | 0.0 |  | NG
98 | 368 | r75.12.25.#368 | 24316.17 | 234295.34 | 6311527.81 | 86.23 | -0.02 |  |  | 0 | 200.0 | 53.6 | OK | 0.0 |  | NG
99 | 369 | wa2355.#369-UI | 24577.61 | 234155.87 | 6311748.94 | 82.75 | -12.90 |  |  | 0 | 200.0 | 73.3 | OK | 0.0 |  | NG
100 | 370A | T724-0000-000043 Stick Figure | 24861.47 | 233954.65 | 6311949.16 | 76.24 | 0.00 |  |  | 0 | 200.0 | 52.2 | OK | 0.0 |  | NG
101 | 371A | T724-0000-000043 Stick Figure | 25148.97 | 233748.47 | 6312149.53 | 70.69 | 0.00 |  |  | 0 | 200.0 | 52.5 | OK | 0.0 |  | NG
102 | 372 | 75.8.20.#372 | 25420.79 | 233553.55 | 6312338.97 | 70.09 | -0.03 |  |  | 0 | 200.0 | 53.0 | OK | 0.0 |  | NG
103 | 373A | T724-0000-000043 Stick Figure | 25687.68 | 233362.05 | 6312524.88 | 69.27 | 0.00 |  |  | 0 | 200.0 | 51.3 | OK | 0.0 |  | NG
104 | 374 | 75.9.24_mod.#374 | 25927.91 | 233189.75 | 6312692.28 | 67.84 | 4.22 |  |  | 0 | 200.0 | 64.7 | OK | 0.0 |  | NG
105 | 375 | r75.12.25.#375 | 26154.76 | 233039.13 | 6312861.90 | 66.24 | 0.01 |  |  | 0 | 200.0 | 53.8 | OK | 0.0 |  | NG
106 | 376 | 76.8.20.#376 | 26404.59 | 232873.27 | 6313048.74 | 64.91 | 0.02 |  |  | 0 | 200.0 | 50.6 | OK | 0.0 |  | NG
107 | 377 | 76.8.20.#377 | 26654.78 | 232707.26 | 6313235.91 | 63.38 | -0.00 |  |  | 0 | 200.0 | 50.5 | OK | 0.0 |  | NG
108 | 378 | 75.8.20.#378 | 26950.91 | 232510.74 | 6313457.44 | 62.41 | 0.06 |  |  | 0 | 200.0 | 46.6 | OK | 0.0 |  | NG
109 | 378A | wa1860.#378a-UI | 27105.43 | 232408.31 | 6313573.13 | 61.95 | -0.16 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
110 | 379 | 76.8.20.#379 | 27247.52 | 232313.82 | 6313679.25 | 61.42 | 0.26 |  |  | 0 | 200.0 | 44.2 | OK | 0.0 |  | NG
111 | 380 | 75.8.20.#380 | 27543.46 | 232118.02 | 6313901.15 | 58.77 | -0.18 |  |  | 0 | 200.0 | 50.3 | OK | 0.0 |  | NG
112 | 381 | r75.12.25 EW Mod3 | 27839.23 | 231921.65 | 6314122.33 | 56.09 | 0.00 |  |  | 0 | 200.0 | 53.5 | OK | 0.0 |  | NG
113 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 28139.97 | 231721.98 | 6314347.23 | 53.68 | 0.00 |  |  | 0 | 65.0 | 46.5 | OK | 0.0 | Nonlinear | OK
114 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 28449.72 | 231516.38 | 6314578.90 | 51.31 | 0.00 |  |  | 0 | 67.3 | 49.9 | OK | 0.0 | Nonlinear | OK
115 | 384 | 75.8.20 EW Mod4 | 28735.71 | 231326.64 | 6314792.88 | 49.16 | -0.03 |  |  | 0 | 200.0 | 53.3 | OK | 0.0 |  | NG
116 | 385 | 75.8.20.#385 | 29010.42 | 231144.28 | 6314998.33 | 48.32 | 0.03 |  |  | 0 | 200.0 | 49.0 | OK | 0.0 |  | NG
117 | 386 | 75.8.20.#386 | 29300.16 | 230952.04 | 6315215.12 | 45.29 | -0.03 |  |  | 0 | 200.0 | 50.2 | OK | 0.0 |  | NG
118 | 387 | r75.12.25.#387 | 29599.05 | 230753.63 | 6315438.65 | 41.34 | 0.02 |  |  | 0 | 200.0 | 52.0 | OK | 0.0 |  | NG
119 | 388 | 75.8.20.#388 | 29891.75 | 230559.42 | 6315657.64 | 40.21 | -0.02 |  |  | 0 | 200.0 | 53.6 | OK | 0.0 |  | NG
120 | 389 | 75.10.25.#389 | 30122.22 | 230406.45 | 6315830.03 | 40.38 | 25.28 |  |  | 0 | 200.0 | 87.0 | OK | 0.0 |  | NG
121 | 390 | 75.8.20.#390 | 30351.34 | 230342.12 | 6316049.93 | 38.71 | 0.00 |  |  | 0 | 200.0 | 54.1 | OK | 0.0 |  | NG
122 | 391 | 75.8.20.#391 | 30638.17 | 230261.60 | 6316325.23 | 38.31 | -0.08 |  |  | 0 | 200.0 | 50.7 | OK | 0.0 |  | NG
123 | 391A | wa1860.#391a-UI | 30773.39 | 230223.46 | 6316454.95 | 41.07 | 0.16 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
124 | 392A | T724-0000-000043 Stick Figure | 30918.81 | 230182.91 | 6316594.61 | 39.84 | 0.00 |  |  | 0 | 200.0 | 42.9 | OK | 0.0 |  | NG
125 | 393A | T724-0000-000043 Stick Figure | 31212.58 | 230103.17 | 6316877.35 | 34.77 | 0.00 |  |  | 0 | 200.0 | 52.5 | OK | 0.0 |  | NG
126 | 394A | T724-0000-000043 Stick Figure | 31509.16 | 230022.62 | 6317162.78 | 35.10 | 0.00 |  |  | 0 | 200.0 | 47.6 | OK | 0.0 |  | NG
127 | 395A | T724-0000-000043 Stick Figure | 31804.99 | 229942.39 | 6317447.52 | 32.59 | 0.00 |  |  | 0 | 200.0 | 50.3 | OK | 0.0 |  | NG
128 | 396A | T724-0000-000043 Stick Figure | 32090.81 | 229865.00 | 6317722.66 | 31.93 | 0.00 |  |  | 0 | 200.0 | 47.9 | OK | 0.0 |  | NG
129 | 397A | WB2370 Stick Figure w 3 02117_040-006 as-built | 32397.14 | 229781.92 | 6318017.51 | 29.96 | 0.00 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
130 | 398A | T724-0000-000043 Stick Figure | 32697.82 | 229700.46 | 6318306.95 | 28.75 | 0.00 |  |  | 0 | 200.0 | 49.0 | OK | 0.0 |  | NG
131 | 399A | T724-0000-000043 Stick Figure | 32988.63 | 229621.49 | 6318586.83 | 28.25 | 0.00 |  |  | 0 | 200.0 | 47.3 | OK | 0.0 |  | NG
132 | 400 | 75.8.20 Re-Ins new xarm | 33279.41 | 229542.44 | 6318866.66 | 26.17 | 0.08 |  |  | 0 | 200.0 | 51.5 | OK | 0.0 |  | NG
133 | 401 | 75.8.20.#401 | 33575.55 | 229462.31 | 6319151.75 | 26.36 | -0.07 |  |  | 0 | 200.0 | 50.9 | OK | 0.0 |  | NG
134 | 402 | 75.8.20.#402 | 33871.12 | 229381.99 | 6319436.20 | 27.96 | 0.03 |  |  | 0 | 200.0 | 48.6 | OK | 0.0 |  | NG
135 | 403 | 75.8.20.#403 | 34155.19 | 229304.93 | 6319709.62 | 26.74 | 0.08 |  |  | 0 | 200.0 | 48.4 | OK | 0.0 |  | NG
136 | 404 | wa1862.#404-UI | 34306.00 | 229264.23 | 6319854.83 | 28.07 | -0.08 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
137 | 404A | wa2327.#404a-UI | 34498.60 | 229211.98 | 6320040.21 | 24.93 | -0.06 |  |  | 0 | 200.0 | 49.2 | OK | 0.0 |  | NG
138 | 405 | 75.10.25.#405 | 34678.22 | 229163.06 | 6320213.04 | 24.79 | -31.33 |  |  | 0 | 200.0 | 86.0 | OK | 0.0 |  | NG
139 | 406 | 75.8.20.#406 | 34900.95 | 228999.80 | 6320364.55 | 24.19 | -0.12 |  |  | 0 | 200.0 | 49.4 | OK | 0.0 |  | NG
140 | 407 | 75.8.20.#407 | 35145.61 | 228820.11 | 6320530.59 | 22.18 | 0.08 |  |  | 0 | 200.0 | 50.3 | OK | 0.0 |  | NG
141 | 408 | 75.8.20.#408 | 35393.10 | 228638.56 | 6320698.79 | 20.71 | -0.01 |  |  | 0 | 200.0 | 51.9 | OK | 0.0 |  | NG
142 | 409 | 75.8.20_mod.#409 | 35630.42 | 228464.44 | 6320860.05 | 18.03 | 2.31 |  |  | 0 | 200.0 | 57.8 | OK | 0.0 |  | NG
143 | 410 | 75.9.24_mod.#410 | 35853.13 | 228307.27 | 6321017.83 | 17.65 | 6.04 |  |  | 0 | 200.0 | 62.2 | OK | 0.0 |  | NG
144 | 411 | r75.12.25 #411 Ins attch Update | 36087.57 | 228160.21 | 6321200.41 | 16.92 | -0.01 |  |  | 0 | 200.0 | 56.0 | OK | 0.0 |  | NG
145 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 36323.19 | 228012.35 | 6321383.86 | 19.61 | 0.00 |  |  | 0 | 66.1 | 46.5 | OK | 0.0 | Nonlinear | OK
146 | 412A | wa2327.#412a-UI | 36534.45 | 227879.38 | 6321548.03 | 18.32 | 0.04 |  |  | 0 | 200.0 | 51.8 | OK | 0.0 |  | NG
147 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 36762.97 | 227735.70 | 6321725.73 | 16.76 | 0.00 |  |  | 0 | 65.8 | 50.3 | OK | 0.0 | Nonlinear | OK
148 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 36961.19 | 227611.52 | 6321880.23 | 18.12 | 0.00 |  |  | 0 | 66.5 | 45.7 | OK | 0.0 | Nonlinear | OK
149 | 415 | wa2327.#415 | 37172.10 | 227479.73 | 6322044.90 | 15.84 | -0.08 |  |  | 0 | 200.0 | 50.8 | OK | 0.0 |  | NG
150 | 415A | wa2327.#415b-UI | 37318.00 | 227388.41 | 6322158.68 | 13.65 | 0.04 |  |  | 0 | 200.0 | 51.9 | OK | 0.0 |  | NG
151 | 415B | 722.5-200x30_22-475.#415b | 37368.66 | 227356.73 | 6322198.21 | 13.85 | 0.00 |  |  | 0 | 200.0 | 200.0 | OK | 0.0 |  | NG
152 | 416 | r75.12.25.#416 | 37549.49 | 227243.65 | 6322339.32 | 12.12 | -0.33 |  |  | 0 | 200.0 | 50.2 | OK | 0.0 |  | NG
153 | 417 | 75.8.20.#417 | 37777.33 | 227100.16 | 6322516.30 | 9.76 | 0.25 |  |  | 0 | 200.0 | 50.4 | OK | 0.0 |  | NG
154 | 417A | wa2327.#417a-UI | 37979.96 | 226973.23 | 6322674.25 | 7.63 | 0.13 |  |  | 0 | 200.0 | 51.7 | OK | 0.0 |  | NG
155 | 418 | 76.8.20_mod_susp.#418 | 38169.51 | 226854.82 | 6322822.27 | 5.72 | -0.36 |  |  | 0 | 200.0 | 53.9 | OK | 0.0 |  | NG
156 | 419 | 75.8.20_mod2.#419 | 38361.14 | 226734.17 | 6322971.15 | 5.48 | 2.69 |  |  | 0 | 200.0 | 0.0 | OK | 0.0 |  | NG
157 | 420 | r 60.10.24.#420 | 38465.78 | 226672.18 | 6323055.45 | 5.00 | 0.20 |  |  | 0 | 200.0 | 0.0 | NG | 0.0 |  | NG
158 | 421 | 80.9.24.#421 | 38557.81 | 226617.92 | 6323129.78 | 5.00 | 42.88 |  |  | 0 | 200.0 | 76.4 | OK | 0.0 |  | NG
159 | 421C | 310 396_623-021.#421c-UI | 38616.29 | 226624.80 | 6323187.86 | 5.10 | 0.75 |  |  | 0 | 200.0 | 0.0 | NG | 0.0 |  | NG
160 | 421B | 310 396_623-022.#421b-UI | 38739.98 | 226640.95 | 6323310.49 | 4.69 | -90.77 |  |  | 0 | 200.0 | 0.0 | NG | 0.0 |  | NG
161 | BNG | bng.#bng-UI | 38784.43 | 226596.81 | 6323315.70 | 5.64 | 0.00 |  |  | 0 | 200.0 | 0.0 | NG | 0.0 |  | NG

## Tab_2
rowtext | str | set | phase | swing_cond | weather_case_description | wire_condition | min_allowed | max_allowed | min_calc | max_calc | _of_allowed_swing | _ok
1 | 282 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.3 | 45.5 | 50.6 | OK
2 | 282 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.2 | 32.6 | 36.2 | OK
3 | 282 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.1 | 14.3 | 15.9 | OK
4 | 282 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.3 | 45.5 | 50.6 | OK
5 | 282 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 45.4 | 50.4 | OK
6 | 282 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.8 | 32.3 | 35.9 | OK
7 | 282 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.6 | 13.9 | 15.4 | OK
8 | 282 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 45.4 | 50.4 | OK
9 | 282 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 37.7 | 47.5 | OK
10 | 282 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.4 | 24.4 | 33.7 | OK
11 | 282 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.2 | 6.6 | 14.7 | OK
12 | 282 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 37.7 | 47.5 | OK
13 | 283 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.7 | 46.4 | 51.9 | OK
14 | 283 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 31.9 | 35.9 | OK
15 | 283 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 11.5 | 13.3 | OK
16 | 283 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.7 | 46.4 | 51.9 | OK
17 | 283 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 46.7 | 53.0 | OK
18 | 283 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.3 | 32.0 | 37.0 | OK
19 | 283 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.7 | 11.2 | 14.1 | OK
20 | 283 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 46.7 | 53.0 | OK
21 | 283 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.9 | 52.2 | OK
22 | 283 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 32.6 | 36.3 | OK
23 | 283 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 12.4 | 13.7 | OK
24 | 283 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.9 | 52.2 | OK
25 | 284A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 44.3 | 49.2 | OK
26 | 284A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.8 | 30.5 | 33.9 | OK
27 | 284A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 11.4 | 12.7 | OK
28 | 284A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 44.3 | 49.2 | OK
29 | 284A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 44.1 | 49.0 | OK
30 | 284A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.9 | 30.5 | 33.9 | OK
31 | 284A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.9 | 11.7 | 13.0 | OK
32 | 284A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 44.1 | 49.0 | OK
33 | 284A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.5 | 49.2 | OK
34 | 284A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.6 | 29.6 | 34.0 | OK
35 | 284A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 10.4 | 12.8 | OK
36 | 284A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.5 | 49.2 | OK
37 | 285A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.9 | 48.7 | OK
38 | 285A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.9 | 30.1 | 33.4 | OK
39 | 285A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 11.0 | 12.3 | OK
40 | 285A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.9 | 48.7 | OK
41 | 285A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 43.7 | 48.6 | OK
42 | 285A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.9 | 30.2 | 33.5 | OK
43 | 285A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 11.5 | 12.7 | OK
44 | 285A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 43.7 | 48.6 | OK
45 | 285A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.2 | 49.3 | OK
46 | 285A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.7 | 29.2 | 34.1 | OK
47 | 285A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 10.1 | 13.0 | OK
48 | 285A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.2 | 49.3 | OK
49 | 286 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.6 | 50.6 | OK
50 | 286 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.5 | 35.0 | OK
51 | 286 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.6 | 12.9 | OK
52 | 286 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.6 | 50.6 | OK
53 | 286 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 45.7 | 51.6 | OK
54 | 286 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 31.3 | 35.8 | OK
55 | 286 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.2 | 11.1 | 13.5 | OK
56 | 286 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 45.7 | 51.6 | OK
57 | 286 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 46.2 | 51.3 | OK
58 | 286 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.5 | 32.2 | 35.8 | OK
59 | 286 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 12.5 | 13.9 | OK
60 | 286 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 46.2 | 51.3 | OK
61 | 287 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.9 | 39.4 | 43.8 | OK
62 | 287 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.4 | 27.0 | 30.0 | OK
63 | 287 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.3 | 10.0 | 11.1 | OK
64 | 287 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.9 | 39.4 | 43.8 | OK
65 | 287 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.8 | 40.3 | 44.8 | OK
66 | 287 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.0 | 27.6 | 30.7 | OK
67 | 287 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.6 | 10.2 | 11.4 | OK
68 | 287 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.8 | 40.3 | 44.8 | OK
69 | 287 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.2 | 39.9 | 45.8 | OK
70 | 287 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.4 | 26.9 | 31.6 | OK
71 | 287 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 9.2 | 12.1 | OK
72 | 287 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.2 | 39.9 | 45.8 | OK
73 | 288A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.3 | 41.2 | 45.8 | OK
74 | 288A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.3 | 28.7 | 31.9 | OK
75 | 288A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.9 | 11.7 | 13.0 | OK
76 | 288A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.3 | 41.2 | 45.8 | OK
77 | 288A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.1 | 41.4 | 46.0 | OK
78 | 288A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.2 | 29.2 | 32.4 | OK
79 | 288A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -6.9 | 12.4 | 13.8 | OK
80 | 288A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.1 | 41.4 | 46.0 | OK
81 | 288A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 40.0 | 47.9 | OK
82 | 288A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 26.5 | 33.5 | OK
83 | 288A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.3 | 8.2 | 13.7 | OK
84 | 288A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 40.0 | 47.9 | OK
85 | 289 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 43.4 | 51.1 | OK
86 | 289 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 29.1 | 35.9 | OK
87 | 289 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.0 | 9.4 | 14.5 | OK
88 | 289 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 43.4 | 51.1 | OK
89 | 289 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 43.4 | 52.0 | OK
90 | 289 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.1 | 28.9 | 36.8 | OK
91 | 289 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.8 | 8.9 | 15.3 | OK
92 | 289 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 43.4 | 52.0 | OK
93 | 289 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 44.2 | 49.1 | OK
94 | 289 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.1 | 30.9 | 34.3 | OK
95 | 289 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.2 | 12.3 | 13.7 | OK
96 | 289 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 44.2 | 49.1 | OK
97 | 290A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 41.0 | 52.0 | OK
98 | 290A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.6 | 26.5 | 37.4 | OK
99 | 290A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.0 | 6.8 | 16.7 | OK
100 | 290A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 41.0 | 52.0 | OK
101 | 290A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 40.9 | 50.6 | OK
102 | 290A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 26.7 | 35.9 | OK
103 | 290A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.9 | 7.6 | 15.4 | OK
104 | 290A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 40.9 | 50.6 | OK
105 | 290A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -49.1 | 39.7 | 54.5 | OK
106 | 290A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -36.1 | 24.6 | 40.1 | OK
107 | 290A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -17.6 | 4.4 | 19.6 | OK
108 | 290A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -49.1 | 39.7 | 54.5 | OK
109 | 291 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 44.6 | 51.8 | OK
110 | 291 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.6 | 30.2 | 36.3 | OK
111 | 291 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.9 | 10.0 | 14.4 | OK
112 | 291 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 44.6 | 51.8 | OK
113 | 291 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 44.9 | 52.8 | OK
114 | 291 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.5 | 30.2 | 37.2 | OK
115 | 291 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.6 | 9.7 | 15.1 | OK
116 | 291 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 44.9 | 52.8 | OK
117 | 291 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 45.4 | 51.0 | OK
118 | 291 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 31.1 | 35.3 | OK
119 | 291 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 11.1 | 13.2 | OK
120 | 291 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 45.4 | 51.0 | OK
121 | 292 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.3 | 43.6 | 48.4 | OK
122 | 292 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.6 | 30.0 | 33.3 | OK
123 | 292 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.7 | 11.1 | 12.3 | OK
124 | 292 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.3 | 43.6 | 48.4 | OK
125 | 292 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 43.9 | 48.8 | OK
126 | 292 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.1 | 30.2 | 33.5 | OK
127 | 292 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.1 | 12.3 | OK
128 | 292 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 43.9 | 48.8 | OK
129 | 292 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 43.5 | 48.4 | OK
130 | 292 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.9 | 29.9 | 33.2 | OK
131 | 292 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 10.9 | 12.1 | OK
132 | 292 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 43.5 | 48.4 | OK
133 | 293 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 42.7 | 48.3 | OK
134 | 293 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.8 | 29.0 | 33.1 | OK
135 | 293 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 10.3 | 12.3 | OK
136 | 293 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 42.7 | 48.3 | OK
137 | 293 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.1 | 42.5 | 47.9 | OK
138 | 293 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.5 | 28.9 | 32.8 | OK
139 | 293 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 10.3 | 12.1 | OK
140 | 293 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.1 | 42.5 | 47.9 | OK
141 | 293 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 42.7 | 48.0 | OK
142 | 293 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.6 | 29.0 | 32.9 | OK
143 | 293 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 10.4 | 12.1 | OK
144 | 293 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 42.7 | 48.0 | OK
145 | 294 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -60.4 | 13.4 | 67.1 | OK
146 | 294 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -50.9 | -2.5 | 56.6 | OK
147 | 294 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -37.2 | -20.1 | 41.3 | OK
148 | 294 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -60.4 | 13.4 | 67.1 | OK
149 | 294 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -60.1 | 14.3 | 66.8 | OK
150 | 294 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -50.5 | -1.6 | 56.1 | OK
151 | 294 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -36.6 | -19.3 | 40.7 | OK
152 | 294 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -60.1 | 14.3 | 66.8 | OK
153 | 294 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -60.3 | 15.1 | 67.0 | OK
154 | 294 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -50.7 | -1.1 | 56.3 | OK
155 | 294 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -36.6 | -19.1 | 40.7 | OK
156 | 294 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -60.3 | 15.1 | 67.0 | OK
157 | 295 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 39.4 | 50.8 | OK
158 | 295 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.7 | 25.2 | 36.3 | OK
159 | 295 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -14.6 | 6.4 | 16.2 | OK
160 | 295 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 39.4 | 50.8 | OK
161 | 295 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 39.5 | 50.0 | OK
162 | 295 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.0 | 25.5 | 35.5 | OK
163 | 295 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -14.0 | 6.8 | 15.5 | OK
164 | 295 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 39.5 | 50.0 | OK
165 | 295 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.4 | 39.4 | 50.5 | OK
166 | 295 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.4 | 25.3 | 36.0 | OK
167 | 295 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -14.4 | 6.5 | 16.0 | OK
168 | 295 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.4 | 39.4 | 50.5 | OK
169 | 296 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.5 | 50.6 | OK
170 | 296 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 31.4 | 34.8 | OK
171 | 296 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.5 | 12.7 | OK
172 | 296 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.5 | 50.6 | OK
173 | 296 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 48.7 | 54.1 | OK
174 | 296 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.8 | 35.2 | 39.1 | OK
175 | 296 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.2 | 15.8 | 17.6 | OK
176 | 296 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 48.7 | 54.1 | OK
177 | 296 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.3 | 50.6 | OK
178 | 296 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 31.2 | 34.9 | OK
179 | 296 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.3 | 12.8 | OK
180 | 296 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.3 | 50.6 | OK
181 | 297 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.9 | 50.8 | 56.4 | OK
182 | 297 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -21.4 | 38.5 | 42.8 | OK
183 | 297 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -1.1 | 20.7 | 23.0 | OK
184 | 297 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.9 | 50.8 | 56.4 | OK
185 | 297 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.4 | 50.9 | 56.6 | OK
186 | 297 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -21.9 | 38.6 | 42.8 | OK
187 | 297 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -1.4 | 20.5 | 22.8 | OK
188 | 297 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.4 | 50.9 | 56.6 | OK
189 | 297 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.9 | 49.9 | OK
190 | 297 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.6 | 30.9 | 34.4 | OK
191 | 297 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 11.4 | 12.7 | OK
192 | 297 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.9 | 49.9 | OK
193 | 298 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.1 | 44.3 | 49.3 | OK
194 | 298 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 30.5 | 33.9 | OK
195 | 298 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.3 | 12.5 | OK
196 | 298 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.1 | 44.3 | 49.3 | OK
197 | 298 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.6 | 47.6 | 52.9 | OK
198 | 298 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.9 | 34.6 | 38.4 | OK
199 | 298 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -6.1 | 16.0 | 17.8 | OK
200 | 298 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.6 | 47.6 | 52.9 | OK
201 | 298 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.1 | 44.2 | 49.1 | OK
202 | 298 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.3 | 30.4 | 33.8 | OK
203 | 298 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 11.1 | 12.4 | OK
204 | 298 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.1 | 44.2 | 49.1 | OK
205 | 299 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 45.0 | 51.4 | OK
206 | 299 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.0 | 30.8 | 35.6 | OK
207 | 299 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 10.9 | 13.4 | OK
208 | 299 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 45.0 | 51.4 | OK
209 | 299 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 45.2 | 51.3 | OK
210 | 299 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.9 | 31.0 | 35.5 | OK
211 | 299 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 11.1 | 13.3 | OK
212 | 299 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 45.2 | 51.3 | OK
213 | 299 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 44.7 | 51.3 | OK
214 | 299 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.1 | 30.5 | 35.7 | OK
215 | 299 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.3 | 10.6 | 13.6 | OK
216 | 299 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 44.7 | 51.3 | OK
217 | 300 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -63.4 | -8.8 | 70.5 | OK
218 | 300 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -55.9 | -19.8 | 62.1 | OK
219 | 300 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -45.2 | -32.3 | 50.2 | OK
220 | 300 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -63.4 | -8.8 | 70.5 | OK
221 | 300 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -62.8 | -6.0 | 69.8 | OK
222 | 300 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -55.0 | -17.5 | 61.1 | OK
223 | 300 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -43.9 | -30.5 | 48.8 | OK
224 | 300 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -62.8 | -6.0 | 69.8 | OK
225 | 300 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -63.0 | -6.0 | 70.0 | OK
226 | 300 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -55.2 | -17.6 | 61.3 | OK
227 | 300 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -44.1 | -30.7 | 49.0 | OK
228 | 300 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -63.0 | -6.0 | 70.0 | OK
229 | 301 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 39.1 | 43.4 | OK
230 | 301 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.6 | 27.0 | 30.0 | OK
231 | 301 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.6 | 10.4 | 11.6 | OK
232 | 301 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 39.1 | 43.4 | OK
233 | 301 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.5 | 40.2 | 44.6 | OK
234 | 301 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.6 | 27.7 | 30.8 | OK
235 | 301 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.1 | 10.6 | 11.8 | OK
236 | 301 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.5 | 40.2 | 44.6 | OK
237 | 301 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 39.3 | 46.1 | OK
238 | 301 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.6 | 26.5 | 31.8 | OK
239 | 301 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 8.9 | 12.3 | OK
240 | 301 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 39.3 | 46.1 | OK
241 | 302 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.8 | 40.4 | 44.9 | OK
242 | 302 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.0 | 27.9 | 31.0 | OK
243 | 302 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.7 | 10.8 | 12.0 | OK
244 | 302 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.8 | 40.4 | 44.9 | OK
245 | 302 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 41.9 | 46.6 | OK
246 | 302 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.3 | 28.8 | 32.0 | OK
247 | 302 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 10.6 | 11.8 | OK
248 | 302 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 41.9 | 46.6 | OK
249 | 302 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 42.0 | 46.7 | OK
250 | 302 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.6 | 29.0 | 32.2 | OK
251 | 302 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.5 | 11.1 | 12.3 | OK
252 | 302 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 42.0 | 46.7 | OK
253 | 303A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.9 | 51.0 | OK
254 | 303A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 31.7 | 35.3 | OK
255 | 303A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 11.9 | 13.2 | OK
256 | 303A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.9 | 51.0 | OK
257 | 303A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 45.5 | 50.5 | OK
258 | 303A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 31.6 | 35.1 | OK
259 | 303A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 12.1 | 13.4 | OK
260 | 303A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 45.5 | 50.5 | OK
261 | 303A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 45.1 | 51.1 | OK
262 | 303A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.9 | 30.8 | 35.4 | OK
263 | 303A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 10.8 | 13.4 | OK
264 | 303A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 45.1 | 51.1 | OK
265 | 304A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.2 | 41.8 | 46.5 | OK
266 | 304A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.9 | 28.7 | 31.9 | OK
267 | 304A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.8 | 10.7 | 11.9 | OK
268 | 304A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.2 | 41.8 | 46.5 | OK
269 | 304A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.7 | 41.9 | 46.6 | OK
270 | 304A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.5 | 28.9 | 32.1 | OK
271 | 304A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.5 | 11.0 | 12.3 | OK
272 | 304A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.7 | 41.9 | 46.6 | OK
273 | 304A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.0 | 41.3 | 46.7 | OK
274 | 304A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.8 | 28.1 | 32.0 | OK
275 | 304A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 9.9 | 12.0 | OK
276 | 304A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.0 | 41.3 | 46.7 | OK
277 | 305 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 46.0 | 52.4 | OK
278 | 305 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.9 | 31.5 | 36.6 | OK
279 | 305 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.7 | 10.9 | 14.1 | OK
280 | 305 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 46.0 | 52.4 | OK
281 | 305 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 46.2 | 53.0 | OK
282 | 305 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.4 | 31.5 | 37.1 | OK
283 | 305 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.1 | 10.7 | 14.5 | OK
284 | 305 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 46.2 | 53.0 | OK
285 | 305 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.3 | 46.5 | 51.6 | OK
286 | 305 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.9 | 32.1 | 35.7 | OK
287 | 305 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.8 | 13.1 | OK
288 | 305 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.3 | 46.5 | 51.6 | OK
289 | 306 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.8 | 50.8 | OK
290 | 306 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.7 | 35.2 | OK
291 | 306 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.8 | 13.1 | OK
292 | 306 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.8 | 50.8 | OK
293 | 306 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.4 | 45.7 | 50.8 | OK
294 | 306 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.6 | 35.1 | OK
295 | 306 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.7 | 13.0 | OK
296 | 306 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.4 | 45.7 | 50.8 | OK
297 | 306 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.4 | 45.8 | 50.9 | OK
298 | 306 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.7 | 35.2 | OK
299 | 306 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.8 | 13.1 | OK
300 | 306 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.4 | 45.8 | 50.9 | OK
301 | 307 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.5 | 45.0 | 50.0 | OK
302 | 307 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.5 | 31.1 | 34.5 | OK
303 | 307 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.6 | 12.9 | OK
304 | 307 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.5 | 45.0 | 50.0 | OK
305 | 307 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.1 | 50.1 | OK
306 | 307 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.1 | 34.5 | OK
307 | 307 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.4 | 12.6 | OK
308 | 307 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.1 | 50.1 | OK
309 | 307 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.4 | 50.9 | OK
310 | 307 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 31.2 | 35.2 | OK
311 | 307 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.2 | 13.1 | OK
312 | 307 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.4 | 50.9 | OK
313 | 308 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 44.9 | 50.7 | OK
314 | 308 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 30.7 | 35.2 | OK
315 | 308 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 10.8 | 13.3 | OK
316 | 308 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 44.9 | 50.7 | OK
317 | 308 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.6 | 49.5 | OK
318 | 308 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.6 | 30.7 | 34.1 | OK
319 | 308 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.2 | 12.5 | OK
320 | 308 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.6 | 49.5 | OK
321 | 308 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 44.1 | 49.0 | OK
322 | 308 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.2 | 30.6 | 34.0 | OK
323 | 308 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 11.7 | 13.0 | OK
324 | 308 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 44.1 | 49.0 | OK
325 | 309 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 44.2 | 51.3 | OK
326 | 309 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 29.9 | 35.9 | OK
327 | 309 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.8 | 9.9 | 14.2 | OK
328 | 309 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 44.2 | 51.3 | OK
329 | 309 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 44.4 | 51.8 | OK
330 | 309 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.7 | 30.0 | 36.4 | OK
331 | 309 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.1 | 9.8 | 14.5 | OK
332 | 309 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 44.4 | 51.8 | OK
333 | 309 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 44.8 | 53.0 | OK
334 | 309 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.7 | 30.0 | 37.5 | OK
335 | 309 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.8 | 9.5 | 15.4 | OK
336 | 309 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 44.8 | 53.0 | OK
337 | 310 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 43.6 | 48.7 | OK
338 | 310 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.1 | 29.9 | 33.5 | OK
339 | 310 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 10.8 | 12.3 | OK
340 | 310 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 43.6 | 48.7 | OK
341 | 310 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.7 | 49.2 | OK
342 | 310 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.6 | 29.8 | 34.0 | OK
343 | 310 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 10.6 | 12.7 | OK
344 | 310 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.7 | 49.2 | OK
345 | 310 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 43.5 | 48.9 | OK
346 | 310 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.4 | 29.7 | 33.7 | OK
347 | 310 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 10.6 | 12.6 | OK
348 | 310 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 43.5 | 48.9 | OK
349 | 311 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.5 | 48.5 | OK
350 | 311 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 29.8 | 33.3 | OK
351 | 311 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 10.7 | 12.2 | OK
352 | 311 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.5 | 48.5 | OK
353 | 311 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.3 | 43.9 | 48.8 | OK
354 | 311 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.5 | 30.3 | 33.6 | OK
355 | 311 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 11.3 | 12.6 | OK
356 | 311 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.3 | 43.9 | 48.8 | OK
357 | 311 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 43.8 | 48.7 | OK
358 | 311 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.8 | 30.1 | 33.5 | OK
359 | 311 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 11.1 | 12.3 | OK
360 | 311 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 43.8 | 48.7 | OK
361 | 312 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.0 | 42.3 | 53.3 | OK
362 | 312 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.6 | 27.4 | 38.5 | OK
363 | 312 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.5 | 7.1 | 17.3 | OK
364 | 312 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.0 | 42.3 | 53.3 | OK
365 | 312 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 42.4 | 53.0 | OK
366 | 312 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.3 | 27.7 | 38.1 | OK
367 | 312 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.2 | 7.4 | 16.9 | OK
368 | 312 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 42.4 | 53.0 | OK
369 | 312 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.9 | 42.0 | 53.2 | OK
370 | 312 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.6 | 27.2 | 38.4 | OK
371 | 312 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.6 | 7.0 | 17.3 | OK
372 | 312 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.9 | 42.0 | 53.2 | OK
373 | 313 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.2 | OK
374 | 313 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 30.8 | 34.7 | OK
375 | 313 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.1 | 12.9 | OK
376 | 313 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.2 | OK
377 | 313 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.9 | 50.3 | OK
378 | 313 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 30.8 | 34.8 | OK
379 | 313 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.1 | 12.9 | OK
380 | 313 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.9 | 50.3 | OK
381 | 313 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.3 | OK
382 | 313 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 30.8 | 34.7 | OK
383 | 313 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.1 | 12.9 | OK
384 | 313 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.3 | OK
385 | 314 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
386 | 314 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.2 | 34.7 | OK
387 | 314 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.5 | 12.7 | OK
388 | 314 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
389 | 314 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.3 | 50.4 | OK
390 | 314 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 31.3 | 34.8 | OK
391 | 314 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.5 | 12.8 | OK
392 | 314 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.3 | 50.4 | OK
393 | 314 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.3 | 50.4 | OK
394 | 314 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.3 | 34.7 | OK
395 | 314 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.5 | 12.8 | OK
396 | 314 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.3 | 50.4 | OK
397 | 315 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.6 | 51.8 | OK
398 | 315 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 32.3 | 35.9 | OK
399 | 315 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 12.0 | 13.4 | OK
400 | 315 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.6 | 51.8 | OK
401 | 315 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.4 | 51.6 | OK
402 | 315 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 32.1 | 35.7 | OK
403 | 315 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.9 | 13.2 | OK
404 | 315 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.4 | 51.6 | OK
405 | 315 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.6 | 51.7 | OK
406 | 315 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 32.2 | 35.8 | OK
407 | 315 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 12.0 | 13.3 | OK
408 | 315 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 46.6 | 51.7 | OK
409 | 316 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.0 | 49.2 | OK
410 | 316 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.5 | 30.2 | 33.9 | OK
411 | 316 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 10.9 | 12.5 | OK
412 | 316 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.0 | 49.2 | OK
413 | 316 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.3 | 49.2 | OK
414 | 316 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.4 | 30.5 | 33.9 | OK
415 | 316 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.1 | 12.4 | OK
416 | 316 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.3 | 49.2 | OK
417 | 316 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.1 | 49.3 | OK
418 | 316 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.5 | 30.3 | 33.9 | OK
419 | 316 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 10.9 | 12.5 | OK
420 | 316 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.1 | 49.3 | OK
421 | 317 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 44.8 | 49.8 | OK
422 | 317 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 30.8 | 34.3 | OK
423 | 317 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.3 | 12.5 | OK
424 | 317 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 44.8 | 49.8 | OK
425 | 317 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.6 | 50.0 | OK
426 | 317 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 30.6 | 34.5 | OK
427 | 317 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.0 | 12.8 | OK
428 | 317 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.6 | 50.0 | OK
429 | 317 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.8 | 49.8 | OK
430 | 317 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 30.9 | 34.3 | OK
431 | 317 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.3 | 12.6 | OK
432 | 317 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.8 | 49.8 | OK
433 | 318 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.7 | 50.9 | OK
434 | 318 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 31.5 | 35.1 | OK
435 | 318 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.5 | 12.9 | OK
436 | 318 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.7 | 50.9 | OK
437 | 318 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.8 | 50.9 | OK
438 | 318 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 31.6 | 35.2 | OK
439 | 318 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.7 | 13.0 | OK
440 | 318 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.8 | 50.9 | OK
441 | 318 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.6 | 50.8 | OK
442 | 318 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.5 | 31.5 | 35.0 | OK
443 | 318 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.5 | 12.8 | OK
444 | 318 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.6 | 50.8 | OK
445 | 319 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.2 | 51.3 | OK
446 | 319 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 31.9 | 35.5 | OK
447 | 319 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.8 | 13.1 | OK
448 | 319 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.2 | 51.3 | OK
449 | 319 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.2 | 51.3 | OK
450 | 319 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 32.0 | 35.5 | OK
451 | 319 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.8 | 13.2 | OK
452 | 319 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.2 | 51.3 | OK
453 | 319 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 46.3 | 51.4 | OK
454 | 319 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 32.0 | 35.6 | OK
455 | 319 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.9 | 13.2 | OK
456 | 319 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 46.3 | 51.4 | OK
457 | 320 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.5 | 49.5 | OK
458 | 320 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.7 | 30.6 | 34.1 | OK
459 | 320 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.2 | 12.5 | OK
460 | 320 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.5 | 49.5 | OK
461 | 320 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.4 | 49.6 | OK
462 | 320 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 30.5 | 34.2 | OK
463 | 320 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.0 | 12.6 | OK
464 | 320 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.4 | 49.6 | OK
465 | 320 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.3 | 49.6 | OK
466 | 320 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 30.4 | 34.2 | OK
467 | 320 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 10.9 | 12.7 | OK
468 | 320 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.3 | 49.6 | OK
469 | 321 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 39.9 | 44.4 | OK
470 | 321 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.6 | 27.6 | 30.6 | OK
471 | 321 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.6 | 10.7 | 11.9 | OK
472 | 321 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 39.9 | 44.4 | OK
473 | 321 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.2 | 41.3 | 45.9 | OK
474 | 321 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.3 | 28.7 | 31.9 | OK
475 | 321 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.6 | 11.3 | 12.6 | OK
476 | 321 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.2 | 41.3 | 45.9 | OK
477 | 321 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.6 | 45.5 | OK
478 | 321 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.1 | 27.6 | 31.2 | OK
479 | 321 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 9.8 | 11.5 | OK
480 | 321 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.6 | 45.5 | OK
481 | 322 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.5 | 41.3 | 45.9 | OK
482 | 322 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.4 | 28.4 | 31.5 | OK
483 | 322 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.6 | 10.7 | 11.9 | OK
484 | 322 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.5 | 41.3 | 45.9 | OK
485 | 322 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.2 | 42.4 | 47.1 | OK
486 | 322 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.9 | 29.3 | 32.5 | OK
487 | 322 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.6 | 11.2 | 12.4 | OK
488 | 322 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.2 | 42.4 | 47.1 | OK
489 | 322 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 41.7 | 47.7 | OK
490 | 322 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.7 | 28.2 | 33.0 | OK
491 | 322 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 9.7 | 12.6 | OK
492 | 322 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 41.7 | 47.7 | OK
493 | 323 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.4 | 50.4 | OK
494 | 323 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.3 | 34.8 | OK
495 | 323 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.5 | 12.8 | OK
496 | 323 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.4 | 50.4 | OK
497 | 323 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.6 | 50.6 | OK
498 | 323 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.4 | 34.9 | OK
499 | 323 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.6 | 12.9 | OK
500 | 323 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.6 | 50.6 | OK
501 | 323 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.3 | 50.5 | OK
502 | 323 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 31.2 | 34.8 | OK
503 | 323 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.3 | 12.8 | OK
504 | 323 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.3 | 50.5 | OK
505 | 323A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 41.4 | 46.1 | OK
506 | 323A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.4 | 28.3 | 31.5 | OK
507 | 323A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 10.2 | 11.5 | OK
508 | 323A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 41.4 | 46.1 | OK
509 | 323A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.7 | 41.2 | 46.4 | OK
510 | 323A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.6 | 28.0 | 31.8 | OK
511 | 323A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.6 | 9.9 | 11.8 | OK
512 | 323A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.7 | 41.2 | 46.4 | OK
513 | 323A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 41.3 | 46.2 | OK
514 | 323A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.4 | 28.2 | 31.6 | OK
515 | 323A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 10.1 | 11.6 | OK
516 | 323A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 41.3 | 46.2 | OK
517 | 324 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 47.0 | 52.5 | OK
518 | 324 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.7 | 32.4 | 36.4 | OK
519 | 324 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 11.7 | 13.5 | OK
520 | 324 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 47.0 | 52.5 | OK
521 | 324 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.4 | 47.2 | 52.6 | OK
522 | 324 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.8 | 32.5 | 36.4 | OK
523 | 324 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 11.8 | 13.4 | OK
524 | 324 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.4 | 47.2 | 52.6 | OK
525 | 324 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 47.4 | 52.7 | OK
526 | 324 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.8 | 32.8 | 36.5 | OK
527 | 324 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 12.0 | 13.4 | OK
528 | 324 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 47.4 | 52.7 | OK
529 | 325 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.3 | 49.2 | OK
530 | 325 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.1 | 30.5 | 33.9 | OK
531 | 325 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 11.3 | 12.6 | OK
532 | 325 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.3 | 49.2 | OK
533 | 325 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.2 | 49.1 | OK
534 | 325 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.1 | 30.5 | 33.9 | OK
535 | 325 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 11.3 | 12.5 | OK
536 | 325 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.2 | 49.1 | OK
537 | 325 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.1 | 49.0 | OK
538 | 325 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.1 | 30.3 | 33.7 | OK
539 | 325 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.2 | 12.4 | OK
540 | 325 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.1 | 49.0 | OK
541 | 326 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.7 | 50.8 | OK
542 | 326 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 31.6 | 35.2 | OK
543 | 326 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.8 | 13.1 | OK
544 | 326 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.7 | 50.8 | OK
545 | 326 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.9 | 51.0 | OK
546 | 326 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.5 | 31.7 | 35.2 | OK
547 | 326 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.7 | 13.0 | OK
548 | 326 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.9 | 51.0 | OK
549 | 326 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 46.2 | 51.6 | OK
550 | 326 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.1 | 31.8 | 35.7 | OK
551 | 326 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 11.5 | 13.2 | OK
552 | 326 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 46.2 | 51.6 | OK
553 | 327 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.1 | 50.4 | OK
554 | 327 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.5 | 30.0 | 35.0 | OK
555 | 327 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 10.3 | 13.5 | OK
556 | 327 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.1 | 50.4 | OK
557 | 327 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.5 | 43.7 | 49.4 | OK
558 | 327 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 29.9 | 34.2 | OK
559 | 327 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 10.5 | 12.9 | OK
560 | 327 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.5 | 43.7 | 49.4 | OK
561 | 327 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 43.5 | 48.3 | OK
562 | 327 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.2 | 30.0 | 33.3 | OK
563 | 327 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 11.2 | 12.5 | OK
564 | 327 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 43.5 | 48.3 | OK
565 | 328 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.9 | 45.5 | 50.6 | OK
566 | 328 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 31.5 | 35.0 | OK
567 | 328 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.8 | 13.2 | OK
568 | 328 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.9 | 45.5 | 50.6 | OK
569 | 328 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.9 | 51.0 | OK
570 | 328 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.9 | 31.8 | 35.3 | OK
571 | 328 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 12.0 | 13.3 | OK
572 | 328 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.9 | 51.0 | OK
573 | 328 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 45.9 | 51.3 | OK
574 | 328 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.9 | 31.6 | 35.5 | OK
575 | 328 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 11.4 | 13.2 | OK
576 | 328 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 45.9 | 51.3 | OK
577 | 329 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.5 | 50.5 | OK
578 | 329 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 31.4 | 34.9 | OK
579 | 329 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.6 | 12.9 | OK
580 | 329 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.5 | 50.5 | OK
581 | 329 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
582 | 329 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.2 | 34.7 | OK
583 | 329 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.4 | 12.7 | OK
584 | 329 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
585 | 329 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.5 | 50.5 | OK
586 | 329 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 31.4 | 34.9 | OK
587 | 329 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.6 | 12.9 | OK
588 | 329 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.5 | 50.5 | OK
589 | 330 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.4 | 50.6 | OK
590 | 330 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 31.3 | 34.9 | OK
591 | 330 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.4 | 12.8 | OK
592 | 330 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.4 | 50.6 | OK
593 | 330 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.3 | 50.7 | OK
594 | 330 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.5 | 31.1 | 35.1 | OK
595 | 330 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 11.2 | 13.0 | OK
596 | 330 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.3 | 50.7 | OK
597 | 330 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.4 | 50.7 | OK
598 | 330 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.5 | 31.2 | 35.0 | OK
599 | 330 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 11.3 | 12.9 | OK
600 | 330 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.4 | 50.7 | OK
601 | 331 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.6 | 50.9 | OK
602 | 331 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 31.4 | 35.2 | OK
603 | 331 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 11.4 | 13.0 | OK
604 | 331 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.6 | 50.9 | OK
605 | 331 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.8 | 50.9 | OK
606 | 331 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 31.6 | 35.1 | OK
607 | 331 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.7 | 13.0 | OK
608 | 331 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.5 | 45.8 | 50.9 | OK
609 | 331 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.6 | 50.8 | OK
610 | 331 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 31.4 | 35.1 | OK
611 | 331 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.4 | 12.9 | OK
612 | 331 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.6 | 50.8 | OK
613 | 332 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.3 | 49.3 | OK
614 | 332 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.5 | 30.5 | 33.9 | OK
615 | 332 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.1 | 12.4 | OK
616 | 332 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.3 | 49.3 | OK
617 | 332 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.2 | 49.4 | OK
618 | 332 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.6 | 30.3 | 34.0 | OK
619 | 332 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 10.9 | 12.6 | OK
620 | 332 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.2 | 49.4 | OK
621 | 332 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.4 | 49.4 | OK
622 | 332 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.4 | 30.6 | 34.0 | OK
623 | 332 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.2 | 12.5 | OK
624 | 332 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.4 | 49.4 | OK
625 | 333 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.4 | 50.7 | OK
626 | 333 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.5 | 31.2 | 35.0 | OK
627 | 333 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 11.3 | 13.0 | OK
628 | 333 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.4 | 50.7 | OK
629 | 333 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 45.8 | 51.0 | OK
630 | 333 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 31.5 | 35.2 | OK
631 | 333 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 11.4 | 13.0 | OK
632 | 333 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 45.8 | 51.0 | OK
633 | 333 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.3 | 50.9 | OK
634 | 333 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 31.1 | 35.2 | OK
635 | 333 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.1 | 13.1 | OK
636 | 333 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.3 | 50.9 | OK
637 | 334 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.1 | 40.5 | 53.5 | OK
638 | 334 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -35.0 | 25.6 | 38.9 | OK
639 | 334 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -16.4 | 5.6 | 18.2 | OK
640 | 334 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.1 | 40.5 | 53.5 | OK
641 | 334 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 40.4 | 52.5 | OK
642 | 334 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.1 | 25.7 | 37.9 | OK
643 | 334 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.6 | 6.1 | 17.4 | OK
644 | 334 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 40.4 | 52.5 | OK
645 | 334 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.8 | 40.7 | 53.1 | OK
646 | 334 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.7 | 25.9 | 38.5 | OK
647 | 334 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -16.0 | 6.0 | 17.8 | OK
648 | 334 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.8 | 40.7 | 53.1 | OK
649 | 335 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 44.1 | 50.1 | OK
650 | 335 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 30.1 | 34.8 | OK
651 | 335 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 10.5 | 13.3 | OK
652 | 335 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 44.1 | 50.1 | OK
653 | 335 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.4 | 50.4 | OK
654 | 335 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 30.3 | 34.9 | OK
655 | 335 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 10.6 | 13.3 | OK
656 | 335 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.4 | 50.4 | OK
657 | 335 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.1 | 50.2 | OK
658 | 335 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 30.0 | 34.9 | OK
659 | 335 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 10.4 | 13.3 | OK
660 | 335 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.1 | 50.2 | OK
661 | 336 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.5 | 50.5 | OK
662 | 336 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.9 | 31.4 | 34.9 | OK
663 | 336 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.7 | 13.0 | OK
664 | 336 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.5 | 50.5 | OK
665 | 336 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.5 | 50.5 | OK
666 | 336 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.4 | 34.8 | OK
667 | 336 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.5 | 12.8 | OK
668 | 336 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.5 | 50.5 | OK
669 | 336 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.4 | 50.4 | OK
670 | 336 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.3 | 34.8 | OK
671 | 336 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.5 | 12.8 | OK
672 | 336 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.4 | 50.4 | OK
673 | 337 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.1 | 42.8 | 47.5 | OK
674 | 337 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.6 | 29.5 | 32.7 | OK
675 | 337 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 11.0 | 12.3 | OK
676 | 337 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.1 | 42.8 | 47.5 | OK
677 | 337 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 43.6 | 48.5 | OK
678 | 337 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 30.2 | 33.5 | OK
679 | 337 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 11.4 | 12.7 | OK
680 | 337 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 43.6 | 48.5 | OK
681 | 337 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 43.3 | 48.4 | OK
682 | 337 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 29.6 | 33.3 | OK
683 | 337 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 10.7 | 12.3 | OK
684 | 337 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 43.3 | 48.4 | OK
685 | 339 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 43.6 | 48.5 | OK
686 | 339 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.1 | 30.1 | 33.5 | OK
687 | 339 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.2 | 11.4 | 12.6 | OK
688 | 339 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 43.6 | 48.5 | OK
689 | 339 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 44.1 | 49.0 | OK
690 | 339 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.7 | 30.5 | 33.9 | OK
691 | 339 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 11.4 | 12.7 | OK
692 | 339 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 44.1 | 49.0 | OK
693 | 339 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.9 | 49.2 | OK
694 | 339 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.5 | 30.1 | 33.9 | OK
695 | 339 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 10.8 | 12.6 | OK
696 | 339 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 43.9 | 49.2 | OK
697 | 340 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.7 | 48.6 | OK
698 | 340 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 30.0 | 33.4 | OK
699 | 340 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.0 | 12.2 | OK
700 | 340 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.7 | 48.6 | OK
701 | 340 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.8 | 43.9 | 48.8 | OK
702 | 340 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 30.2 | 33.6 | OK
703 | 340 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.1 | 12.3 | OK
704 | 340 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.8 | 43.9 | 48.8 | OK
705 | 340 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.8 | 48.7 | OK
706 | 340 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.9 | 30.1 | 33.5 | OK
707 | 340 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 11.1 | 12.3 | OK
708 | 340 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.8 | 48.7 | OK
709 | 341 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
710 | 341 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.3 | 34.7 | OK
711 | 341 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.5 | 12.7 | OK
712 | 341 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
713 | 341 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
714 | 341 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 31.3 | 34.7 | OK
715 | 341 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.5 | 12.7 | OK
716 | 341 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 45.3 | 50.4 | OK
717 | 341 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.4 | 50.4 | OK
718 | 341 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.3 | 34.8 | OK
719 | 341 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.5 | 12.8 | OK
720 | 341 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.4 | 50.4 | OK
721 | 342 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.2 | 50.8 | OK
722 | 342 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 31.0 | 35.2 | OK
723 | 342 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.1 | 13.2 | OK
724 | 342 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.2 | 50.8 | OK
725 | 342 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.3 | 50.8 | OK
726 | 342 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 31.1 | 35.2 | OK
727 | 342 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.1 | 13.1 | OK
728 | 342 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.3 | 50.8 | OK
729 | 342 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 45.2 | 51.1 | OK
730 | 342 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.9 | 30.9 | 35.4 | OK
731 | 342 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 10.9 | 13.4 | OK
732 | 342 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 45.2 | 51.1 | OK
733 | 343 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.6 | 39.6 | 44.0 | OK
734 | 343 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.0 | 27.2 | 30.3 | OK
735 | 343 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.0 | 10.3 | 11.5 | OK
736 | 343 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.6 | 39.6 | 44.0 | OK
737 | 343 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.9 | 40.8 | 45.3 | OK
738 | 343 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.0 | 28.0 | 31.1 | OK
739 | 343 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.4 | 10.6 | 11.7 | OK
740 | 343 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.9 | 40.8 | 45.3 | OK
741 | 343 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.1 | 40.4 | 45.7 | OK
742 | 343 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.3 | 27.4 | 31.4 | OK
743 | 343 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.6 | 9.6 | 11.8 | OK
744 | 343 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.1 | 40.4 | 45.7 | OK
745 | 344 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.1 | 39.7 | 44.1 | OK
746 | 344 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.5 | 27.3 | 30.3 | OK
747 | 344 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.5 | 10.5 | 11.7 | OK
748 | 344 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.1 | 39.7 | 44.1 | OK
749 | 344 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.8 | 45.0 | 50.0 | OK
750 | 344 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -22.0 | 32.9 | 36.6 | OK
751 | 344 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -3.8 | 16.0 | 17.8 | OK
752 | 344 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.8 | 45.0 | 50.0 | OK
753 | 344 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 39.9 | 46.1 | OK
754 | 344 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.7 | 26.7 | 31.9 | OK
755 | 344 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 8.9 | 12.4 | OK
756 | 344 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.5 | 39.9 | 46.1 | OK
757 | 345 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -33.2 | 49.1 | 54.6 | OK
758 | 345 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -18.2 | 37.5 | 41.6 | OK
759 | 345 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 0.9 | 21.0 | 23.3 | OK
760 | 345 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -33.2 | 49.1 | 54.6 | OK
761 | 345 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -33.2 | 49.5 | 55.0 | OK
762 | 345 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -18.0 | 37.8 | 42.0 | OK
763 | 345 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 1.2 | 21.3 | 23.7 | OK
764 | 345 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -33.2 | 49.5 | 55.0 | OK
765 | 345 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 41.9 | 46.5 | OK
766 | 345 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.3 | 28.6 | 31.8 | OK
767 | 345 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 10.5 | 11.6 | OK
768 | 345 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 41.9 | 46.5 | OK
769 | 346 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 41.6 | 46.3 | OK
770 | 346 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.5 | 28.6 | 31.7 | OK
771 | 346 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 10.5 | 11.6 | OK
772 | 346 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 41.6 | 46.3 | OK
773 | 346 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.4 | 46.4 | 51.6 | OK
774 | 346 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -23.3 | 34.1 | 37.9 | OK
775 | 346 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -4.3 | 16.6 | 18.4 | OK
776 | 346 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.4 | 46.4 | 51.6 | OK
777 | 346 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 41.1 | 46.5 | OK
778 | 346 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.9 | 28.0 | 32.1 | OK
779 | 346 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 9.9 | 12.1 | OK
780 | 346 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 41.1 | 46.5 | OK
781 | 346A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -63.8 | 63.9 | 71.0 | OK
782 | 346A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 47.1 | 52.4 | OK
783 | 346A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -17.9 | 18.7 | 20.8 | OK
784 | 346A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -63.8 | 63.9 | 71.0 | OK
785 | 346A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -61.5 | 62.1 | 69.0 | OK
786 | 346A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -44.2 | 45.3 | 50.4 | OK
787 | 346A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -16.3 | 18.0 | 20.0 | OK
788 | 346A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -61.5 | 62.1 | 69.0 | OK
789 | 346A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -64.0 | 64.9 | 72.1 | OK
790 | 346A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 48.4 | 53.8 | OK
791 | 346A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -16.9 | 20.3 | 22.6 | OK
792 | 346A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -64.0 | 64.9 | 72.1 | OK
793 | 347 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 40.0 | 45.5 | OK
794 | 347 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.3 | 27.2 | 31.5 | OK
795 | 347 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 9.5 | 12.0 | OK
796 | 347 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 40.0 | 45.5 | OK
797 | 347 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.3 | 45.6 | OK
798 | 347 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.3 | 27.4 | 31.5 | OK
799 | 347 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.7 | 9.7 | 11.8 | OK
800 | 347 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.3 | 45.6 | OK
801 | 347 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 39.7 | 45.5 | OK
802 | 347 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.4 | 27.0 | 31.5 | OK
803 | 347 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 9.4 | 12.1 | OK
804 | 347 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 39.7 | 45.5 | OK
805 | 348 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.7 | 49.6 | OK
806 | 348 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.7 | 30.7 | 34.2 | OK
807 | 348 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.2 | 12.5 | OK
808 | 348 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.7 | 49.6 | OK
809 | 348 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.7 | 49.7 | OK
810 | 348 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.7 | 30.8 | 34.2 | OK
811 | 348 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.2 | 12.5 | OK
812 | 348 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.7 | 44.7 | 49.7 | OK
813 | 348 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 44.6 | 49.7 | OK
814 | 348 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 30.6 | 34.3 | OK
815 | 348 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.1 | 12.6 | OK
816 | 348 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 44.6 | 49.7 | OK
817 | 349 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.0 | 47.0 | 53.4 | OK
818 | 349 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.6 | 32.3 | 37.3 | OK
819 | 349 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.9 | 11.3 | 14.3 | OK
820 | 349 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.0 | 47.0 | 53.4 | OK
821 | 349 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.1 | 47.2 | 53.4 | OK
822 | 349 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.6 | 32.4 | 37.3 | OK
823 | 349 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.8 | 11.4 | 14.2 | OK
824 | 349 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.1 | 47.2 | 53.4 | OK
825 | 349 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.2 | 47.0 | 53.6 | OK
826 | 349 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.8 | 32.2 | 37.6 | OK
827 | 349 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.1 | 11.2 | 14.5 | OK
828 | 349 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.2 | 47.0 | 53.6 | OK
829 | 350 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.9 | 32.2 | 54.3 | OK
830 | 350 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -37.5 | 17.5 | 41.7 | OK
831 | 350 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -21.2 | -1.3 | 23.5 | OK
832 | 350 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.9 | 32.2 | 54.3 | OK
833 | 350 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.4 | 33.3 | 53.8 | OK
834 | 350 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 18.8 | 40.8 | OK
835 | 350 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -20.1 | 0.0 | 22.3 | OK
836 | 350 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.4 | 33.3 | 53.8 | OK
837 | 350 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -49.8 | 32.6 | 55.4 | OK
838 | 350 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -38.4 | 17.6 | 42.6 | OK
839 | 350 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -21.9 | -1.7 | 24.3 | OK
840 | 350 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -49.8 | 32.6 | 55.4 | OK
841 | 351 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 45.1 | 52.1 | OK
842 | 351 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.9 | 30.6 | 36.5 | OK
843 | 351 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.0 | 10.2 | 14.4 | OK
844 | 351 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 45.1 | 52.1 | OK
845 | 351 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 44.7 | 51.3 | OK
846 | 351 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 30.4 | 35.8 | OK
847 | 351 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.5 | 10.4 | 13.9 | OK
848 | 351 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 44.7 | 51.3 | OK
849 | 351 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 44.2 | 49.1 | OK
850 | 351 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 30.4 | 33.7 | OK
851 | 351 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 11.1 | 12.4 | OK
852 | 351 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 44.2 | 49.1 | OK
853 | 352 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.3 | 46.8 | 52.0 | OK
854 | 352 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 32.5 | 36.1 | OK
855 | 352 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 12.1 | 13.5 | OK
856 | 352 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.3 | 46.8 | 52.0 | OK
857 | 352 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 46.8 | 52.0 | OK
858 | 352 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 32.4 | 36.0 | OK
859 | 352 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.9 | 13.2 | OK
860 | 352 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 46.8 | 52.0 | OK
861 | 352 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.9 | 47.2 | 53.2 | OK
862 | 352 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.4 | 32.5 | 37.1 | OK
863 | 352 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.7 | 11.5 | 14.1 | OK
864 | 352 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.9 | 47.2 | 53.2 | OK
865 | 353A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -23.5 | 34.2 | 38.0 | OK
866 | 353A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -13.7 | 25.1 | 27.8 | OK
867 | 353A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -1.1 | 12.9 | 14.3 | OK
868 | 353A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -23.5 | 34.2 | 38.0 | OK
869 | 353A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -27.8 | 27.9 | 30.9 | OK
870 | 353A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -18.8 | 18.8 | 20.9 | OK
871 | 353A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -6.7 | 6.9 | 7.6 | OK
872 | 353A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -27.8 | 27.9 | 30.9 | OK
873 | 353A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -27.6 | 30.6 | 34.0 | OK
874 | 353A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -18.0 | 21.2 | 23.5 | OK
875 | 353A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -5.4 | 8.7 | 9.7 | OK
876 | 353A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -27.6 | 30.6 | 34.0 | OK
877 | 354 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.3 | 41.7 | 46.4 | OK
878 | 354 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -22.5 | 29.9 | 33.2 | OK
879 | 354 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -5.4 | 13.5 | 15.0 | OK
880 | 354 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.3 | 41.7 | 46.4 | OK
881 | 354 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.3 | 35.5 | 41.5 | OK
882 | 354 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.7 | 23.7 | 28.6 | OK
883 | 354 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 7.8 | 11.1 | OK
884 | 354 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.3 | 35.5 | 41.5 | OK
885 | 354 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 39.4 | 43.8 | OK
886 | 354 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.4 | 27.4 | 30.4 | OK
887 | 354 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.7 | 11.0 | 12.2 | OK
888 | 354 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 39.4 | 43.8 | OK
889 | 355A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.1 | 41.0 | 45.5 | OK
890 | 355A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.0 | 28.1 | 31.2 | OK
891 | 355A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.4 | 10.5 | 11.7 | OK
892 | 355A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.1 | 41.0 | 45.5 | OK
893 | 355A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.5 | 40.2 | 44.6 | OK
894 | 355A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.7 | 27.7 | 30.8 | OK
895 | 355A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.6 | 10.7 | 11.9 | OK
896 | 355A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.5 | 40.2 | 44.6 | OK
897 | 355A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.3 | 39.3 | 45.9 | OK
898 | 355A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.6 | 26.2 | 31.8 | OK
899 | 355A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 8.6 | 12.5 | OK
900 | 355A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.3 | 39.3 | 45.9 | OK
901 | 356 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 47.2 | 52.9 | OK
902 | 356 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.1 | 32.5 | 36.7 | OK
903 | 356 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.4 | 11.7 | 13.7 | OK
904 | 356 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 47.2 | 52.9 | OK
905 | 356 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.6 | 47.6 | 54.0 | OK
906 | 356 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.0 | 32.7 | 37.8 | OK
907 | 356 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.1 | 11.4 | 14.5 | OK
908 | 356 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.6 | 47.6 | 54.0 | OK
909 | 356 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.1 | 48.0 | 53.4 | OK
910 | 356 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 33.5 | 37.3 | OK
911 | 356 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 12.8 | 14.2 | OK
912 | 356 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.1 | 48.0 | 53.4 | OK
913 | 357 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.8 | 49.7 | OK
914 | 357 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.4 | 30.9 | 34.3 | OK
915 | 357 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.5 | 12.7 | OK
916 | 357 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.8 | 49.7 | OK
917 | 357 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.2 | 44.8 | 49.8 | OK
918 | 357 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 31.0 | 34.4 | OK
919 | 357 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.7 | 11.6 | 12.9 | OK
920 | 357 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.2 | 44.8 | 49.8 | OK
921 | 357 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.7 | 49.6 | OK
922 | 357 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.3 | 30.8 | 34.2 | OK
923 | 357 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 11.4 | 12.7 | OK
924 | 357 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.7 | 49.6 | OK
925 | 358 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.0 | 46.4 | 52.2 | OK
926 | 358 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.6 | 31.8 | 36.2 | OK
927 | 358 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.3 | 11.3 | 13.6 | OK
928 | 358 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.0 | 46.4 | 52.2 | OK
929 | 358 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 49.6 | 55.1 | OK
930 | 358 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.0 | 36.1 | 40.1 | OK
931 | 358 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -6.9 | 16.5 | 18.4 | OK
932 | 358 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 49.6 | 55.1 | OK
933 | 358 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 46.5 | 52.1 | OK
934 | 358 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.5 | 32.0 | 36.1 | OK
935 | 358 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 11.5 | 13.4 | OK
936 | 358 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 46.5 | 52.1 | OK
937 | 359A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.0 | 46.3 | 51.5 | OK
938 | 359A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -20.9 | 34.4 | 38.2 | OK
939 | 359A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -2.5 | 17.5 | 19.5 | OK
940 | 359A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.0 | 46.3 | 51.5 | OK
941 | 359A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 47.4 | 52.7 | OK
942 | 359A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -22.3 | 35.1 | 39.0 | OK
943 | 359A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -3.1 | 17.7 | 19.7 | OK
944 | 359A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 47.4 | 52.7 | OK
945 | 359A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -51.2 | 24.5 | 56.9 | OK
946 | 359A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 9.7 | 45.6 | OK
947 | 359A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -26.4 | -8.2 | 29.3 | OK
948 | 359A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -51.2 | 24.5 | 56.9 | OK
949 | 359 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 36.8 | 42.4 | OK
950 | 359 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.2 | 24.7 | 29.1 | OK
951 | 359 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 8.4 | 11.1 | OK
952 | 359 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 36.8 | 42.4 | OK
953 | 359 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -6.2 | 52.6 | 58.4 | OK
954 | 359 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | 4.9 | 44.1 | 49.0 | OK
955 | 359 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 18.3 | 32.3 | 35.9 | OK
956 | 359 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -6.2 | 52.6 | 58.4 | OK
957 | 359 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -34.0 | 35.4 | 39.4 | OK
958 | 359 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -22.7 | 24.3 | 27.1 | OK
959 | 359 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.6 | 9.4 | 10.5 | OK
960 | 359 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -34.0 | 35.4 | 39.4 | OK
961 | 360 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 47.7 | 53.0 | OK
962 | 360 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.6 | 33.1 | 36.8 | OK
963 | 360 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 12.4 | 13.7 | OK
964 | 360 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 47.7 | 53.0 | OK
965 | 360 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 48.1 | 53.4 | OK
966 | 360 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.0 | 33.1 | 36.8 | OK
967 | 360 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.4 | 11.9 | 13.7 | OK
968 | 360 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 48.1 | 53.4 | OK
969 | 360 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -49.5 | 48.7 | 55.0 | OK
970 | 360 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.6 | 33.6 | 38.4 | OK
971 | 360 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.1 | 12.0 | 14.6 | OK
972 | 360 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -49.5 | 48.7 | 55.0 | OK
973 | 361 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 46.3 | 52.1 | OK
974 | 361 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.5 | 31.8 | 36.1 | OK
975 | 361 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.2 | 11.4 | 13.6 | OK
976 | 361 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 46.3 | 52.1 | OK
977 | 361 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 46.5 | 51.8 | OK
978 | 361 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 32.1 | 35.8 | OK
979 | 361 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 11.7 | 13.2 | OK
980 | 361 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 46.5 | 51.8 | OK
981 | 361 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 46.1 | 51.6 | OK
982 | 361 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 31.7 | 35.7 | OK
983 | 361 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 11.5 | 13.3 | OK
984 | 361 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 46.1 | 51.6 | OK
985 | 362 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.1 | 46.1 | 51.2 | OK
986 | 362 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 31.8 | 35.3 | OK
987 | 362 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.6 | 12.9 | OK
988 | 362 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.1 | 46.1 | 51.2 | OK
989 | 362 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 46.0 | 51.1 | OK
990 | 362 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.5 | 31.8 | 35.3 | OK
991 | 362 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.8 | 13.1 | OK
992 | 362 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 46.0 | 51.1 | OK
993 | 362 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.8 | 50.9 | OK
994 | 362 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 31.6 | 35.1 | OK
995 | 362 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.6 | 12.9 | OK
996 | 362 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.8 | 50.9 | OK
997 | 363 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.3 | 43.3 | 48.1 | OK
998 | 363 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.7 | 29.9 | 33.2 | OK
999 | 363 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 11.3 | 12.6 | OK
1000 | 363 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.3 | 43.3 | 48.1 | OK
1001 | 363 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 44.3 | 49.3 | OK
1002 | 363 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.7 | 30.6 | 34.1 | OK
1003 | 363 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 11.6 | 12.8 | OK
1004 | 363 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 44.3 | 49.3 | OK
1005 | 363 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 44.4 | 50.8 | OK
1006 | 363 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 30.2 | 35.4 | OK
1007 | 363 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.3 | 10.4 | 13.6 | OK
1008 | 363 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 44.4 | 50.8 | OK
1009 | 364 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -33.9 | 35.4 | 39.3 | OK
1010 | 364 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -22.6 | 24.3 | 27.0 | OK
1011 | 364 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.6 | 9.4 | 10.4 | OK
1012 | 364 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -33.9 | 35.4 | 39.3 | OK
1013 | 364 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.5 | 36.7 | 40.8 | OK
1014 | 364 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -23.8 | 25.1 | 27.9 | OK
1015 | 364 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.1 | 9.6 | 10.6 | OK
1016 | 364 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.5 | 36.7 | 40.8 | OK
1017 | 364 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.5 | 36.7 | 40.8 | OK
1018 | 364 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -23.8 | 25.2 | 28.0 | OK
1019 | 364 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.1 | 9.6 | 10.7 | OK
1020 | 364 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.5 | 36.7 | 40.8 | OK
1021 | 365A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 43.8 | 48.7 | OK
1022 | 365A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.7 | 30.0 | 33.4 | OK
1023 | 365A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.7 | 11.0 | 12.3 | OK
1024 | 365A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 43.8 | 48.7 | OK
1025 | 365A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 43.4 | 48.2 | OK
1026 | 365A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.9 | 29.9 | 33.2 | OK
1027 | 365A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 11.2 | 12.5 | OK
1028 | 365A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 43.4 | 48.2 | OK
1029 | 365A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 43.1 | 49.4 | OK
1030 | 365A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 29.1 | 34.2 | OK
1031 | 365A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 9.9 | 13.1 | OK
1032 | 365A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 43.1 | 49.4 | OK
1033 | 366A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -53.4 | 53.6 | 59.6 | OK
1034 | 366A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -37.4 | 37.6 | 41.8 | OK
1035 | 366A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.8 | 14.0 | 15.6 | OK
1036 | 366A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -53.4 | 53.6 | 59.6 | OK
1037 | 366A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -52.9 | 53.6 | 59.6 | OK
1038 | 366A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 37.7 | 41.9 | OK
1039 | 366A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.2 | 14.4 | 16.0 | OK
1040 | 366A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -52.9 | 53.6 | 59.6 | OK
1041 | 366A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -53.8 | 52.8 | 59.8 | OK
1042 | 366A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -38.1 | 36.5 | 42.3 | OK
1043 | 366A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -14.9 | 12.7 | 16.5 | OK
1044 | 366A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -53.8 | 52.8 | 59.8 | OK
1045 | 367 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.2 | 35.7 | 40.2 | OK
1046 | 367 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.6 | 24.1 | 27.3 | OK
1047 | 367 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.0 | 8.6 | 10.0 | OK
1048 | 367 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.2 | 35.7 | 40.2 | OK
1049 | 367 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.4 | 35.4 | 40.4 | OK
1050 | 367 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.9 | 23.8 | 27.6 | OK
1051 | 367 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.3 | 8.3 | 10.4 | OK
1052 | 367 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.4 | 35.4 | 40.4 | OK
1053 | 367 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.5 | 36.6 | 40.6 | OK
1054 | 367 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -23.8 | 25.0 | 27.8 | OK
1055 | 367 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.2 | 9.5 | 10.6 | OK
1056 | 367 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -35.5 | 36.6 | 40.6 | OK
1057 | 368 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 45.5 | 52.7 | OK
1058 | 368 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.1 | 31.0 | 36.8 | OK
1059 | 368 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.9 | 10.7 | 14.3 | OK
1060 | 368 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.5 | 45.5 | 52.7 | OK
1061 | 368 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.2 | 46.4 | 53.6 | OK
1062 | 368 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.7 | 31.7 | 37.5 | OK
1063 | 368 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.0 | 11.0 | 14.5 | OK
1064 | 368 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.2 | 46.4 | 53.6 | OK
1065 | 368 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 45.3 | 52.9 | OK
1066 | 368 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.3 | 30.8 | 37.0 | OK
1067 | 368 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.1 | 10.3 | 14.6 | OK
1068 | 368 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 45.3 | 52.9 | OK
1069 | 369 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -66.0 | -23.4 | 73.3 | OK
1070 | 369 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -59.4 | -30.9 | 66.0 | OK
1071 | 369 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -50.3 | -40.0 | 55.9 | OK
1072 | 369 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -66.0 | -23.4 | 73.3 | OK
1073 | 369 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -65.6 | -21.2 | 72.9 | OK
1074 | 369 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -58.8 | -29.1 | 65.3 | OK
1075 | 369 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -49.4 | -38.7 | 54.9 | OK
1076 | 369 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -65.6 | -21.2 | 72.9 | OK
1077 | 369 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -65.3 | -20.0 | 72.6 | OK
1078 | 369 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -58.5 | -28.2 | 64.9 | OK
1079 | 369 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -48.9 | -38.0 | 54.4 | OK
1080 | 369 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -65.3 | -20.0 | 72.6 | OK
1081 | 370A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 41.3 | 51.5 | OK
1082 | 370A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.0 | 27.1 | 36.6 | OK
1083 | 370A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -14.2 | 7.6 | 15.8 | OK
1084 | 370A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 41.3 | 51.5 | OK
1085 | 370A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 41.5 | 51.0 | OK
1086 | 370A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.4 | 27.4 | 36.1 | OK
1087 | 370A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.7 | 8.0 | 15.2 | OK
1088 | 370A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 41.5 | 51.0 | OK
1089 | 370A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.0 | 40.6 | 52.2 | OK
1090 | 370A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.7 | 26.2 | 37.5 | OK
1091 | 370A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.1 | 6.7 | 16.8 | OK
1092 | 370A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.0 | 40.6 | 52.2 | OK
1093 | 371A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 46.8 | 52.0 | OK
1094 | 371A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.1 | 32.3 | 35.8 | OK
1095 | 371A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.9 | 13.2 | OK
1096 | 371A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 46.8 | 52.0 | OK
1097 | 371A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.3 | 51.5 | OK
1098 | 371A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 32.0 | 35.5 | OK
1099 | 371A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.9 | 13.2 | OK
1100 | 371A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.3 | 51.5 | OK
1101 | 371A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 46.2 | 52.5 | OK
1102 | 371A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.9 | 31.5 | 36.5 | OK
1103 | 371A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.6 | 10.9 | 14.0 | OK
1104 | 371A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 46.2 | 52.5 | OK
1105 | 372 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 45.8 | 51.7 | OK
1106 | 372 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 31.3 | 35.9 | OK
1107 | 372 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.2 | 11.1 | 13.6 | OK
1108 | 372 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 45.8 | 51.7 | OK
1109 | 372 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 46.7 | 53.0 | OK
1110 | 372 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.3 | 31.9 | 37.0 | OK
1111 | 372 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.7 | 11.2 | 14.2 | OK
1112 | 372 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.7 | 46.7 | 53.0 | OK
1113 | 372 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 46.8 | 52.0 | OK
1114 | 372 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.5 | 32.8 | 36.4 | OK
1115 | 372 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 12.9 | 14.3 | OK
1116 | 372 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 46.8 | 52.0 | OK
1117 | 373A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.4 | 42.8 | 47.5 | OK
1118 | 373A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.8 | 29.2 | 32.5 | OK
1119 | 373A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 10.7 | 11.9 | OK
1120 | 373A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.4 | 42.8 | 47.5 | OK
1121 | 373A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 46.2 | 51.3 | OK
1122 | 373A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -22.7 | 33.8 | 37.6 | OK
1123 | 373A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -4.0 | 16.4 | 18.3 | OK
1124 | 373A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.8 | 46.2 | 51.3 | OK
1125 | 373A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 41.4 | 48.3 | OK
1126 | 373A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 27.7 | 33.5 | OK
1127 | 373A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 9.1 | 13.2 | OK
1128 | 373A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.5 | 41.4 | 48.3 | OK
1129 | 374 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -21.7 | 57.0 | 63.4 | OK
1130 | 374 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -5.5 | 47.0 | 52.2 | OK
1131 | 374 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 13.5 | 32.2 | 35.8 | OK
1132 | 374 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -21.7 | 57.0 | 63.4 | OK
1133 | 374 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -25.2 | 58.2 | 64.7 | OK
1134 | 374 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -7.9 | 47.7 | 53.0 | OK
1135 | 374 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 12.4 | 32.2 | 35.8 | OK
1136 | 374 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -25.2 | 58.2 | 64.7 | OK
1137 | 374 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.5 | 51.0 | 56.7 | OK
1138 | 374 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -21.9 | 38.6 | 42.9 | OK
1139 | 374 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -1.3 | 20.6 | 22.9 | OK
1140 | 374 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.5 | 51.0 | 56.7 | OK
1141 | 375 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 44.5 | 52.9 | OK
1142 | 375 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.8 | 29.7 | 37.5 | OK
1143 | 375 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -14.0 | 9.2 | 15.6 | OK
1144 | 375 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 44.5 | 52.9 | OK
1145 | 375 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 48.4 | 53.8 | OK
1146 | 375 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.0 | 35.1 | 39.0 | OK
1147 | 375 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -6.6 | 16.1 | 17.8 | OK
1148 | 375 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 48.4 | 53.8 | OK
1149 | 375 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 43.7 | 48.6 | OK
1150 | 375 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.5 | 30.1 | 33.5 | OK
1151 | 375 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 11.2 | 12.4 | OK
1152 | 375 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 43.7 | 48.6 | OK
1153 | 376 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 45.1 | 50.1 | OK
1154 | 376 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 31.3 | 34.7 | OK
1155 | 376 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 11.9 | 13.2 | OK
1156 | 376 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 45.1 | 50.1 | OK
1157 | 376 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.5 | 45.5 | 50.5 | OK
1158 | 376 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.3 | 31.6 | 35.1 | OK
1159 | 376 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.6 | 12.0 | 13.4 | OK
1160 | 376 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.5 | 45.5 | 50.5 | OK
1161 | 376 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.3 | 50.6 | OK
1162 | 376 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 31.2 | 34.9 | OK
1163 | 376 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.3 | 12.9 | OK
1164 | 376 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 45.3 | 50.6 | OK
1165 | 377 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.2 | 50.3 | OK
1166 | 377 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.2 | 34.6 | OK
1167 | 377 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.4 | 12.7 | OK
1168 | 377 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.2 | 50.3 | OK
1169 | 377 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.4 | 50.5 | OK
1170 | 377 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 31.4 | 34.9 | OK
1171 | 377 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.6 | 12.9 | OK
1172 | 377 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.4 | 50.5 | OK
1173 | 377 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.2 | 50.2 | OK
1174 | 377 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 31.1 | 34.6 | OK
1175 | 377 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.4 | 12.7 | OK
1176 | 377 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 45.2 | 50.2 | OK
1177 | 378 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.2 | 40.8 | 45.3 | OK
1178 | 378 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.3 | 28.2 | 31.3 | OK
1179 | 378 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.9 | 10.9 | 12.1 | OK
1180 | 378 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.2 | 40.8 | 45.3 | OK
1181 | 378 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.3 | 41.8 | 46.4 | OK
1182 | 378 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.1 | 28.9 | 32.1 | OK
1183 | 378 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.2 | 11.1 | 12.4 | OK
1184 | 378 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.3 | 41.8 | 46.4 | OK
1185 | 378 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 41.6 | 46.6 | OK
1186 | 378 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.8 | 28.3 | 32.0 | OK
1187 | 378 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.6 | 10.1 | 11.8 | OK
1188 | 378 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 41.6 | 46.6 | OK
1189 | 379 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.9 | 38.6 | 42.9 | OK
1190 | 379 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.6 | 26.6 | 29.6 | OK
1191 | 379 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.2 | 10.4 | 11.5 | OK
1192 | 379 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.9 | 38.6 | 42.9 | OK
1193 | 379 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.9 | 39.8 | 44.2 | OK
1194 | 379 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.4 | 27.5 | 30.6 | OK
1195 | 379 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.4 | 10.8 | 12.0 | OK
1196 | 379 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -37.9 | 39.8 | 44.2 | OK
1197 | 379 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.6 | 39.2 | 44.0 | OK
1198 | 379 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.1 | 26.6 | 30.1 | OK
1199 | 379 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 9.4 | 11.1 | OK
1200 | 379 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.6 | 39.2 | 44.0 | OK
1201 | 380 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.8 | 50.2 | OK
1202 | 380 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 30.7 | 34.7 | OK
1203 | 380 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.0 | 12.9 | OK
1204 | 380 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.8 | 50.2 | OK
1205 | 380 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 44.9 | 50.1 | OK
1206 | 380 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 30.9 | 34.5 | OK
1207 | 380 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.2 | 12.7 | OK
1208 | 380 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 44.9 | 50.1 | OK
1209 | 380 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.8 | 50.3 | OK
1210 | 380 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 30.7 | 34.8 | OK
1211 | 380 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 11.0 | 13.0 | OK
1212 | 380 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.3 | 44.8 | 50.3 | OK
1213 | 381 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 46.7 | 52.6 | OK
1214 | 381 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.9 | 32.1 | 36.6 | OK
1215 | 381 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.4 | 11.4 | 13.8 | OK
1216 | 381 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.3 | 46.7 | 52.6 | OK
1217 | 381 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.2 | 46.9 | 53.5 | OK
1218 | 381 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.7 | 32.1 | 37.4 | OK
1219 | 381 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.0 | 11.1 | 14.5 | OK
1220 | 381 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -48.2 | 46.9 | 53.5 | OK
1221 | 381 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 47.4 | 52.7 | OK
1222 | 381 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 33.0 | 36.6 | OK
1223 | 381 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 12.4 | 13.8 | OK
1224 | 381 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.8 | 47.4 | 52.7 | OK
1225 | 382A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.3 | 41.8 | 46.5 | OK
1226 | 382A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.0 | 28.6 | 31.8 | OK
1227 | 382A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.9 | 10.6 | 11.8 | OK
1228 | 382A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.3 | 41.8 | 46.5 | OK
1229 | 382A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.7 | 41.6 | 46.3 | OK
1230 | 382A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.5 | 28.6 | 31.8 | OK
1231 | 382A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.5 | 10.8 | 12.0 | OK
1232 | 382A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.7 | 41.6 | 46.3 | OK
1233 | 382A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 41.1 | 46.5 | OK
1234 | 382A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.7 | 27.8 | 31.9 | OK
1235 | 382A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 9.7 | 11.9 | OK
1236 | 382A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.9 | 41.1 | 46.5 | OK
1237 | 383A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.7 | 49.7 | OK
1238 | 383A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 30.8 | 34.2 | OK
1239 | 383A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.7 | 11.4 | 12.7 | OK
1240 | 383A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 44.7 | 49.7 | OK
1241 | 383A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 44.4 | 49.3 | OK
1242 | 383A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.4 | 30.6 | 34.0 | OK
1243 | 383A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.2 | 11.6 | 12.9 | OK
1244 | 383A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 44.4 | 49.3 | OK
1245 | 383A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.9 | 44.0 | 49.9 | OK
1246 | 383A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 29.9 | 34.4 | OK
1247 | 383A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 10.4 | 13.0 | OK
1248 | 383A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.9 | 44.0 | 49.9 | OK
1249 | 384 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 46.2 | 52.4 | OK
1250 | 384 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.9 | 31.6 | 36.5 | OK
1251 | 384 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.6 | 11.1 | 14.0 | OK
1252 | 384 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 46.2 | 52.4 | OK
1253 | 384 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.9 | 46.5 | 53.3 | OK
1254 | 384 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.6 | 31.7 | 37.3 | OK
1255 | 384 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.1 | 10.9 | 14.5 | OK
1256 | 384 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.9 | 46.5 | 53.3 | OK
1257 | 384 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 47.1 | 52.3 | OK
1258 | 384 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.0 | 32.7 | 36.3 | OK
1259 | 384 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 12.2 | 13.6 | OK
1260 | 384 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 47.1 | 52.3 | OK
1261 | 385 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 43.9 | 48.8 | OK
1262 | 385 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.1 | 30.4 | 33.8 | OK
1263 | 385 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 11.6 | 12.9 | OK
1264 | 385 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 43.9 | 48.8 | OK
1265 | 385 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 44.1 | 49.0 | OK
1266 | 385 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.4 | 30.5 | 33.9 | OK
1267 | 385 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 11.5 | 12.8 | OK
1268 | 385 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 44.1 | 49.0 | OK
1269 | 385 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 43.7 | 48.6 | OK
1270 | 385 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.2 | 30.2 | 33.6 | OK
1271 | 385 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 11.4 | 12.7 | OK
1272 | 385 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.9 | 43.7 | 48.6 | OK
1273 | 386 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.8 | 50.2 | OK
1274 | 386 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 30.7 | 34.7 | OK
1275 | 386 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.0 | 12.9 | OK
1276 | 386 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.8 | 50.2 | OK
1277 | 386 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.8 | 50.0 | OK
1278 | 386 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 30.7 | 34.5 | OK
1279 | 386 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.4 | 11.1 | 12.7 | OK
1280 | 386 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.8 | 50.0 | OK
1281 | 386 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.8 | 50.1 | OK
1282 | 386 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 30.8 | 34.5 | OK
1283 | 386 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.1 | 12.7 | OK
1284 | 386 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.8 | 50.1 | OK
1285 | 387 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 46.7 | 51.9 | OK
1286 | 387 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.0 | 32.4 | 36.0 | OK
1287 | 387 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 12.0 | 13.3 | OK
1288 | 387 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 46.7 | 51.9 | OK
1289 | 387 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 46.7 | 51.9 | OK
1290 | 387 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.0 | 32.3 | 35.9 | OK
1291 | 387 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 12.0 | 13.3 | OK
1292 | 387 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 46.7 | 51.9 | OK
1293 | 387 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.7 | 46.8 | 52.0 | OK
1294 | 387 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 32.3 | 35.9 | OK
1295 | 387 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.8 | 13.2 | OK
1296 | 387 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.7 | 46.8 | 52.0 | OK
1297 | 388 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.3 | 46.5 | 51.6 | OK
1298 | 388 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.0 | 33.8 | 37.6 | OK
1299 | 388 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -5.0 | 16.0 | 17.8 | OK
1300 | 388 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.3 | 46.5 | 51.6 | OK
1301 | 388 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.4 | 48.2 | 53.6 | OK
1302 | 388 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.6 | 35.1 | 39.0 | OK
1303 | 388 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -5.6 | 16.5 | 18.3 | OK
1304 | 388 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.4 | 48.2 | 53.6 | OK
1305 | 388 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.2 | 50.3 | OK
1306 | 388 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 30.0 | 34.9 | OK
1307 | 388 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 10.3 | 13.4 | OK
1308 | 388 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.2 | 50.3 | OK
1309 | 389 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 68.1 | 78.3 | 87.0 | OK
1310 | 389 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | 67.0 | 74.9 | 83.2 | OK
1311 | 389 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 67.7 | 70.9 | 78.8 | OK
1312 | 389 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 68.1 | 78.3 | 87.0 | OK
1313 | 389 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 67.6 | 77.2 | 85.7 | OK
1314 | 389 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | 66.7 | 74.1 | 82.3 | OK
1315 | 389 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 67.5 | 70.4 | 78.2 | OK
1316 | 389 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 67.6 | 77.2 | 85.7 | OK
1317 | 389 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 63.0 | 75.7 | 84.1 | OK
1318 | 389 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | 62.5 | 72.1 | 80.1 | OK
1319 | 389 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 63.9 | 67.6 | 75.1 | OK
1320 | 389 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 63.0 | 75.7 | 84.1 | OK
1321 | 390 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.5 | 46.8 | 52.0 | OK
1322 | 390 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.1 | 34.1 | 37.9 | OK
1323 | 390 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -4.9 | 16.2 | 18.0 | OK
1324 | 390 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.5 | 46.8 | 52.0 | OK
1325 | 390 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.1 | 48.7 | 54.1 | OK
1326 | 390 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.1 | 35.5 | 39.5 | OK
1327 | 390 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -5.8 | 16.7 | 18.5 | OK
1328 | 390 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.1 | 48.7 | 54.1 | OK
1329 | 390 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 44.6 | 51.1 | OK
1330 | 390 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 30.2 | 35.7 | OK
1331 | 390 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.6 | 10.2 | 14.0 | OK
1332 | 390 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.0 | 44.6 | 51.1 | OK
1333 | 391 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.2 | 43.1 | 47.9 | OK
1334 | 391 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.6 | 29.7 | 33.0 | OK
1335 | 391 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 11.2 | 12.5 | OK
1336 | 391 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.2 | 43.1 | 47.9 | OK
1337 | 391 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 44.3 | 49.2 | OK
1338 | 391 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.3 | 30.7 | 34.1 | OK
1339 | 391 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 11.7 | 13.0 | OK
1340 | 391 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 44.3 | 49.2 | OK
1341 | 391 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 44.2 | 50.7 | OK
1342 | 391 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.8 | 29.9 | 35.3 | OK
1343 | 391 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.3 | 10.2 | 13.7 | OK
1344 | 391 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 44.2 | 50.7 | OK
1345 | 392A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 38.0 | 42.2 | OK
1346 | 392A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -20.0 | 27.0 | 30.0 | OK
1347 | 392A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -4.8 | 12.2 | 13.5 | OK
1348 | 392A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 38.0 | 42.2 | OK
1349 | 392A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -31.9 | 38.6 | 42.9 | OK
1350 | 392A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -20.2 | 27.5 | 30.5 | OK
1351 | 392A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -4.7 | 12.5 | 13.8 | OK
1352 | 392A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -31.9 | 38.6 | 42.9 | OK
1353 | 392A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.4 | 36.9 | 41.0 | OK
1354 | 392A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.5 | 25.1 | 27.9 | OK
1355 | 392A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.6 | 9.2 | 10.3 | OK
1356 | 392A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -36.4 | 36.9 | 41.0 | OK
1357 | 393A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.1 | 47.2 | 52.5 | OK
1358 | 393A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.4 | 32.6 | 36.2 | OK
1359 | 393A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 12.0 | 13.3 | OK
1360 | 393A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.1 | 47.2 | 52.5 | OK
1361 | 393A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 47.0 | 52.2 | OK
1362 | 393A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 32.4 | 36.0 | OK
1363 | 393A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 11.9 | 13.2 | OK
1364 | 393A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 47.0 | 52.2 | OK
1365 | 393A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 47.2 | 52.5 | OK
1366 | 393A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.6 | 32.5 | 36.2 | OK
1367 | 393A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 11.8 | 13.2 | OK
1368 | 393A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 47.2 | 52.5 | OK
1369 | 394A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 42.7 | 47.5 | OK
1370 | 394A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 29.2 | 32.4 | OK
1371 | 394A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 10.7 | 11.8 | OK
1372 | 394A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 42.7 | 47.5 | OK
1373 | 394A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 42.8 | 47.6 | OK
1374 | 394A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.1 | 29.3 | 32.5 | OK
1375 | 394A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 10.7 | 11.9 | OK
1376 | 394A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.7 | 42.8 | 47.6 | OK
1377 | 394A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 42.7 | 47.5 | OK
1378 | 394A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 29.2 | 32.4 | OK
1379 | 394A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 10.7 | 11.8 | OK
1380 | 394A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 42.7 | 47.5 | OK
1381 | 395A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 45.2 | 50.2 | OK
1382 | 395A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 31.0 | 34.5 | OK
1383 | 395A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.4 | 12.7 | OK
1384 | 395A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 45.2 | 50.2 | OK
1385 | 395A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 45.1 | 50.2 | OK
1386 | 395A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 31.0 | 34.4 | OK
1387 | 395A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.4 | 12.6 | OK
1388 | 395A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 45.1 | 50.2 | OK
1389 | 395A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 45.2 | 50.3 | OK
1390 | 395A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.8 | 31.1 | 34.5 | OK
1391 | 395A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.4 | 12.7 | OK
1392 | 395A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 45.2 | 50.3 | OK
1393 | 396A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.4 | 42.2 | 47.1 | OK
1394 | 396A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 28.7 | 32.2 | OK
1395 | 396A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.6 | 10.3 | 11.8 | OK
1396 | 396A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.4 | 42.2 | 47.1 | OK
1397 | 396A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 42.9 | 47.7 | OK
1398 | 396A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.2 | 29.3 | 32.6 | OK
1399 | 396A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 10.7 | 11.9 | OK
1400 | 396A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 42.9 | 47.7 | OK
1401 | 396A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 43.1 | 47.9 | OK
1402 | 396A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.2 | 29.6 | 32.8 | OK
1403 | 396A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 10.9 | 12.1 | OK
1404 | 396A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 43.1 | 47.9 | OK
1405 | 398A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 43.2 | 48.3 | OK
1406 | 398A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.8 | 29.4 | 33.1 | OK
1407 | 398A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 10.6 | 12.2 | OK
1408 | 398A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 43.2 | 48.3 | OK
1409 | 398A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.8 | 43.8 | 48.7 | OK
1410 | 398A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.9 | 30.0 | 33.3 | OK
1411 | 398A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 10.9 | 12.2 | OK
1412 | 398A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.8 | 43.8 | 48.7 | OK
1413 | 398A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.1 | 49.0 | OK
1414 | 398A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 30.3 | 33.6 | OK
1415 | 398A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 11.1 | 12.4 | OK
1416 | 398A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 44.1 | 49.0 | OK
1417 | 399A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.5 | 42.4 | 47.2 | OK
1418 | 399A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 28.9 | 32.2 | OK
1419 | 399A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 10.5 | 11.7 | OK
1420 | 399A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.5 | 42.4 | 47.2 | OK
1421 | 399A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.2 | 42.6 | 47.3 | OK
1422 | 399A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.7 | 29.2 | 32.4 | OK
1423 | 399A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 10.7 | 11.9 | OK
1424 | 399A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.2 | 42.6 | 47.3 | OK
1425 | 399A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 42.3 | 47.3 | OK
1426 | 399A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.1 | 28.8 | 32.3 | OK
1427 | 399A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.7 | 10.4 | 11.8 | OK
1428 | 399A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.6 | 42.3 | 47.3 | OK
1429 | 400 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.3 | 51.5 | OK
1430 | 400 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 31.9 | 35.5 | OK
1431 | 400 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.2 | 11.9 | 13.2 | OK
1432 | 400 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.9 | 46.3 | 51.5 | OK
1433 | 400 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.7 | 50.9 | OK
1434 | 400 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.4 | 31.3 | 34.9 | OK
1435 | 400 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.4 | 12.8 | OK
1436 | 400 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.7 | 50.9 | OK
1437 | 400 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 46.0 | 51.5 | OK
1438 | 400 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.0 | 31.5 | 35.5 | OK
1439 | 400 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.3 | 13.1 | OK
1440 | 400 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.4 | 46.0 | 51.5 | OK
1441 | 401 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.2 | 50.7 | OK
1442 | 401 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 31.0 | 35.1 | OK
1443 | 401 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 11.1 | 13.1 | OK
1444 | 401 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 45.2 | 50.7 | OK
1445 | 401 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.6 | 50.9 | OK
1446 | 401 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 31.3 | 35.1 | OK
1447 | 401 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.3 | 12.9 | OK
1448 | 401 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.8 | 45.6 | 50.9 | OK
1449 | 401 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.6 | 50.7 | OK
1450 | 401 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.9 | 31.5 | 35.1 | OK
1451 | 401 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 11.8 | 13.1 | OK
1452 | 401 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.1 | 45.6 | 50.7 | OK
1453 | 402 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 43.5 | 48.4 | OK
1454 | 402 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.7 | 29.9 | 33.2 | OK
1455 | 402 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.8 | 10.9 | 12.2 | OK
1456 | 402 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 43.5 | 48.4 | OK
1457 | 402 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.7 | 48.6 | OK
1458 | 402 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 30.0 | 33.3 | OK
1459 | 402 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 10.9 | 12.1 | OK
1460 | 402 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 43.7 | 48.6 | OK
1461 | 402 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 43.6 | 48.5 | OK
1462 | 402 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.7 | 30.0 | 33.3 | OK
1463 | 402 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.7 | 11.0 | 12.2 | OK
1464 | 402 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 43.6 | 48.5 | OK
1465 | 403 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.6 | 42.5 | 47.2 | OK
1466 | 403 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.2 | 29.7 | 33.0 | OK
1467 | 403 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.2 | 12.1 | 13.4 | OK
1468 | 403 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.6 | 42.5 | 47.2 | OK
1469 | 403 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.2 | 43.5 | 48.4 | OK
1470 | 403 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.6 | 30.6 | 34.0 | OK
1471 | 403 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.2 | 12.6 | 14.0 | OK
1472 | 403 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.2 | 43.5 | 48.4 | OK
1473 | 403 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.3 | 42.7 | 47.4 | OK
1474 | 403 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.8 | 29.2 | 32.5 | OK
1475 | 403 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.3 | 10.8 | 12.0 | OK
1476 | 403 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.3 | 42.7 | 47.4 | OK
1477 | 404A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.7 | 45.6 | OK
1478 | 404A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.8 | 27.7 | 30.9 | OK
1479 | 404A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 10.0 | 11.2 | OK
1480 | 404A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.7 | 45.6 | OK
1481 | 404A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 40.9 | 45.5 | OK
1482 | 404A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.7 | 27.9 | 31.0 | OK
1483 | 404A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.9 | 10.2 | 11.3 | OK
1484 | 404A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 40.9 | 45.5 | OK
1485 | 404A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 34.1 | 49.2 | OK
1486 | 404A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 20.9 | 35.8 | OK
1487 | 404A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.6 | 3.5 | 17.4 | OK
1488 | 404A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 34.1 | 49.2 | OK
1489 | 405 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -77.4 | -65.1 | 86.0 | OK
1490 | 405 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -73.3 | -63.4 | 81.5 | OK
1491 | 405 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -68.3 | -64.3 | 75.9 | OK
1492 | 405 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -77.4 | -65.1 | 86.0 | OK
1493 | 405 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -76.8 | -66.1 | 85.3 | OK
1494 | 405 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -73.2 | -64.7 | 81.3 | OK
1495 | 405 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -68.8 | -65.4 | 76.5 | OK
1496 | 405 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -76.8 | -66.1 | 85.3 | OK
1497 | 405 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -76.9 | -66.2 | 85.4 | OK
1498 | 405 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -73.3 | -64.8 | 81.4 | OK
1499 | 405 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -68.9 | -65.5 | 76.6 | OK
1500 | 405 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -76.9 | -66.2 | 85.4 | OK
1501 | 406 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 44.3 | 49.2 | OK
1502 | 406 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.3 | 30.7 | 34.1 | OK
1503 | 406 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 11.8 | 13.1 | OK
1504 | 406 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.2 | 44.3 | 49.2 | OK
1505 | 406 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.0 | 44.5 | 49.4 | OK
1506 | 406 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.1 | 30.9 | 34.4 | OK
1507 | 406 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.9 | 12.0 | 13.4 | OK
1508 | 406 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.0 | 44.5 | 49.4 | OK
1509 | 406 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 39.2 | 49.3 | OK
1510 | 406 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 25.6 | 35.1 | OK
1511 | 406 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -13.7 | 7.1 | 15.2 | OK
1512 | 406 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 39.2 | 49.3 | OK
1513 | 407 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.2 | OK
1514 | 407 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 30.8 | 34.6 | OK
1515 | 407 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.1 | 12.8 | OK
1516 | 407 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.2 | OK
1517 | 407 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.2 | OK
1518 | 407 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 30.8 | 34.6 | OK
1519 | 407 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 11.1 | 12.8 | OK
1520 | 407 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.2 | OK
1521 | 407 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.3 | OK
1522 | 407 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 30.8 | 34.7 | OK
1523 | 407 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 11.1 | 12.9 | OK
1524 | 407 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.9 | 50.3 | OK
1525 | 408 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 44.0 | 48.9 | OK
1526 | 408 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 30.2 | 33.6 | OK
1527 | 408 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 11.0 | 12.3 | OK
1528 | 408 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 44.0 | 48.9 | OK
1529 | 408 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 46.7 | 51.9 | OK
1530 | 408 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.5 | 33.6 | 37.3 | OK
1531 | 408 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.0 | 14.9 | 16.6 | OK
1532 | 408 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.9 | 46.7 | 51.9 | OK
1533 | 408 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 43.9 | 48.9 | OK
1534 | 408 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.3 | 30.1 | 33.6 | OK
1535 | 408 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.1 | 10.9 | 12.3 | OK
1536 | 408 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 43.9 | 48.9 | OK
1537 | 409 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.1 | 52.0 | 57.8 | OK
1538 | 409 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.2 | 39.0 | 43.3 | OK
1539 | 409 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -3.0 | 20.0 | 22.3 | OK
1540 | 409 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.1 | 52.0 | 57.8 | OK
1541 | 409 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.7 | 51.7 | 57.5 | OK
1542 | 409 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -24.8 | 38.6 | 42.9 | OK
1543 | 409 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -3.6 | 19.5 | 21.7 | OK
1544 | 409 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.7 | 51.7 | 57.5 | OK
1545 | 409 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 49.3 | 54.7 | OK
1546 | 409 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.1 | 35.3 | 39.3 | OK
1547 | 409 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.2 | 15.4 | 17.1 | OK
1548 | 409 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.3 | 49.3 | 54.7 | OK
1549 | 410 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -25.4 | 55.6 | 61.8 | OK
1550 | 410 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -9.8 | 44.8 | 49.8 | OK
1551 | 410 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 9.4 | 29.0 | 32.2 | OK
1552 | 410 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -25.4 | 55.6 | 61.8 | OK
1553 | 410 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -25.0 | 56.0 | 62.2 | OK
1554 | 410 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -9.3 | 45.2 | 50.3 | OK
1555 | 410 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 9.9 | 29.5 | 32.8 | OK
1556 | 410 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -25.0 | 56.0 | 62.2 | OK
1557 | 410 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 54.0 | 60.0 | OK
1558 | 410 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -13.4 | 42.8 | 47.5 | OK
1559 | 410 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 6.1 | 26.4 | 29.3 | OK
1560 | 410 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 54.0 | 60.0 | OK
1561 | 411 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 47.2 | 52.9 | OK
1562 | 411 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -33.0 | 32.5 | 36.6 | OK
1563 | 411 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.3 | 11.7 | 13.7 | OK
1564 | 411 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.6 | 47.2 | 52.9 | OK
1565 | 411 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 50.4 | 56.0 | OK
1566 | 411 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.1 | 36.2 | 40.2 | OK
1567 | 411 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.5 | 15.8 | 17.5 | OK
1568 | 411 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.6 | 50.4 | 56.0 | OK
1569 | 411 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 47.2 | 52.5 | OK
1570 | 411 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.3 | 32.6 | 36.3 | OK
1571 | 411 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 12.1 | 13.4 | OK
1572 | 411 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.9 | 47.2 | 52.5 | OK
1573 | 411A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.2 | 40.8 | 45.3 | OK
1574 | 411A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.2 | 27.9 | 31.0 | OK
1575 | 411A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.6 | 10.3 | 11.5 | OK
1576 | 411A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.2 | 40.8 | 45.3 | OK
1577 | 411A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.6 | 40.3 | 44.8 | OK
1578 | 411A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.9 | 27.8 | 30.9 | OK
1579 | 411A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.7 | 10.7 | 11.9 | OK
1580 | 411A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.6 | 40.3 | 44.8 | OK
1581 | 411A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.8 | 39.4 | 46.5 | OK
1582 | 411A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 26.3 | 32.2 | OK
1583 | 411A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.5 | 8.5 | 12.8 | OK
1584 | 411A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.8 | 39.4 | 46.5 | OK
1585 | 411A | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.3 | 36.7 | 42.6 | OK
1586 | 411A | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.2 | 24.4 | 29.1 | OK
1587 | 411A | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 8.1 | 11.1 | OK
1588 | 411A | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.3 | 36.7 | 42.6 | OK
1589 | 412A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.1 | 50.0 | OK
1590 | 412A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.0 | 29.9 | 34.5 | OK
1591 | 412A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.7 | 10.5 | 13.0 | OK
1592 | 412A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 44.1 | 50.0 | OK
1593 | 412A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 44.7 | 51.8 | OK
1594 | 412A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.5 | 30.1 | 36.1 | OK
1595 | 412A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.7 | 10.0 | 14.1 | OK
1596 | 412A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 44.7 | 51.8 | OK
1597 | 412A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 45.7 | 50.8 | OK
1598 | 412A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.0 | 31.9 | 35.4 | OK
1599 | 412A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.4 | 12.7 | 14.1 | OK
1600 | 412A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.4 | 45.7 | 50.8 | OK
1601 | 413A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 45.3 | 50.3 | OK
1602 | 413A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.6 | 31.3 | 34.7 | OK
1603 | 413A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.1 | 12.0 | 13.3 | OK
1604 | 413A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 45.3 | 50.3 | OK
1605 | 413A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.1 | 45.1 | 50.1 | OK
1606 | 413A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.9 | 31.2 | 34.7 | OK
1607 | 413A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.6 | 12.2 | 13.6 | OK
1608 | 413A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.1 | 45.1 | 50.1 | OK
1609 | 413A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 44.4 | 49.8 | OK
1610 | 413A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.6 | 30.2 | 34.1 | OK
1611 | 413A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 10.8 | 12.5 | OK
1612 | 413A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 44.4 | 49.8 | OK
1613 | 413A | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 42.5 | 48.8 | OK
1614 | 413A | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.3 | 28.6 | 33.7 | OK
1615 | 413A | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 9.7 | 12.9 | OK
1616 | 413A | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.9 | 42.5 | 48.8 | OK
1617 | 414A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.2 | 41.1 | 45.7 | OK
1618 | 414A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.1 | 28.1 | 31.3 | OK
1619 | 414A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.4 | 10.5 | 11.7 | OK
1620 | 414A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -40.2 | 41.1 | 45.7 | OK
1621 | 414A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.2 | 40.8 | 45.3 | OK
1622 | 414A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -26.2 | 28.0 | 31.2 | OK
1623 | 414A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -8.8 | 10.8 | 12.0 | OK
1624 | 414A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -39.2 | 40.8 | 45.3 | OK
1625 | 414A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.4 | 45.6 | OK
1626 | 414A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -28.0 | 27.3 | 31.1 | OK
1627 | 414A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.4 | 9.6 | 11.5 | OK
1628 | 414A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.0 | 40.4 | 45.6 | OK
1629 | 414A | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 37.9 | 42.5 | OK
1630 | 414A | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -25.9 | 25.6 | 28.8 | OK
1631 | 414A | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -9.5 | 9.1 | 10.5 | OK
1632 | 414A | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -38.2 | 37.9 | 42.5 | OK
1633 | 415 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.2 | 49.4 | OK
1634 | 415 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.6 | 30.2 | 33.9 | OK
1635 | 415 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 10.9 | 12.5 | OK
1636 | 415 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.4 | 44.2 | 49.4 | OK
1637 | 415 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 44.7 | 50.8 | OK
1638 | 415 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.7 | 30.5 | 35.2 | OK
1639 | 415 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.0 | 10.6 | 13.3 | OK
1640 | 415 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.7 | 44.7 | 50.8 | OK
1641 | 415 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 45.1 | 50.1 | OK
1642 | 415 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.5 | 31.3 | 34.8 | OK
1643 | 415 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 12.1 | 13.4 | OK
1644 | 415 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 45.1 | 50.1 | OK
1645 | 415A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.4 | 49.5 | OK
1646 | 415A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.3 | 30.1 | 33.6 | OK
1647 | 415A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.0 | 10.8 | 12.2 | OK
1648 | 415A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.6 | 44.4 | 49.5 | OK
1649 | 415A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 46.7 | 51.9 | OK
1650 | 415A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.6 | 31.8 | 35.4 | OK
1651 | 415A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.3 | 11.6 | 12.9 | OK
1652 | 415A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.5 | 46.7 | 51.9 | OK
1653 | 415A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 43.6 | 49.8 | OK
1654 | 415A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.7 | 29.3 | 34.1 | OK
1655 | 415A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.6 | 10.0 | 12.8 | OK
1656 | 415A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.8 | 43.6 | 49.8 | OK
1657 | 415B | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -31.0 | 31.0 | -44.6 | 44.0 | 143.9 | NG
1658 | 415B | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -73.0 | 73.0 | -30.7 | 29.9 | 42.0 | OK
1659 | 415B | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -9.9 | 9.9 | -11.5 | 10.5 | 115.7 | NG
1660 | 415B | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -23.0 | 23.0 | -44.6 | 44.0 | 194.0 | NG
1661 | 415B | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -31.0 | 31.0 | -42.5 | 41.3 | 137.1 | NG
1662 | 415B | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -73.0 | 73.0 | -29.3 | 27.9 | 40.1 | OK
1663 | 415B | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -9.9 | 9.9 | -11.1 | 9.6 | 112.4 | NG
1664 | 415B | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -23.0 | 23.0 | -42.5 | 41.3 | 184.8 | NG
1665 | 415B | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -31.0 | 31.0 | -44.4 | 44.8 | 144.5 | NG
1666 | 415B | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -73.0 | 73.0 | -30.2 | 30.8 | 42.2 | OK
1667 | 415B | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -9.9 | 9.9 | -10.8 | 11.4 | 115.1 | NG
1668 | 415B | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -23.0 | 23.0 | -44.4 | 44.8 | 194.8 | NG
1669 | 415B | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0.0 | 0.0 | -40.1 | 30.4 | 200.0 | NG
1670 | 415B | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0.0 | 0.0 | -29.2 | 18.6 | 200.0 | NG
1671 | 415B | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0.0 | 0.0 | -14.3 | 3.0 | 200.0 | NG
1672 | 415B | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0.0 | 0.0 | -40.1 | 30.4 | 200.0 | NG
1673 | 416 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.9 | 44.0 | 49.9 | OK
1674 | 416 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.1 | 30.0 | 34.5 | OK
1675 | 416 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 10.5 | 13.1 | OK
1676 | 416 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.9 | 44.0 | 49.9 | OK
1677 | 416 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.3 | 50.2 | OK
1678 | 416 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.3 | 30.3 | 34.8 | OK
1679 | 416 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.8 | 10.6 | 13.1 | OK
1680 | 416 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.2 | 44.3 | 50.2 | OK
1681 | 416 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 43.9 | 50.0 | OK
1682 | 416 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 29.9 | 34.6 | OK
1683 | 416 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -11.9 | 10.4 | 13.2 | OK
1684 | 416 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -45.0 | 43.9 | 50.0 | OK
1685 | 417 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 45.2 | 50.2 | OK
1686 | 417 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.5 | 31.5 | 35.0 | OK
1687 | 417 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 12.2 | 13.6 | OK
1688 | 417 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.6 | 45.2 | 50.2 | OK
1689 | 417 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 45.4 | 50.4 | OK
1690 | 417 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.6 | 31.6 | 35.1 | OK
1691 | 417 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.0 | 12.3 | 13.7 | OK
1692 | 417 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.7 | 45.4 | 50.4 | OK
1693 | 417 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 44.8 | 49.8 | OK
1694 | 417 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.0 | 31.0 | 34.5 | OK
1695 | 417 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.5 | 11.7 | 13.0 | OK
1696 | 417 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -44.0 | 44.8 | 49.8 | OK
1697 | 417A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 46.3 | 51.5 | OK
1698 | 417A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -27.2 | 32.8 | 36.5 | OK
1699 | 417A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -7.7 | 14.1 | 15.6 | OK
1700 | 417A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -41.6 | 46.3 | 51.5 | OK
1701 | 417A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.3 | 40.6 | 48.1 | OK
1702 | 417A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -30.2 | 27.0 | 33.5 | OK
1703 | 417A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.1 | 8.6 | 13.5 | OK
1704 | 417A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -43.3 | 40.6 | 48.1 | OK
1705 | 417A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 45.3 | 51.7 | OK
1706 | 417A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -32.2 | 30.6 | 35.8 | OK
1707 | 417A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -12.3 | 10.5 | 13.7 | OK
1708 | 417A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.6 | 45.3 | 51.7 | OK
1709 | 418 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 48.5 | 53.9 | OK
1710 | 418 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -31.2 | 34.1 | 37.9 | OK
1711 | 418 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.2 | 13.7 | 15.2 | OK
1712 | 418 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -46.2 | 48.5 | 53.9 | OK
1713 | 418 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 39.8 | 52.4 | OK
1714 | 418 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -34.2 | 25.4 | 38.0 | OK
1715 | 418 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -15.8 | 5.9 | 17.6 | OK
1716 | 418 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -47.2 | 39.8 | 52.4 | OK
1717 | 418 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 42.5 | 47.6 | OK
1718 | 418 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | -29.4 | 29.0 | 32.7 | OK
1719 | 418 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | -10.9 | 10.4 | 12.1 | OK
1720 | 418 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | -42.8 | 42.5 | 47.6 | OK
1721 | 421 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 58.0 | 67.4 | 74.9 | OK
1722 | 421 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | 57.7 | 64.4 | 71.6 | OK
1723 | 421 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 58.6 | 61.1 | 67.9 | OK
1724 | 421 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 58.0 | 67.4 | 74.9 | OK
1725 | 421 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 58.7 | 68.7 | 76.4 | OK
1726 | 421 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | 58.2 | 65.5 | 72.8 | OK
1727 | 421 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 59.2 | 61.9 | 68.8 | OK
1728 | 421 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 58.7 | 68.7 | 76.4 | OK
1729 | 421 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 48.1 | 63.4 | 70.4 | OK
1730 | 421 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | -90.0 | 90.0 | 48.5 | 59.3 | 65.9 | OK
1731 | 421 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | -90.0 | 90.0 | 50.5 | 54.6 | 60.7 | OK
1732 | 421 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | -90.0 | 90.0 | 48.1 | 63.4 | 70.4 | OK

## Tab_3
rowtext | str | set | phase | swing_cond | weather_case_description | wire_condition | min_req_vert_load | vert_load_wind_from_left | vert_load_wind_from_right | vert_load_margin | ok
1 | 281A | 14 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 792 | 783 | 783 | OK
2 | 281A | 14 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 858 | 851 | 851 | OK
3 | 281A | 14 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 897 | 894 | 894 | OK
4 | 281A | 14 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 792 | 783 | 783 | OK
5 | 281A | 15 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1093 | 1104 | 1093 | OK
6 | 281A | 15 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1119 | 1128 | 1119 | OK
7 | 281A | 15 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1137 | 1140 | 1137 | OK
8 | 281A | 15 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1093 | 1104 | 1093 | OK
9 | 281A | 16 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1105 | 1115 | 1105 | OK
10 | 281A | 16 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1129 | 1137 | 1129 | OK
11 | 281A | 16 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1145 | 1148 | 1145 | OK
12 | 281A | 16 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1105 | 1115 | 1105 | OK
13 | 282 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2687 | 2665 | 2665 | OK
14 | 282 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2657 | 2640 | 2640 | OK
15 | 282 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2635 | 2629 | 2629 | OK
16 | 282 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2687 | 2665 | 2665 | OK
17 | 282 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2674 | 2655 | 2655 | OK
18 | 282 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2647 | 2632 | 2632 | OK
19 | 282 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2628 | 2622 | 2622 | OK
20 | 282 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2674 | 2655 | 2655 | OK
21 | 282 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2973 | 2992 | 2973 | OK
22 | 282 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2908 | 2922 | 2908 | OK
23 | 282 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2872 | 2877 | 2872 | OK
24 | 282 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2973 | 2992 | 2973 | OK
25 | 283 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2822 | 2833 | 2822 | OK
26 | 283 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2843 | 2851 | 2843 | OK
27 | 283 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2857 | 2860 | 2857 | OK
28 | 283 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2822 | 2833 | 2822 | OK
29 | 283 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2750 | 2762 | 2750 | OK
30 | 283 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2781 | 2791 | 2781 | OK
31 | 283 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2801 | 2805 | 2801 | OK
32 | 283 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2750 | 2762 | 2750 | OK
33 | 283 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2827 | 2815 | 2815 | OK
34 | 283 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2844 | 2835 | 2835 | OK
35 | 283 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2852 | 2849 | 2849 | OK
36 | 283 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2827 | 2815 | 2815 | OK
37 | 286 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3041 | 3041 | 3041 | OK
38 | 286 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3043 | 3043 | 3043 | OK
39 | 286 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3044 | 3044 | 3044 | OK
40 | 286 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3041 | 3041 | 3041 | OK
41 | 286 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2971 | 2976 | 2971 | OK
42 | 286 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2984 | 2988 | 2984 | OK
43 | 286 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2992 | 2993 | 2992 | OK
44 | 286 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2971 | 2976 | 2971 | OK
45 | 286 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3040 | 3031 | 3031 | OK
46 | 286 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3043 | 3036 | 3036 | OK
47 | 286 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3042 | 3040 | 3040 | OK
48 | 286 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3040 | 3031 | 3031 | OK
49 | 287 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2798 | 2798 | 2798 | OK
50 | 287 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2720 | 2720 | 2720 | OK
51 | 287 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2673 | 2673 | 2673 | OK
52 | 287 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2798 | 2798 | 2798 | OK
53 | 287 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2694 | 2691 | 2691 | OK
54 | 287 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2628 | 2626 | 2626 | OK
55 | 287 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2588 | 2587 | 2587 | OK
56 | 287 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2694 | 2691 | 2691 | OK
57 | 287 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2631 | 2639 | 2631 | OK
58 | 287 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2574 | 2579 | 2574 | OK
59 | 287 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2540 | 2543 | 2540 | OK
60 | 287 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2631 | 2639 | 2631 | OK
61 | 287A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 435 | 435 | 435 | OK
62 | 287A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 510 | 510 | 510 | OK
63 | 287A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 556 | 556 | 556 | OK
64 | 287A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 435 | 435 | 435 | OK
65 | 287A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 534 | 535 | 534 | OK
66 | 287A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 597 | 598 | 597 | OK
67 | 287A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 635 | 636 | 635 | OK
68 | 287A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 534 | 535 | 534 | OK
69 | 287A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 605 | 602 | 602 | OK
70 | 287A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 659 | 656 | 656 | OK
71 | 287A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 691 | 690 | 690 | OK
72 | 287A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 605 | 602 | 602 | OK
73 | 287A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 724 | 735 | 724 | OK
74 | 287A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 802 | 809 | 802 | OK
75 | 287A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 851 | 854 | 851 | OK
76 | 287A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 724 | 735 | 724 | OK
77 | 287A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 702 | 714 | 702 | OK
78 | 287A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 783 | 791 | 783 | OK
79 | 287A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 834 | 837 | 834 | OK
80 | 287A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 702 | 714 | 702 | OK
81 | 287A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 838 | 837 | 837 | OK
82 | 287A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 899 | 898 | 898 | OK
83 | 287A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 936 | 935 | 935 | OK
84 | 287A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 838 | 837 | 837 | OK
85 | 289 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2774 | 2778 | 2774 | OK
86 | 289 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2767 | 2770 | 2767 | OK
87 | 289 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2763 | 2764 | 2763 | OK
88 | 289 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2774 | 2778 | 2774 | OK
89 | 289 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2723 | 2735 | 2723 | OK
90 | 289 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2723 | 2732 | 2723 | OK
91 | 289 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2724 | 2727 | 2724 | OK
92 | 289 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2723 | 2735 | 2723 | OK
93 | 289 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2978 | 2949 | 2949 | OK
94 | 289 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2941 | 2920 | 2920 | OK
95 | 289 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2914 | 2906 | 2906 | OK
96 | 289 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2978 | 2949 | 2949 | OK
97 | 291 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2735 | 2735 | 2735 | OK
98 | 291 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2743 | 2743 | 2743 | OK
99 | 291 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2747 | 2747 | 2747 | OK
100 | 291 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2735 | 2735 | 2735 | OK
101 | 291 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2669 | 2675 | 2669 | OK
102 | 291 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2686 | 2691 | 2686 | OK
103 | 291 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2697 | 2699 | 2697 | OK
104 | 291 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2669 | 2675 | 2669 | OK
105 | 291 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2739 | 2730 | 2730 | OK
106 | 291 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2746 | 2739 | 2739 | OK
107 | 291 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2749 | 2746 | 2746 | OK
108 | 291 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2739 | 2730 | 2730 | OK
109 | 292 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2784 | 2775 | 2775 | OK
110 | 292 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2760 | 2754 | 2754 | OK
111 | 292 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2744 | 2742 | 2742 | OK
112 | 292 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2784 | 2775 | 2775 | OK
113 | 292 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2736 | 2728 | 2728 | OK
114 | 292 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2719 | 2713 | 2713 | OK
115 | 292 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2707 | 2705 | 2705 | OK
116 | 292 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2736 | 2728 | 2728 | OK
117 | 292 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2775 | 2770 | 2770 | OK
118 | 292 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2752 | 2749 | 2749 | OK
119 | 292 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2738 | 2737 | 2737 | OK
120 | 292 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2775 | 2770 | 2770 | OK
121 | 293 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2945 | 2883 | 2883 | OK
122 | 293 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2913 | 2874 | 2874 | OK
123 | 293 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2887 | 2873 | 2873 | OK
124 | 293 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2945 | 2883 | 2883 | OK
125 | 293 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2984 | 2924 | 2924 | OK
126 | 293 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2948 | 2909 | 2909 | OK
127 | 293 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2918 | 2905 | 2905 | OK
128 | 293 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2984 | 2924 | 2924 | OK
129 | 293 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2966 | 2906 | 2906 | OK
130 | 293 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2933 | 2894 | 2894 | OK
131 | 293 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2905 | 2891 | 2891 | OK
132 | 293 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2966 | 2906 | 2906 | OK
133 | 294 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2203 | 2343 | 2203 | OK
134 | 294 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2272 | 2362 | 2272 | OK
135 | 294 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2331 | 2362 | 2331 | OK
136 | 294 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2203 | 2343 | 2203 | OK
137 | 294 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2212 | 2347 | 2212 | OK
138 | 294 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2277 | 2364 | 2277 | OK
139 | 294 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2334 | 2364 | 2334 | OK
140 | 294 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2212 | 2347 | 2212 | OK
141 | 294 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2176 | 2311 | 2176 | OK
142 | 294 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2247 | 2335 | 2247 | OK
143 | 294 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2308 | 2338 | 2308 | OK
144 | 294 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2176 | 2311 | 2176 | OK
145 | 295 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2559 | 2492 | 2492 | OK
146 | 295 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2529 | 2487 | 2487 | OK
147 | 295 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2503 | 2489 | 2489 | OK
148 | 295 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2559 | 2492 | 2492 | OK
149 | 295 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2593 | 2535 | 2535 | OK
150 | 295 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2559 | 2524 | 2524 | OK
151 | 295 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2532 | 2521 | 2521 | OK
152 | 295 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2593 | 2535 | 2535 | OK
153 | 295 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2579 | 2514 | 2514 | OK
154 | 295 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2548 | 2506 | 2506 | OK
155 | 295 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2521 | 2507 | 2507 | OK
156 | 295 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2579 | 2514 | 2514 | OK
157 | 296 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2825 | 2839 | 2825 | OK
158 | 296 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2833 | 2843 | 2833 | OK
159 | 296 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2839 | 2843 | 2839 | OK
160 | 296 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2825 | 2839 | 2825 | OK
161 | 296 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2812 | 2787 | 2787 | OK
162 | 296 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2822 | 2802 | 2802 | OK
163 | 296 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2823 | 2815 | 2815 | OK
164 | 296 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2812 | 2787 | 2787 | OK
165 | 296 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2838 | 2852 | 2838 | OK
166 | 296 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2844 | 2855 | 2844 | OK
167 | 296 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2849 | 2854 | 2849 | OK
168 | 296 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2838 | 2852 | 2838 | OK
169 | 297 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2922 | 2876 | 2876 | OK
170 | 297 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2912 | 2878 | 2878 | OK
171 | 297 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2899 | 2886 | 2886 | OK
172 | 297 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2922 | 2876 | 2876 | OK
173 | 297 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2884 | 2841 | 2841 | OK
174 | 297 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2879 | 2847 | 2847 | OK
175 | 297 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2870 | 2857 | 2857 | OK
176 | 297 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2884 | 2841 | 2841 | OK
177 | 297 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2874 | 2894 | 2874 | OK
178 | 297 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2872 | 2888 | 2872 | OK
179 | 297 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2874 | 2880 | 2874 | OK
180 | 297 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2874 | 2894 | 2874 | OK
181 | 298 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2856 | 2874 | 2856 | OK
182 | 298 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2846 | 2860 | 2846 | OK
183 | 298 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2842 | 2848 | 2842 | OK
184 | 298 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2856 | 2874 | 2856 | OK
185 | 298 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2877 | 2850 | 2850 | OK
186 | 298 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2863 | 2843 | 2843 | OK
187 | 298 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2850 | 2843 | 2843 | OK
188 | 298 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2877 | 2850 | 2850 | OK
189 | 298 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2866 | 2882 | 2866 | OK
190 | 298 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2854 | 2867 | 2854 | OK
191 | 298 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2849 | 2854 | 2849 | OK
192 | 298 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2866 | 2882 | 2866 | OK
193 | 299 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2720 | 2655 | 2655 | OK
194 | 299 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2709 | 2670 | 2670 | OK
195 | 299 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2697 | 2684 | 2684 | OK
196 | 299 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2720 | 2655 | 2655 | OK
197 | 299 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2713 | 2662 | 2662 | OK
198 | 299 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2705 | 2676 | 2676 | OK
199 | 299 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2697 | 2688 | 2688 | OK
200 | 299 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2713 | 2662 | 2662 | OK
201 | 299 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2744 | 2681 | 2681 | OK
202 | 299 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2732 | 2695 | 2695 | OK
203 | 299 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2719 | 2707 | 2707 | OK
204 | 299 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2744 | 2681 | 2681 | OK
205 | 300 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2929 | 3069 | 2929 | OK
206 | 300 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2957 | 3040 | 2957 | OK
207 | 300 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2984 | 3011 | 2984 | OK
208 | 300 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2929 | 3069 | 2929 | OK
209 | 300 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2947 | 3079 | 2947 | OK
210 | 300 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2969 | 3048 | 2969 | OK
211 | 300 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2993 | 3018 | 2993 | OK
212 | 300 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2947 | 3079 | 2947 | OK
213 | 300 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2919 | 3049 | 2919 | OK
214 | 300 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2946 | 3023 | 2946 | OK
215 | 300 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2973 | 2998 | 2973 | OK
216 | 300 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2919 | 3049 | 2919 | OK
217 | 301 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2593 | 2501 | 2501 | OK
218 | 301 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2489 | 2434 | 2434 | OK
219 | 301 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2419 | 2400 | 2400 | OK
220 | 301 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2593 | 2501 | 2501 | OK
221 | 301 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2481 | 2399 | 2399 | OK
222 | 301 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2395 | 2345 | 2345 | OK
223 | 301 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2336 | 2320 | 2320 | OK
224 | 301 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2481 | 2399 | 2399 | OK
225 | 301 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2418 | 2348 | 2348 | OK
226 | 301 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2341 | 2301 | 2301 | OK
227 | 301 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2290 | 2277 | 2277 | OK
228 | 301 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2418 | 2348 | 2348 | OK
229 | 301A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 273 | 296 | 273 | OK
230 | 301A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 378 | 392 | 378 | OK
231 | 301A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 444 | 449 | 444 | OK
232 | 301A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 273 | 296 | 273 | OK
233 | 301A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 380 | 398 | 380 | OK
234 | 301A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 470 | 480 | 470 | OK
235 | 301A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 525 | 529 | 525 | OK
236 | 301A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 380 | 398 | 380 | OK
237 | 301A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 458 | 467 | 458 | OK
238 | 301A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 536 | 540 | 536 | OK
239 | 301A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 583 | 584 | 583 | OK
240 | 301A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 458 | 467 | 458 | OK
241 | 301A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 431 | 435 | 431 | OK
242 | 301A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 509 | 512 | 509 | OK
243 | 301A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 558 | 559 | 558 | OK
244 | 301A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 431 | 435 | 431 | OK
245 | 301A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 567 | 568 | 567 | OK
246 | 301A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 628 | 628 | 628 | OK
247 | 301A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 665 | 665 | 665 | OK
248 | 301A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 567 | 568 | 567 | OK
249 | 301A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 618 | 622 | 618 | OK
250 | 301A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 672 | 675 | 672 | OK
251 | 301A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 705 | 706 | 705 | OK
252 | 301A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 618 | 622 | 618 | OK
253 | 302 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2671 | 2665 | 2665 | OK
254 | 302 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2601 | 2596 | 2596 | OK
255 | 302 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2557 | 2555 | 2555 | OK
256 | 302 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2671 | 2665 | 2665 | OK
257 | 302 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2463 | 2463 | 2463 | OK
258 | 302 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2419 | 2420 | 2419 | OK
259 | 302 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2393 | 2393 | 2393 | OK
260 | 302 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2463 | 2463 | 2463 | OK
261 | 302 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2479 | 2472 | 2472 | OK
262 | 302 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2432 | 2427 | 2427 | OK
263 | 302 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2403 | 2401 | 2401 | OK
264 | 302 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2479 | 2472 | 2472 | OK
265 | 305 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3055 | 3061 | 3055 | OK
266 | 305 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3077 | 3082 | 3077 | OK
267 | 305 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3092 | 3094 | 3092 | OK
268 | 305 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3055 | 3061 | 3055 | OK
269 | 305 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3016 | 3023 | 3016 | OK
270 | 305 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3047 | 3052 | 3047 | OK
271 | 305 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3066 | 3069 | 3066 | OK
272 | 305 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3016 | 3023 | 3016 | OK
273 | 305 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3085 | 3084 | 3084 | OK
274 | 305 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3104 | 3104 | 3104 | OK
275 | 305 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3115 | 3115 | 3115 | OK
276 | 305 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3085 | 3084 | 3084 | OK
277 | 306 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3179 | 3176 | 3176 | OK
278 | 306 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3186 | 3183 | 3183 | OK
279 | 306 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3189 | 3188 | 3188 | OK
280 | 306 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3179 | 3176 | 3176 | OK
281 | 306 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3177 | 3174 | 3174 | OK
282 | 306 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3185 | 3182 | 3182 | OK
283 | 306 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3190 | 3189 | 3189 | OK
284 | 306 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3177 | 3174 | 3174 | OK
285 | 306 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3162 | 3160 | 3160 | OK
286 | 306 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3172 | 3170 | 3170 | OK
287 | 306 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3177 | 3177 | 3177 | OK
288 | 306 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3162 | 3160 | 3160 | OK
289 | 307 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3278 | 3276 | 3276 | OK
290 | 307 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3272 | 3271 | 3271 | OK
291 | 307 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3269 | 3268 | 3268 | OK
292 | 307 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3278 | 3276 | 3276 | OK
293 | 307 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3236 | 3235 | OK
294 | 307 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3235 | 3236 | 3235 | OK
295 | 307 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3235 | 3236 | 3235 | OK
296 | 307 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3236 | 3235 | OK
297 | 307 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3169 | 3173 | 3169 | OK
298 | 307 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3178 | 3181 | 3178 | OK
299 | 307 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3183 | 3185 | 3183 | OK
300 | 307 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3169 | 3173 | 3169 | OK
301 | 308 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3215 | 3215 | 3215 | OK
302 | 308 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3218 | 3218 | 3218 | OK
303 | 308 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3220 | 3220 | 3220 | OK
304 | 308 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3215 | 3215 | 3215 | OK
305 | 308 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3308 | 3304 | 3304 | OK
306 | 308 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3298 | 3295 | 3295 | OK
307 | 308 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3292 | 3291 | 3291 | OK
308 | 308 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3308 | 3304 | 3304 | OK
309 | 308 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3446 | 3435 | 3435 | OK
310 | 308 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3418 | 3410 | 3410 | OK
311 | 308 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3400 | 3397 | 3397 | OK
312 | 308 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3446 | 3435 | 3435 | OK
313 | 309 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2758 | 2764 | 2758 | OK
314 | 309 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2761 | 2766 | 2761 | OK
315 | 309 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2764 | 2766 | 2764 | OK
316 | 309 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2758 | 2764 | 2758 | OK
317 | 309 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2724 | 2732 | 2724 | OK
318 | 309 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2733 | 2738 | 2733 | OK
319 | 309 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2739 | 2741 | 2739 | OK
320 | 309 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2724 | 2732 | 2724 | OK
321 | 309 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2643 | 2657 | 2643 | OK
322 | 309 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2661 | 2671 | 2661 | OK
323 | 309 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2674 | 2678 | 2674 | OK
324 | 309 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2643 | 2657 | 2643 | OK
325 | 310 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2444 | 2439 | 2439 | OK
326 | 310 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2430 | 2426 | 2426 | OK
327 | 310 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2420 | 2419 | 2419 | OK
328 | 310 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2444 | 2439 | 2439 | OK
329 | 310 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2420 | 2419 | 2419 | OK
330 | 310 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2409 | 2408 | 2408 | OK
331 | 310 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2402 | 2401 | 2401 | OK
332 | 310 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2420 | 2419 | 2419 | OK
333 | 310 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2443 | 2438 | 2438 | OK
334 | 310 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2430 | 2426 | 2426 | OK
335 | 310 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2421 | 2420 | 2420 | OK
336 | 310 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2443 | 2438 | 2438 | OK
337 | 311 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2457 | 2443 | 2443 | OK
338 | 311 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2440 | 2429 | 2429 | OK
339 | 311 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2427 | 2423 | 2423 | OK
340 | 311 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2457 | 2443 | 2443 | OK
341 | 311 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2456 | 2440 | 2440 | OK
342 | 311 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2438 | 2426 | 2426 | OK
343 | 311 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2424 | 2420 | 2420 | OK
344 | 311 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2456 | 2440 | 2440 | OK
345 | 311 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2448 | 2431 | 2431 | OK
346 | 311 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2432 | 2419 | 2419 | OK
347 | 311 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2420 | 2414 | 2414 | OK
348 | 311 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2448 | 2431 | 2431 | OK
349 | 312 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2735 | 2758 | 2735 | OK
350 | 312 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2741 | 2759 | 2741 | OK
351 | 312 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2749 | 2756 | 2749 | OK
352 | 312 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2735 | 2758 | 2735 | OK
353 | 312 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2748 | 2769 | 2748 | OK
354 | 312 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2753 | 2769 | 2753 | OK
355 | 312 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2760 | 2766 | 2760 | OK
356 | 312 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2748 | 2769 | 2748 | OK
357 | 312 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2754 | 2778 | 2754 | OK
358 | 312 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2758 | 2776 | 2758 | OK
359 | 312 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2764 | 2772 | 2764 | OK
360 | 312 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2754 | 2778 | 2754 | OK
361 | 313 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3227 | 3227 | OK
362 | 313 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3233 | 3227 | 3227 | OK
363 | 313 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3231 | 3228 | 3228 | OK
364 | 313 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3227 | 3227 | OK
365 | 313 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3224 | 3218 | 3218 | OK
366 | 313 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3224 | 3219 | 3219 | OK
367 | 313 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3222 | 3220 | 3220 | OK
368 | 313 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3224 | 3218 | 3218 | OK
369 | 313 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3226 | 3218 | 3218 | OK
370 | 313 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3225 | 3218 | 3218 | OK
371 | 313 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3223 | 3220 | 3220 | OK
372 | 313 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3226 | 3218 | 3218 | OK
373 | 314 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3199 | 3199 | 3199 | OK
374 | 314 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3203 | 3203 | 3203 | OK
375 | 314 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3206 | 3206 | 3206 | OK
376 | 314 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3199 | 3199 | 3199 | OK
377 | 314 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3210 | 3209 | 3209 | OK
378 | 314 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3213 | 3212 | 3212 | OK
379 | 314 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3215 | 3214 | 3214 | OK
380 | 314 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3210 | 3209 | 3209 | OK
381 | 314 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3203 | 3203 | 3203 | OK
382 | 314 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3206 | 3206 | 3206 | OK
383 | 314 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3209 | 3209 | 3209 | OK
384 | 314 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3203 | 3203 | 3203 | OK
385 | 315 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2981 | 2979 | 2979 | OK
386 | 315 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3001 | 3000 | 3000 | OK
387 | 315 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3014 | 3013 | 3013 | OK
388 | 315 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2981 | 2979 | 2979 | OK
389 | 315 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2996 | 2996 | 2996 | OK
390 | 315 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3016 | 3016 | 3016 | OK
391 | 315 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3028 | 3028 | 3028 | OK
392 | 315 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2996 | 2996 | 2996 | OK
393 | 315 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2985 | 2984 | 2984 | OK
394 | 315 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3006 | 3005 | 3005 | OK
395 | 315 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3018 | 3018 | 3018 | OK
396 | 315 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2985 | 2984 | 2984 | OK
397 | 316 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3252 | 3253 | 3252 | OK
398 | 316 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3237 | 3238 | 3237 | OK
399 | 316 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3229 | 3230 | 3229 | OK
400 | 316 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3252 | 3253 | 3252 | OK
401 | 316 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3238 | 3237 | 3237 | OK
402 | 316 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3224 | 3224 | 3224 | OK
403 | 316 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3216 | 3216 | 3216 | OK
404 | 316 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3238 | 3237 | 3237 | OK
405 | 316 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3242 | 3244 | 3242 | OK
406 | 316 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3229 | 3230 | 3229 | OK
407 | 316 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3222 | 3222 | 3222 | OK
408 | 316 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3242 | 3244 | 3242 | OK
409 | 317 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3269 | 3268 | 3268 | OK
410 | 317 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3263 | 3263 | 3263 | OK
411 | 317 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3260 | 3260 | 3260 | OK
412 | 317 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3269 | 3268 | 3268 | OK
413 | 317 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3270 | 3272 | 3270 | OK
414 | 317 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3264 | 3266 | 3264 | OK
415 | 317 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3261 | 3262 | 3261 | OK
416 | 317 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3270 | 3272 | 3270 | OK
417 | 317 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3267 | 3267 | 3267 | OK
418 | 317 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3262 | 3261 | 3261 | OK
419 | 317 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3258 | 3258 | 3258 | OK
420 | 317 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3267 | 3267 | 3267 | OK
421 | 318 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3146 | 3147 | 3146 | OK
422 | 318 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3158 | 3158 | 3158 | OK
423 | 318 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3165 | 3165 | 3165 | OK
424 | 318 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3146 | 3147 | 3146 | OK
425 | 318 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3160 | 3159 | 3159 | OK
426 | 318 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3170 | 3169 | 3169 | OK
427 | 318 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3176 | 3176 | 3176 | OK
428 | 318 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3160 | 3159 | 3159 | OK
429 | 318 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3159 | 3160 | 3159 | OK
430 | 318 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3168 | 3169 | 3168 | OK
431 | 318 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3175 | 3175 | 3175 | OK
432 | 318 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3159 | 3160 | 3159 | OK
433 | 319 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3117 | 3116 | 3116 | OK
434 | 319 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3133 | 3132 | 3132 | OK
435 | 319 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3142 | 3141 | 3141 | OK
436 | 319 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3117 | 3116 | 3116 | OK
437 | 319 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3116 | 3115 | 3115 | OK
438 | 319 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3132 | 3131 | 3131 | OK
439 | 319 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3142 | 3142 | 3142 | OK
440 | 319 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3116 | 3115 | 3115 | OK
441 | 319 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3106 | 3105 | 3105 | OK
442 | 319 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3123 | 3121 | 3121 | OK
443 | 319 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3133 | 3132 | 3132 | OK
444 | 319 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3106 | 3105 | 3105 | OK
445 | 320 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3281 | 3284 | 3281 | OK
446 | 320 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3270 | 3273 | 3270 | OK
447 | 320 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3264 | 3265 | 3264 | OK
448 | 320 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3281 | 3284 | 3281 | OK
449 | 320 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3290 | 3294 | 3290 | OK
450 | 320 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3279 | 3282 | 3279 | OK
451 | 320 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3273 | 3274 | 3273 | OK
452 | 320 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3290 | 3294 | 3290 | OK
453 | 320 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3291 | 3292 | 3291 | OK
454 | 320 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3280 | 3281 | 3280 | OK
455 | 320 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3273 | 3273 | 3273 | OK
456 | 320 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3291 | 3292 | 3291 | OK
457 | 321 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2816 | 2809 | 2809 | OK
458 | 321 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2735 | 2730 | 2730 | OK
459 | 321 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2685 | 2683 | 2683 | OK
460 | 321 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2816 | 2809 | 2809 | OK
461 | 321 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2693 | 2684 | 2684 | OK
462 | 321 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2627 | 2620 | 2620 | OK
463 | 321 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2586 | 2583 | 2583 | OK
464 | 321 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2693 | 2684 | 2684 | OK
465 | 321 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2626 | 2627 | 2626 | OK
466 | 321 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2570 | 2571 | 2570 | OK
467 | 321 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2536 | 2537 | 2536 | OK
468 | 321 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2626 | 2627 | 2626 | OK
469 | 321A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 381 | 385 | 381 | OK
470 | 321A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 465 | 468 | 465 | OK
471 | 321A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 518 | 519 | 518 | OK
472 | 321A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 381 | 385 | 381 | OK
473 | 321A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 500 | 506 | 500 | OK
474 | 321A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 570 | 573 | 570 | OK
475 | 321A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 612 | 614 | 612 | OK
476 | 321A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 500 | 506 | 500 | OK
477 | 321A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 566 | 565 | 565 | OK
478 | 321A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 626 | 625 | 625 | OK
479 | 321A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 662 | 662 | 662 | OK
480 | 321A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 566 | 565 | 565 | OK
481 | 321A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 546 | 548 | 546 | OK
482 | 321A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 607 | 609 | 607 | OK
483 | 321A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 645 | 646 | 645 | OK
484 | 321A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 546 | 548 | 546 | OK
485 | 321A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 640 | 643 | 640 | OK
486 | 321A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 687 | 690 | 687 | OK
487 | 321A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 717 | 718 | 717 | OK
488 | 321A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 640 | 643 | 640 | OK
489 | 321A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 706 | 703 | 703 | OK
490 | 321A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 746 | 743 | 743 | OK
491 | 321A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 770 | 769 | 769 | OK
492 | 321A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 706 | 703 | 703 | OK
493 | 322 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2632 | 2629 | 2629 | OK
494 | 322 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2578 | 2575 | 2575 | OK
495 | 322 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2544 | 2543 | 2543 | OK
496 | 322 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2632 | 2629 | 2629 | OK
497 | 322 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2547 | 2543 | 2543 | OK
498 | 322 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2504 | 2500 | 2500 | OK
499 | 322 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2477 | 2476 | 2476 | OK
500 | 322 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2547 | 2543 | 2543 | OK
501 | 322 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2480 | 2485 | 2480 | OK
502 | 322 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2445 | 2448 | 2445 | OK
503 | 322 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2424 | 2425 | 2424 | OK
504 | 322 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2480 | 2485 | 2480 | OK
505 | 323 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2452 | 2452 | 2452 | OK
506 | 323 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2453 | 2453 | 2453 | OK
507 | 323 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2453 | 2453 | 2453 | OK
508 | 323 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2452 | 2452 | 2452 | OK
509 | 323 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2447 | 2446 | 2446 | OK
510 | 323 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2450 | 2450 | 2450 | OK
511 | 323 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2452 | 2451 | 2451 | OK
512 | 323 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2447 | 2446 | 2446 | OK
513 | 323 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2449 | 2447 | 2447 | OK
514 | 323 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2451 | 2450 | 2450 | OK
515 | 323 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2452 | 2451 | 2451 | OK
516 | 323 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2449 | 2447 | 2447 | OK
517 | 323A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2002 | 2003 | 2002 | OK
518 | 323A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1977 | 1977 | 1977 | OK
519 | 323A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1963 | 1963 | 1963 | OK
520 | 323A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2002 | 2003 | 2002 | OK
521 | 323A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2001 | 2004 | 2001 | OK
522 | 323A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1974 | 1976 | 1974 | OK
523 | 323A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1959 | 1960 | 1959 | OK
524 | 323A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2001 | 2004 | 2001 | OK
525 | 323A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2003 | 2003 | 2003 | OK
526 | 323A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1978 | 1978 | 1978 | OK
527 | 323A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1965 | 1965 | 1965 | OK
528 | 323A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2003 | 2003 | 2003 | OK
529 | 324 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1833 | 1835 | 1833 | OK
530 | 324 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1853 | 1855 | 1853 | OK
531 | 324 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1865 | 1865 | 1865 | OK
532 | 324 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1833 | 1835 | 1833 | OK
533 | 324 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1826 | 1826 | 1826 | OK
534 | 324 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1849 | 1849 | 1849 | OK
535 | 324 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1861 | 1861 | 1861 | OK
536 | 324 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1826 | 1826 | 1826 | OK
537 | 324 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1812 | 1812 | 1812 | OK
538 | 324 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1834 | 1834 | 1834 | OK
539 | 324 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1846 | 1846 | 1846 | OK
540 | 324 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1812 | 1812 | 1812 | OK
541 | 325 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2882 | 2881 | 2881 | OK
542 | 325 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2871 | 2870 | 2870 | OK
543 | 325 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2864 | 2864 | 2864 | OK
544 | 325 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2882 | 2881 | 2881 | OK
545 | 325 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2887 | 2886 | 2886 | OK
546 | 325 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2874 | 2874 | 2874 | OK
547 | 325 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2867 | 2867 | 2867 | OK
548 | 325 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2887 | 2886 | 2886 | OK
549 | 325 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2897 | 2895 | 2895 | OK
550 | 325 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2884 | 2883 | 2883 | OK
551 | 325 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2877 | 2876 | 2876 | OK
552 | 325 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2897 | 2895 | 2895 | OK
553 | 326 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3152 | 3149 | 3149 | OK
554 | 326 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3158 | 3155 | 3155 | OK
555 | 326 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3160 | 3160 | 3160 | OK
556 | 326 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3152 | 3149 | 3149 | OK
557 | 326 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3114 | 3113 | 3113 | OK
558 | 326 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3125 | 3124 | 3124 | OK
559 | 326 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3132 | 3131 | 3131 | OK
560 | 326 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3114 | 3113 | 3113 | OK
561 | 326 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3051 | 3053 | 3051 | OK
562 | 326 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3069 | 3071 | 3069 | OK
563 | 326 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3080 | 3081 | 3080 | OK
564 | 326 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3051 | 3053 | 3051 | OK
565 | 327 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3197 | 3203 | 3197 | OK
566 | 327 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3192 | 3196 | 3192 | OK
567 | 327 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3190 | 3192 | 3190 | OK
568 | 327 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3197 | 3203 | 3197 | OK
569 | 327 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3276 | 3280 | 3276 | OK
570 | 327 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3260 | 3262 | 3260 | OK
571 | 327 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3251 | 3252 | 3251 | OK
572 | 327 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3276 | 3280 | 3276 | OK
573 | 327 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3395 | 3392 | 3392 | OK
574 | 327 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3363 | 3360 | 3360 | OK
575 | 327 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3343 | 3342 | 3342 | OK
576 | 327 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3395 | 3392 | 3392 | OK
577 | 328 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3076 | 3072 | 3072 | OK
578 | 328 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3078 | 3075 | 3075 | OK
579 | 328 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3079 | 3078 | 3078 | OK
580 | 328 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3076 | 3072 | 3072 | OK
581 | 328 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3046 | 3043 | 3043 | OK
582 | 328 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3053 | 3050 | 3050 | OK
583 | 328 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3056 | 3055 | 3055 | OK
584 | 328 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3046 | 3043 | 3043 | OK
585 | 328 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2978 | 2981 | 2978 | OK
586 | 328 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2993 | 2995 | 2993 | OK
587 | 328 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3002 | 3003 | 3002 | OK
588 | 328 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2978 | 2981 | 2978 | OK
589 | 329 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2994 | 2994 | 2994 | OK
590 | 329 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2999 | 2998 | 2998 | OK
591 | 329 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3001 | 3001 | 3001 | OK
592 | 329 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2994 | 2994 | 2994 | OK
593 | 329 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2995 | 2995 | 2995 | OK
594 | 329 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3000 | 3000 | 3000 | OK
595 | 329 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3003 | 3003 | 3003 | OK
596 | 329 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2995 | 2995 | 2995 | OK
597 | 329 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2996 | 2994 | 2994 | OK
598 | 329 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3001 | 2999 | 2999 | OK
599 | 329 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3003 | 3003 | 3003 | OK
600 | 329 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2996 | 2994 | 2994 | OK
601 | 330 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2890 | 2891 | 2890 | OK
602 | 330 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2897 | 2897 | 2897 | OK
603 | 330 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2901 | 2902 | 2901 | OK
604 | 330 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2890 | 2891 | 2890 | OK
605 | 330 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2884 | 2885 | 2884 | OK
606 | 330 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2892 | 2893 | 2892 | OK
607 | 330 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2897 | 2898 | 2897 | OK
608 | 330 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2884 | 2885 | 2884 | OK
609 | 330 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2886 | 2887 | 2886 | OK
610 | 330 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2894 | 2895 | 2894 | OK
611 | 330 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2899 | 2899 | 2899 | OK
612 | 330 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2886 | 2887 | 2886 | OK
613 | 331 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2996 | 2997 | 2996 | OK
614 | 331 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3007 | 3008 | 3007 | OK
615 | 331 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3014 | 3014 | 3014 | OK
616 | 331 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2996 | 2997 | 2996 | OK
617 | 331 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3008 | 3007 | 3007 | OK
618 | 331 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3018 | 3017 | 3017 | OK
619 | 331 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3024 | 3023 | 3023 | OK
620 | 331 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3008 | 3007 | 3007 | OK
621 | 331 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3006 | 3006 | 3006 | OK
622 | 331 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3016 | 3016 | 3016 | OK
623 | 331 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3022 | 3022 | 3022 | OK
624 | 331 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3006 | 3006 | 3006 | OK
625 | 332 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3323 | 3322 | 3322 | OK
626 | 332 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3310 | 3309 | 3309 | OK
627 | 332 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3302 | 3302 | 3302 | OK
628 | 332 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3323 | 3322 | 3322 | OK
629 | 332 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3327 | 3327 | 3327 | OK
630 | 332 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3313 | 3313 | 3313 | OK
631 | 332 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3305 | 3305 | 3305 | OK
632 | 332 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3327 | 3327 | 3327 | OK
633 | 332 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3318 | 3316 | 3316 | OK
634 | 332 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3306 | 3304 | 3304 | OK
635 | 332 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3298 | 3297 | 3297 | OK
636 | 332 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3318 | 3316 | 3316 | OK
637 | 333 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3138 | 3127 | 3127 | OK
638 | 333 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3142 | 3134 | 3134 | OK
639 | 333 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3143 | 3140 | 3140 | OK
640 | 333 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3138 | 3127 | 3127 | OK
641 | 333 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3096 | 3087 | 3087 | OK
642 | 333 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3107 | 3100 | 3100 | OK
643 | 333 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3112 | 3109 | 3109 | OK
644 | 333 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3096 | 3087 | 3087 | OK
645 | 333 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3132 | 3124 | 3124 | OK
646 | 333 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3138 | 3131 | 3131 | OK
647 | 333 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3140 | 3137 | 3137 | OK
648 | 333 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3132 | 3124 | 3124 | OK
649 | 334 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3167 | 3189 | 3167 | OK
650 | 334 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3180 | 3196 | 3180 | OK
651 | 334 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3192 | 3198 | 3192 | OK
652 | 334 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3167 | 3189 | 3167 | OK
653 | 334 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3247 | 3264 | 3247 | OK
654 | 334 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3248 | 3261 | 3248 | OK
655 | 334 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3252 | 3257 | 3252 | OK
656 | 334 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3247 | 3264 | 3247 | OK
657 | 334 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3181 | 3200 | 3181 | OK
658 | 334 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3192 | 3206 | 3192 | OK
659 | 334 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3202 | 3208 | 3202 | OK
660 | 334 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3181 | 3200 | 3181 | OK
661 | 335 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3312 | 3304 | 3304 | OK
662 | 335 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3302 | 3296 | 3296 | OK
663 | 335 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3295 | 3292 | 3292 | OK
664 | 335 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3312 | 3304 | 3304 | OK
665 | 335 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3284 | 3277 | 3277 | OK
666 | 335 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3278 | 3274 | 3274 | OK
667 | 335 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3274 | 3272 | 3272 | OK
668 | 335 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3284 | 3277 | 3277 | OK
669 | 335 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3307 | 3299 | 3299 | OK
670 | 335 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3298 | 3292 | 3292 | OK
671 | 335 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3291 | 3289 | 3289 | OK
672 | 335 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3307 | 3299 | 3299 | OK
673 | 336 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3195 | 3193 | 3193 | OK
674 | 336 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3197 | 3195 | 3195 | OK
675 | 336 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3197 | 3196 | 3196 | OK
676 | 336 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3195 | 3193 | 3193 | OK
677 | 336 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3185 | 3184 | 3184 | OK
678 | 336 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3188 | 3188 | 3188 | OK
679 | 336 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3191 | 3190 | 3190 | OK
680 | 336 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3185 | 3184 | 3184 | OK
681 | 336 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3191 | 3188 | 3188 | OK
682 | 336 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3193 | 3191 | 3191 | OK
683 | 336 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3194 | 3194 | 3194 | OK
684 | 336 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3191 | 3188 | 3188 | OK
685 | 337 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2977 | 2975 | 2975 | OK
686 | 337 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2935 | 2933 | 2933 | OK
687 | 337 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2909 | 2908 | 2908 | OK
688 | 337 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2977 | 2975 | 2975 | OK
689 | 337 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2904 | 2901 | 2901 | OK
690 | 337 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2873 | 2871 | 2871 | OK
691 | 337 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2854 | 2853 | 2853 | OK
692 | 337 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2904 | 2901 | 2901 | OK
693 | 337 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2862 | 2863 | 2862 | OK
694 | 337 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2836 | 2837 | 2836 | OK
695 | 337 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2821 | 2821 | 2821 | OK
696 | 337 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2862 | 2863 | 2862 | OK
697 | 337A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1118 | 1120 | 1118 | OK
698 | 337A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1148 | 1149 | 1148 | OK
699 | 337A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1167 | 1167 | 1167 | OK
700 | 337A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1118 | 1120 | 1118 | OK
701 | 337A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1190 | 1192 | 1190 | OK
702 | 337A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1208 | 1210 | 1208 | OK
703 | 337A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1220 | 1220 | 1220 | OK
704 | 337A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1190 | 1192 | 1190 | OK
705 | 337A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1237 | 1237 | 1237 | OK
706 | 337A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1251 | 1250 | 1250 | OK
707 | 337A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1259 | 1258 | 1258 | OK
708 | 337A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1237 | 1237 | 1237 | OK
709 | 337A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 346 | 346 | 346 | OK
710 | 337A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 350 | 350 | 350 | OK
711 | 337A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 352 | 352 | 352 | OK
712 | 337A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 346 | 346 | 346 | OK
713 | 337A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 354 | 354 | 354 | OK
714 | 337A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 356 | 356 | 356 | OK
715 | 337A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 358 | 358 | 358 | OK
716 | 337A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 354 | 354 | 354 | OK
717 | 337A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 353 | 353 | 353 | OK
718 | 337A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 356 | 356 | 356 | OK
719 | 337A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 357 | 357 | 357 | OK
720 | 337A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 353 | 353 | 353 | OK
721 | 338 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 406 | 406 | 406 | OK
722 | 338 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 403 | 403 | 403 | OK
723 | 338 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 401 | 401 | 401 | OK
724 | 338 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 406 | 406 | 406 | OK
725 | 338 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 399 | 399 | 399 | OK
726 | 338 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 396 | 396 | 396 | OK
727 | 338 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 395 | 395 | 395 | OK
728 | 338 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 399 | 399 | 399 | OK
729 | 338 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1727 | 1726 | 1726 | OK
730 | 338 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1762 | 1761 | 1761 | OK
731 | 338 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1784 | 1783 | 1783 | OK
732 | 338 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1727 | 1726 | 1726 | OK
733 | 338 | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1224 | 1225 | 1224 | OK
734 | 338 | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1277 | 1278 | 1277 | OK
735 | 338 | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1309 | 1310 | 1309 | OK
736 | 338 | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1224 | 1225 | 1224 | OK
737 | 338 | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1299 | 1300 | 1299 | OK
738 | 338 | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1340 | 1341 | 1340 | OK
739 | 338 | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1366 | 1366 | 1366 | OK
740 | 338 | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1299 | 1300 | 1299 | OK
741 | 339 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3132 | 3130 | 3130 | OK
742 | 339 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3099 | 3097 | 3097 | OK
743 | 339 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3078 | 3077 | 3077 | OK
744 | 339 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3132 | 3130 | 3130 | OK
745 | 339 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3074 | 3072 | 3072 | OK
746 | 339 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3050 | 3049 | 3049 | OK
747 | 339 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3036 | 3035 | 3035 | OK
748 | 339 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3074 | 3072 | 3072 | OK
749 | 339 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3026 | 3028 | 3026 | OK
750 | 339 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3008 | 3009 | 3008 | OK
751 | 339 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2997 | 2997 | 2997 | OK
752 | 339 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3026 | 3028 | 3026 | OK
753 | 340 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3246 | 3248 | 3246 | OK
754 | 340 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3224 | 3225 | 3224 | OK
755 | 340 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3210 | 3211 | 3210 | OK
756 | 340 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3246 | 3248 | 3246 | OK
757 | 340 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3231 | 3232 | 3231 | OK
758 | 340 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3210 | 3210 | 3210 | OK
759 | 340 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3197 | 3197 | 3197 | OK
760 | 340 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3231 | 3232 | 3231 | OK
761 | 340 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3243 | 3242 | 3242 | OK
762 | 340 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3221 | 3220 | 3220 | OK
763 | 340 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3207 | 3207 | 3207 | OK
764 | 340 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3243 | 3242 | 3242 | OK
765 | 341 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3136 | 3135 | 3135 | OK
766 | 341 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3139 | 3138 | 3138 | OK
767 | 341 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3141 | 3140 | 3140 | OK
768 | 341 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3136 | 3135 | 3135 | OK
769 | 341 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3139 | 3138 | 3138 | OK
770 | 341 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3142 | 3142 | 3142 | OK
771 | 341 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3144 | 3144 | 3144 | OK
772 | 341 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3139 | 3138 | 3138 | OK
773 | 341 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3141 | 3139 | 3139 | OK
774 | 341 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3144 | 3143 | 3143 | OK
775 | 341 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3145 | 3145 | 3145 | OK
776 | 341 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3141 | 3139 | 3139 | OK
777 | 342 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3172 | 3175 | 3172 | OK
778 | 342 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3176 | 3179 | 3176 | OK
779 | 342 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3179 | 3180 | 3179 | OK
780 | 342 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3172 | 3175 | 3172 | OK
781 | 342 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3178 | 3181 | 3178 | OK
782 | 342 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3184 | 3186 | 3184 | OK
783 | 342 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3188 | 3188 | 3188 | OK
784 | 342 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3178 | 3181 | 3178 | OK
785 | 342 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3166 | 3168 | 3166 | OK
786 | 342 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3173 | 3175 | 3173 | OK
787 | 342 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3177 | 3178 | 3177 | OK
788 | 342 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3166 | 3168 | 3166 | OK
789 | 343 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2931 | 2926 | 2926 | OK
790 | 343 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2848 | 2844 | 2844 | OK
791 | 343 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2796 | 2795 | 2795 | OK
792 | 343 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2931 | 2926 | 2926 | OK
793 | 343 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2812 | 2808 | 2808 | OK
794 | 343 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2744 | 2741 | 2741 | OK
795 | 343 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2702 | 2701 | 2701 | OK
796 | 343 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2812 | 2808 | 2808 | OK
797 | 343 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2752 | 2754 | 2752 | OK
798 | 343 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2693 | 2694 | 2693 | OK
799 | 343 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2658 | 2658 | 2658 | OK
800 | 343 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2752 | 2754 | 2752 | OK
801 | 343A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 493 | 496 | 493 | OK
802 | 343A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 572 | 574 | 572 | OK
803 | 343A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 621 | 622 | 621 | OK
804 | 343A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 493 | 496 | 493 | OK
805 | 343A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 611 | 614 | 611 | OK
806 | 343A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 674 | 675 | 674 | OK
807 | 343A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 712 | 712 | 712 | OK
808 | 343A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 611 | 614 | 611 | OK
809 | 343A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 679 | 677 | 677 | OK
810 | 343A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 732 | 731 | 731 | OK
811 | 343A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 764 | 763 | 763 | OK
812 | 343A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 679 | 677 | 677 | OK
813 | 343A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 408 | 407 | 407 | OK
814 | 343A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 485 | 485 | 485 | OK
815 | 343A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 533 | 533 | 533 | OK
816 | 343A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 408 | 407 | 407 | OK
817 | 343A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 534 | 558 | 534 | OK
818 | 343A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 598 | 616 | 598 | OK
819 | 343A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 641 | 648 | 641 | OK
820 | 343A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 534 | 558 | 534 | OK
821 | 343A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 623 | 616 | 616 | OK
822 | 343A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 676 | 671 | 671 | OK
823 | 343A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 708 | 707 | 707 | OK
824 | 343A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 623 | 616 | 616 | OK
825 | 344 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2722 | 2746 | 2722 | OK
826 | 344 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2649 | 2666 | 2649 | OK
827 | 344 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2607 | 2614 | 2607 | OK
828 | 344 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2722 | 2746 | 2722 | OK
829 | 344 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2575 | 2536 | 2536 | OK
830 | 344 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2516 | 2487 | 2487 | OK
831 | 344 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2474 | 2463 | 2463 | OK
832 | 344 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2575 | 2536 | 2536 | OK
833 | 344 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2509 | 2546 | 2509 | OK
834 | 344 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2459 | 2486 | 2459 | OK
835 | 344 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2432 | 2443 | 2432 | OK
836 | 344 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2509 | 2546 | 2509 | OK
837 | 345 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3164 | 3113 | 3113 | OK
838 | 345 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3133 | 3095 | 3095 | OK
839 | 345 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3107 | 3092 | 3092 | OK
840 | 345 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3164 | 3113 | 3113 | OK
841 | 345 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3153 | 3093 | 3093 | OK
842 | 345 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3124 | 3079 | 3079 | OK
843 | 345 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3098 | 3081 | 3081 | OK
844 | 345 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3153 | 3093 | 3093 | OK
845 | 345 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3188 | 3221 | 3188 | OK
846 | 345 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3156 | 3180 | 3156 | OK
847 | 345 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3140 | 3149 | 3140 | OK
848 | 345 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3188 | 3221 | 3188 | OK
849 | 346 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2613 | 2648 | 2613 | OK
850 | 346 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2595 | 2622 | 2595 | OK
851 | 346 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2604 | 2615 | 2604 | OK
852 | 346 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2613 | 2648 | 2613 | OK
853 | 346 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2574 | 2542 | 2542 | OK
854 | 346 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2552 | 2528 | 2528 | OK
855 | 346 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2543 | 2534 | 2534 | OK
856 | 346 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2574 | 2542 | 2542 | OK
857 | 346 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2627 | 2667 | 2627 | OK
858 | 346 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2608 | 2640 | 2608 | OK
859 | 346 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2617 | 2631 | 2617 | OK
860 | 346 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2627 | 2667 | 2627 | OK
861 | 346A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 661 | 648 | 648 | OK
862 | 346A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 739 | 728 | 728 | OK
863 | 346A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 753 | 748 | 748 | OK
864 | 346A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 661 | 648 | 648 | OK
865 | 346A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 741 | 747 | 741 | OK
866 | 346A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 829 | 832 | 829 | OK
867 | 346A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 861 | 862 | 861 | OK
868 | 346A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 741 | 747 | 741 | OK
869 | 346A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 636 | 616 | 616 | OK
870 | 346A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 716 | 696 | 696 | OK
871 | 346A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 727 | 715 | 715 | OK
872 | 346A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 636 | 616 | 616 | OK
873 | 347 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2383 | 2390 | 2383 | OK
874 | 347 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2361 | 2367 | 2361 | OK
875 | 347 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2366 | 2369 | 2366 | OK
876 | 347 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2383 | 2390 | 2383 | OK
877 | 347 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2347 | 2356 | 2347 | OK
878 | 347 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2320 | 2328 | 2320 | OK
879 | 347 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2317 | 2321 | 2317 | OK
880 | 347 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2347 | 2356 | 2347 | OK
881 | 347 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2397 | 2410 | 2397 | OK
882 | 347 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2375 | 2387 | 2375 | OK
883 | 347 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2383 | 2390 | 2383 | OK
884 | 347 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2397 | 2410 | 2397 | OK
885 | 348 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2847 | 2844 | 2844 | OK
886 | 348 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2841 | 2838 | 2838 | OK
887 | 348 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2836 | 2835 | 2835 | OK
888 | 348 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2847 | 2844 | 2844 | OK
889 | 348 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2848 | 2845 | 2845 | OK
890 | 348 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2842 | 2840 | 2840 | OK
891 | 348 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2838 | 2838 | 2838 | OK
892 | 348 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2848 | 2845 | 2845 | OK
893 | 348 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2850 | 2846 | 2846 | OK
894 | 348 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2844 | 2840 | 2840 | OK
895 | 348 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2839 | 2838 | 2838 | OK
896 | 348 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2850 | 2846 | 2846 | OK
897 | 349 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3044 | 3024 | 3024 | OK
898 | 349 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3075 | 3060 | 3060 | OK
899 | 349 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3089 | 3083 | 3083 | OK
900 | 349 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3044 | 3024 | 3024 | OK
901 | 349 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3038 | 3022 | 3022 | OK
902 | 349 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3074 | 3063 | 3063 | OK
903 | 349 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3093 | 3089 | 3089 | OK
904 | 349 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3038 | 3022 | 3022 | OK
905 | 349 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3034 | 3014 | 3014 | OK
906 | 349 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3067 | 3052 | 3052 | OK
907 | 349 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3082 | 3076 | 3076 | OK
908 | 349 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3034 | 3014 | 3014 | OK
909 | 350 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3699 | 3744 | 3699 | OK
910 | 350 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3652 | 3685 | 3652 | OK
911 | 350 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3632 | 3644 | 3632 | OK
912 | 350 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3699 | 3744 | 3699 | OK
913 | 350 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3681 | 3718 | 3681 | OK
914 | 350 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3629 | 3656 | 3629 | OK
915 | 350 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3604 | 3614 | 3604 | OK
916 | 350 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3681 | 3718 | 3681 | OK
917 | 350 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3583 | 3635 | 3583 | OK
918 | 350 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3549 | 3588 | 3549 | OK
919 | 350 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3539 | 3553 | 3539 | OK
920 | 350 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3583 | 3635 | 3583 | OK
921 | 351 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3046 | 3027 | 3027 | OK
922 | 351 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3055 | 3042 | 3042 | OK
923 | 351 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3057 | 3052 | 3052 | OK
924 | 351 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3046 | 3027 | 3027 | OK
925 | 351 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3119 | 3102 | 3102 | OK
926 | 351 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3121 | 3108 | 3108 | OK
927 | 351 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3119 | 3115 | 3115 | OK
928 | 351 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3119 | 3102 | 3102 | OK
929 | 351 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3289 | 3257 | 3257 | OK
930 | 351 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3269 | 3244 | 3244 | OK
931 | 351 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3251 | 3241 | 3241 | OK
932 | 351 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3289 | 3257 | 3257 | OK
933 | 352 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3037 | 3045 | 3037 | OK
934 | 352 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3054 | 3058 | 3054 | OK
935 | 352 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3063 | 3065 | 3063 | OK
936 | 352 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3037 | 3045 | 3037 | OK
937 | 352 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3010 | 3009 | 3009 | OK
938 | 352 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3032 | 3031 | 3031 | OK
939 | 352 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3044 | 3044 | 3044 | OK
940 | 352 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3010 | 3009 | 3009 | OK
941 | 352 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2919 | 2928 | 2919 | OK
942 | 352 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2949 | 2956 | 2949 | OK
943 | 352 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2967 | 2970 | 2967 | OK
944 | 352 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2919 | 2928 | 2919 | OK
945 | 353A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4069 | 4026 | 4026 | OK
946 | 353A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3820 | 3792 | 3792 | OK
947 | 353A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3662 | 3652 | 3652 | OK
948 | 353A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4069 | 4026 | 4026 | OK
949 | 353A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4347 | 4332 | 4332 | OK
950 | 353A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 4043 | 4033 | 4033 | OK
951 | 353A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3854 | 3851 | 3851 | OK
952 | 353A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4347 | 4332 | 4332 | OK
953 | 353A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4069 | 4042 | 4042 | OK
954 | 353A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3819 | 3802 | 3802 | OK
955 | 353A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3664 | 3657 | 3657 | OK
956 | 353A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4069 | 4042 | 4042 | OK
957 | 353 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -1200 | -1186 | -1200 | NG
958 | 353 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -910 | -901 | -910 | NG
959 | 353 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | -729 | -726 | -729 | NG
960 | 353 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -1200 | -1186 | -1200 | NG
961 | 353 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -905 | -875 | -905 | NG
962 | 353 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -672 | -651 | -672 | NG
963 | 353 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | -523 | -516 | -523 | NG
964 | 353 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -905 | -875 | -905 | NG
965 | 353 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -903 | -883 | -903 | NG
966 | 353 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -668 | -655 | -668 | NG
967 | 353 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | -521 | -516 | -521 | NG
968 | 353 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -903 | -883 | -903 | NG
969 | 353 | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -186 | -188 | -188 | NG
970 | 353 | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -10 | -12 | -12 | NG
971 | 353 | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 98 | 98 | 98 | OK
972 | 353 | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -186 | -188 | -188 | NG
973 | 353 | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 180 | 189 | 180 | OK
974 | 353 | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 306 | 313 | 306 | OK
975 | 353 | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 385 | 388 | 385 | OK
976 | 353 | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 180 | 189 | 180 | OK
977 | 353 | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 115 | 120 | 115 | OK
978 | 353 | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 249 | 252 | 249 | OK
979 | 353 | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 332 | 333 | 332 | OK
980 | 353 | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 115 | 120 | 115 | OK
981 | 354 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3080 | 3061 | 3061 | OK
982 | 354 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2984 | 2970 | 2970 | OK
983 | 354 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2921 | 2916 | 2916 | OK
984 | 354 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3080 | 3061 | 3061 | OK
985 | 354 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3359 | 3367 | 3359 | OK
986 | 354 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3227 | 3233 | 3227 | OK
987 | 354 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3146 | 3148 | 3146 | OK
988 | 354 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3359 | 3367 | 3359 | OK
989 | 354 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3132 | 3119 | 3119 | OK
990 | 354 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3029 | 3020 | 3020 | OK
991 | 354 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2964 | 2961 | 2961 | OK
992 | 354 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3132 | 3119 | 3119 | OK
993 | 356 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2820 | 2822 | 2820 | OK
994 | 356 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2853 | 2855 | 2853 | OK
995 | 356 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2873 | 2873 | 2873 | OK
996 | 356 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2820 | 2822 | 2820 | OK
997 | 356 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2735 | 2743 | 2735 | OK
998 | 356 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2778 | 2784 | 2778 | OK
999 | 356 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2804 | 2807 | 2804 | OK
1000 | 356 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2735 | 2743 | 2735 | OK
1001 | 356 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2804 | 2796 | 2796 | OK
1002 | 356 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2837 | 2831 | 2831 | OK
1003 | 356 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2855 | 2853 | 2853 | OK
1004 | 356 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2804 | 2796 | 2796 | OK
1005 | 357 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2827 | 2824 | 2824 | OK
1006 | 357 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2822 | 2820 | 2820 | OK
1007 | 357 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2820 | 2819 | 2819 | OK
1008 | 357 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2827 | 2824 | 2824 | OK
1009 | 357 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2824 | 2835 | 2824 | OK
1010 | 357 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2821 | 2830 | 2821 | OK
1011 | 357 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2821 | 2825 | 2821 | OK
1012 | 357 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2824 | 2835 | 2824 | OK
1013 | 357 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2834 | 2833 | 2833 | OK
1014 | 357 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2829 | 2829 | 2829 | OK
1015 | 357 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2827 | 2826 | 2826 | OK
1016 | 357 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2834 | 2833 | 2833 | OK
1017 | 358 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2582 | 2600 | 2582 | OK
1018 | 358 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2605 | 2619 | 2605 | OK
1019 | 358 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2621 | 2626 | 2621 | OK
1020 | 358 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2582 | 2600 | 2582 | OK
1021 | 358 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2613 | 2553 | 2553 | OK
1022 | 358 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2624 | 2580 | 2580 | OK
1023 | 358 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2621 | 2604 | 2604 | OK
1024 | 358 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2613 | 2553 | 2553 | OK
1025 | 358 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2583 | 2601 | 2583 | OK
1026 | 358 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2606 | 2619 | 2606 | OK
1027 | 358 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2621 | 2627 | 2621 | OK
1028 | 358 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2583 | 2601 | 2583 | OK
1029 | 359A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2489 | 2417 | 2417 | OK
1030 | 359A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2435 | 2382 | 2382 | OK
1031 | 359A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2391 | 2372 | 2372 | OK
1032 | 359A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2489 | 2417 | 2417 | OK
1033 | 359A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2328 | 2268 | 2268 | OK
1034 | 359A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2290 | 2245 | 2245 | OK
1035 | 359A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2257 | 2240 | 2240 | OK
1036 | 359A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2328 | 2268 | 2268 | OK
1037 | 359A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2251 | 2584 | 2251 | OK
1038 | 359A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2260 | 2479 | 2260 | OK
1039 | 359A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2303 | 2381 | 2303 | OK
1040 | 359A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2251 | 2584 | 2251 | OK
1041 | 359 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1526 | 1593 | 1526 | OK
1042 | 359 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1496 | 1544 | 1496 | OK
1043 | 359 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1488 | 1506 | 1488 | OK
1044 | 359 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1526 | 1593 | 1526 | OK
1045 | 359 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1876 | 1463 | 1463 | OK
1046 | 359 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1776 | 1511 | 1511 | OK
1047 | 359 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1675 | 1583 | 1583 | OK
1048 | 359 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1876 | 1463 | 1463 | OK
1049 | 359 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1793 | 1833 | 1793 | OK
1050 | 359 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1739 | 1769 | 1739 | OK
1051 | 359 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1716 | 1727 | 1716 | OK
1052 | 359 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1793 | 1833 | 1793 | OK
1053 | 360 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1967 | 1956 | 1956 | OK
1054 | 360 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1986 | 1978 | 1978 | OK
1055 | 360 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1994 | 1992 | 1992 | OK
1056 | 360 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1967 | 1956 | 1956 | OK
1057 | 360 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1823 | 1951 | 1823 | OK
1058 | 360 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1860 | 1941 | 1860 | OK
1059 | 360 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1892 | 1920 | 1892 | OK
1060 | 360 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1823 | 1951 | 1823 | OK
1061 | 360 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1821 | 1827 | 1821 | OK
1062 | 360 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1853 | 1857 | 1853 | OK
1063 | 360 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1869 | 1871 | 1869 | OK
1064 | 360 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1821 | 1827 | 1821 | OK
1065 | 361 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3105 | 3106 | 3105 | OK
1066 | 361 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3130 | 3132 | 3130 | OK
1067 | 361 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3147 | 3147 | 3147 | OK
1068 | 361 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3105 | 3106 | 3105 | OK
1069 | 361 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3108 | 3108 | 3108 | OK
1070 | 361 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3133 | 3133 | 3133 | OK
1071 | 361 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3148 | 3148 | 3148 | OK
1072 | 361 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3108 | 3108 | 3108 | OK
1073 | 361 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3142 | 3141 | 3141 | OK
1074 | 361 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3162 | 3162 | 3162 | OK
1075 | 361 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3176 | 3175 | 3175 | OK
1076 | 361 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3142 | 3141 | 3141 | OK
1077 | 362 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3191 | 3191 | 3191 | OK
1078 | 362 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3207 | 3207 | 3207 | OK
1079 | 362 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3216 | 3216 | 3216 | OK
1080 | 362 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3191 | 3191 | 3191 | OK
1081 | 362 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3211 | 3211 | 3211 | OK
1082 | 362 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3224 | 3224 | 3224 | OK
1083 | 362 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3232 | 3232 | 3232 | OK
1084 | 362 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3211 | 3211 | 3211 | OK
1085 | 362 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3225 | 3222 | 3222 | OK
1086 | 362 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3237 | 3234 | 3234 | OK
1087 | 362 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3244 | 3243 | 3243 | OK
1088 | 362 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3225 | 3222 | 3222 | OK
1089 | 363 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2443 | 2439 | 2439 | OK
1090 | 363 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2412 | 2409 | 2409 | OK
1091 | 363 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2393 | 2392 | 2392 | OK
1092 | 363 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2443 | 2439 | 2439 | OK
1093 | 363 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2321 | 2317 | 2317 | OK
1094 | 363 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2304 | 2301 | 2301 | OK
1095 | 363 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2293 | 2292 | 2292 | OK
1096 | 363 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2321 | 2317 | 2317 | OK
1097 | 363 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2217 | 2223 | 2217 | OK
1098 | 363 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2213 | 2218 | 2213 | OK
1099 | 363 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2212 | 2214 | 2212 | OK
1100 | 363 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2217 | 2223 | 2217 | OK
1101 | 363A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 776 | 779 | 776 | OK
1102 | 363A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 809 | 811 | 809 | OK
1103 | 363A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 830 | 831 | 830 | OK
1104 | 363A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 776 | 779 | 776 | OK
1105 | 363A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 877 | 880 | 877 | OK
1106 | 363A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 899 | 901 | 899 | OK
1107 | 363A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 913 | 914 | 913 | OK
1108 | 363A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 877 | 880 | 877 | OK
1109 | 363A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 963 | 959 | 959 | OK
1110 | 363A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 973 | 970 | 970 | OK
1111 | 363A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 979 | 978 | 978 | OK
1112 | 363A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 963 | 959 | 959 | OK
1113 | 363A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 244 | 252 | 244 | OK
1114 | 363A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 342 | 347 | 342 | OK
1115 | 363A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 403 | 405 | 403 | OK
1116 | 363A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 244 | 252 | 244 | OK
1117 | 363A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 346 | 351 | 346 | OK
1118 | 363A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 431 | 434 | 431 | OK
1119 | 363A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 484 | 485 | 484 | OK
1120 | 363A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 346 | 351 | 346 | OK
1121 | 363A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 426 | 433 | 426 | OK
1122 | 363A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 499 | 504 | 499 | OK
1123 | 363A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 545 | 547 | 545 | OK
1124 | 363A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 426 | 433 | 426 | OK
1125 | 364 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3023 | 3011 | 3011 | OK
1126 | 364 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2883 | 2876 | 2876 | OK
1127 | 364 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2797 | 2794 | 2794 | OK
1128 | 364 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3023 | 3011 | 3011 | OK
1129 | 364 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2836 | 2830 | 2830 | OK
1130 | 364 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2721 | 2717 | 2717 | OK
1131 | 364 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2650 | 2649 | 2649 | OK
1132 | 364 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2836 | 2830 | 2830 | OK
1133 | 364 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2848 | 2832 | 2832 | OK
1134 | 364 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2731 | 2719 | 2719 | OK
1135 | 364 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2657 | 2653 | 2653 | OK
1136 | 364 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2848 | 2832 | 2832 | OK
1137 | 367 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4232 | 4209 | 4209 | OK
1138 | 367 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 4070 | 4056 | 4056 | OK
1139 | 367 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3971 | 3966 | 3966 | OK
1140 | 367 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4232 | 4209 | 4209 | OK
1141 | 367 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4228 | 4217 | 4217 | OK
1142 | 367 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 4068 | 4061 | 4061 | OK
1143 | 367 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3970 | 3968 | 3968 | OK
1144 | 367 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4228 | 4217 | 4217 | OK
1145 | 367 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4213 | 4178 | 4178 | OK
1146 | 367 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 4049 | 4026 | 4026 | OK
1147 | 367 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3947 | 3939 | 3939 | OK
1148 | 367 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 4213 | 4178 | 4178 | OK
1149 | 368 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2599 | 2538 | 2538 | OK
1150 | 368 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2595 | 2561 | 2561 | OK
1151 | 368 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2589 | 2578 | 2578 | OK
1152 | 368 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2599 | 2538 | 2538 | OK
1153 | 368 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2525 | 2464 | 2464 | OK
1154 | 368 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2533 | 2498 | 2498 | OK
1155 | 368 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2533 | 2522 | 2522 | OK
1156 | 368 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2525 | 2464 | 2464 | OK
1157 | 368 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2613 | 2557 | 2557 | OK
1158 | 368 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2610 | 2580 | 2580 | OK
1159 | 368 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2605 | 2596 | 2596 | OK
1160 | 368 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2613 | 2557 | 2557 | OK
1161 | 369 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3067 | 3189 | 3067 | OK
1162 | 369 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3104 | 3173 | 3104 | OK
1163 | 369 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3135 | 3156 | 3135 | OK
1164 | 369 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3067 | 3189 | 3067 | OK
1165 | 369 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3071 | 3187 | 3071 | OK
1166 | 369 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3105 | 3171 | 3105 | OK
1167 | 369 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3133 | 3154 | 3133 | OK
1168 | 369 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3071 | 3187 | 3071 | OK
1169 | 369 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3060 | 3179 | 3060 | OK
1170 | 369 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3097 | 3164 | 3097 | OK
1171 | 369 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3127 | 3147 | 3127 | OK
1172 | 369 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3060 | 3179 | 3060 | OK
1173 | 370A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3106 | 3063 | 3063 | OK
1174 | 370A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3086 | 3063 | 3063 | OK
1175 | 370A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3072 | 3065 | 3065 | OK
1176 | 370A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3106 | 3063 | 3063 | OK
1177 | 370A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3135 | 3092 | 3092 | OK
1178 | 370A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3111 | 3089 | 3089 | OK
1179 | 370A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3095 | 3089 | 3089 | OK
1180 | 370A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3135 | 3092 | 3092 | OK
1181 | 370A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3113 | 3072 | 3072 | OK
1182 | 370A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3093 | 3072 | 3072 | OK
1183 | 370A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3080 | 3074 | 3074 | OK
1184 | 370A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3113 | 3072 | 3072 | OK
1185 | 371A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2766 | 2761 | 2761 | OK
1186 | 371A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2804 | 2799 | 2799 | OK
1187 | 371A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2825 | 2824 | 2824 | OK
1188 | 371A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2766 | 2761 | 2761 | OK
1189 | 371A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2840 | 2834 | 2834 | OK
1190 | 371A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2869 | 2864 | 2864 | OK
1191 | 371A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2886 | 2884 | 2884 | OK
1192 | 371A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2840 | 2834 | 2834 | OK
1193 | 371A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2761 | 2763 | 2761 | OK
1194 | 371A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2800 | 2802 | 2800 | OK
1195 | 371A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2824 | 2825 | 2824 | OK
1196 | 371A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2761 | 2763 | 2761 | OK
1197 | 372 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2822 | 2827 | 2822 | OK
1198 | 372 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2841 | 2844 | 2841 | OK
1199 | 372 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2852 | 2853 | 2852 | OK
1200 | 372 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2822 | 2827 | 2822 | OK
1201 | 372 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2701 | 2724 | 2701 | OK
1202 | 372 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2736 | 2753 | 2736 | OK
1203 | 372 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2760 | 2766 | 2760 | OK
1204 | 372 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2701 | 2724 | 2701 | OK
1205 | 372 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2855 | 2843 | 2843 | OK
1206 | 372 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2869 | 2859 | 2859 | OK
1207 | 372 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2875 | 2871 | 2871 | OK
1208 | 372 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2855 | 2843 | 2843 | OK
1209 | 373A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2872 | 2930 | 2872 | OK
1210 | 373A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2854 | 2894 | 2854 | OK
1211 | 373A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2850 | 2864 | 2850 | OK
1212 | 373A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2872 | 2930 | 2872 | OK
1213 | 373A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3004 | 2994 | 2994 | OK
1214 | 373A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2969 | 2962 | 2962 | OK
1215 | 373A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2947 | 2945 | 2945 | OK
1216 | 373A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3004 | 2994 | 2994 | OK
1217 | 373A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2885 | 2954 | 2885 | OK
1218 | 373A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2866 | 2916 | 2866 | OK
1219 | 373A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2864 | 2882 | 2864 | OK
1220 | 373A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2885 | 2954 | 2885 | OK
1221 | 374 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2687 | 2563 | 2563 | OK
1222 | 374 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2673 | 2586 | 2586 | OK
1223 | 374 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2651 | 2620 | 2620 | OK
1224 | 374 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2687 | 2563 | 2563 | OK
1225 | 374 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2473 | 2355 | 2355 | OK
1226 | 374 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2486 | 2402 | 2402 | OK
1227 | 374 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2481 | 2450 | 2450 | OK
1228 | 374 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2473 | 2355 | 2355 | OK
1229 | 374 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2555 | 2537 | 2537 | OK
1230 | 374 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2556 | 2542 | 2542 | OK
1231 | 374 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2554 | 2548 | 2548 | OK
1232 | 374 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2555 | 2537 | 2537 | OK
1233 | 375 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2424 | 2498 | 2424 | OK
1234 | 375 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2446 | 2499 | 2446 | OK
1235 | 375 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2467 | 2487 | 2467 | OK
1236 | 375 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2424 | 2498 | 2424 | OK
1237 | 375 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2550 | 2552 | 2550 | OK
1238 | 375 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2556 | 2557 | 2556 | OK
1239 | 375 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2559 | 2560 | 2559 | OK
1240 | 375 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2550 | 2552 | 2550 | OK
1241 | 375 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2707 | 2765 | 2707 | OK
1242 | 375 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2692 | 2733 | 2692 | OK
1243 | 375 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2689 | 2704 | 2689 | OK
1244 | 375 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2707 | 2765 | 2707 | OK
1245 | 376 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2779 | 2770 | 2770 | OK
1246 | 376 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2773 | 2765 | 2765 | OK
1247 | 376 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2767 | 2764 | 2764 | OK
1248 | 376 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2779 | 2770 | 2770 | OK
1249 | 376 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2722 | 2730 | 2722 | OK
1250 | 376 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2723 | 2730 | 2723 | OK
1251 | 376 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2725 | 2728 | 2725 | OK
1252 | 376 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2722 | 2730 | 2722 | OK
1253 | 376 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2673 | 2673 | 2673 | OK
1254 | 376 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2679 | 2680 | 2679 | OK
1255 | 376 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2683 | 2683 | 2683 | OK
1256 | 376 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2673 | 2673 | 2673 | OK
1257 | 377 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2945 | 2948 | 2945 | OK
1258 | 377 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2946 | 2948 | 2946 | OK
1259 | 377 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2946 | 2947 | 2946 | OK
1260 | 377 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2945 | 2948 | 2945 | OK
1261 | 377 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2937 | 2940 | 2937 | OK
1262 | 377 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2940 | 2942 | 2940 | OK
1263 | 377 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2942 | 2942 | 2942 | OK
1264 | 377 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2937 | 2940 | 2937 | OK
1265 | 377 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2955 | 2953 | 2953 | OK
1266 | 377 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2956 | 2955 | 2955 | OK
1267 | 377 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2956 | 2956 | 2956 | OK
1268 | 377 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2955 | 2953 | 2953 | OK
1269 | 378 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2780 | 2776 | 2776 | OK
1270 | 378 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2710 | 2707 | 2707 | OK
1271 | 378 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2667 | 2666 | 2666 | OK
1272 | 378 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2780 | 2776 | 2776 | OK
1273 | 378 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2674 | 2671 | 2671 | OK
1274 | 378 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2619 | 2617 | 2617 | OK
1275 | 378 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2585 | 2584 | 2584 | OK
1276 | 378 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2674 | 2671 | 2671 | OK
1277 | 378 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2595 | 2597 | 2595 | OK
1278 | 378 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2550 | 2552 | 2550 | OK
1279 | 378 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2524 | 2525 | 2524 | OK
1280 | 378 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2595 | 2597 | 2595 | OK
1281 | 378A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 402 | 402 | 402 | OK
1282 | 378A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 488 | 489 | 488 | OK
1283 | 378A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 542 | 542 | 542 | OK
1284 | 378A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 402 | 402 | 402 | OK
1285 | 378A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 512 | 512 | 512 | OK
1286 | 378A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 583 | 583 | 583 | OK
1287 | 378A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 626 | 626 | 626 | OK
1288 | 378A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 512 | 512 | 512 | OK
1289 | 378A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 584 | 581 | 581 | OK
1290 | 378A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 645 | 643 | 643 | OK
1291 | 378A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 682 | 681 | 681 | OK
1292 | 378A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 584 | 581 | 581 | OK
1293 | 378A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 406 | 410 | 406 | OK
1294 | 378A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 483 | 486 | 483 | OK
1295 | 378A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 530 | 531 | 530 | OK
1296 | 378A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 406 | 410 | 406 | OK
1297 | 378A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 520 | 525 | 520 | OK
1298 | 378A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 581 | 585 | 581 | OK
1299 | 378A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 619 | 621 | 619 | OK
1300 | 378A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 520 | 525 | 520 | OK
1301 | 378A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 602 | 601 | 601 | OK
1302 | 378A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 652 | 651 | 651 | OK
1303 | 378A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 682 | 681 | 681 | OK
1304 | 378A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 602 | 601 | 601 | OK
1305 | 379 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2918 | 2910 | 2910 | OK
1306 | 379 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2818 | 2813 | 2813 | OK
1307 | 379 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2756 | 2754 | 2754 | OK
1308 | 379 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2918 | 2910 | 2910 | OK
1309 | 379 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2792 | 2785 | 2785 | OK
1310 | 379 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2708 | 2703 | 2703 | OK
1311 | 379 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2656 | 2654 | 2654 | OK
1312 | 379 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2792 | 2785 | 2785 | OK
1313 | 379 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2727 | 2728 | 2727 | OK
1314 | 379 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2653 | 2653 | 2653 | OK
1315 | 379 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2608 | 2608 | 2608 | OK
1316 | 379 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2727 | 2728 | 2727 | OK
1317 | 380 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3225 | 3228 | 3225 | OK
1318 | 380 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3222 | 3224 | 3222 | OK
1319 | 380 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3220 | 3221 | 3220 | OK
1320 | 380 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3225 | 3228 | 3225 | OK
1321 | 380 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3236 | 3235 | OK
1322 | 380 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3232 | 3233 | 3232 | OK
1323 | 380 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3230 | 3230 | 3230 | OK
1324 | 380 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3236 | 3235 | OK
1325 | 380 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3227 | 3229 | 3227 | OK
1326 | 380 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3225 | 3227 | 3225 | OK
1327 | 380 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3224 | 3224 | 3224 | OK
1328 | 380 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3227 | 3229 | 3227 | OK
1329 | 381 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3028 | 3031 | 3028 | OK
1330 | 381 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3058 | 3060 | 3058 | OK
1331 | 381 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3076 | 3076 | 3076 | OK
1332 | 381 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3028 | 3031 | 3028 | OK
1333 | 381 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2964 | 2969 | 2964 | OK
1334 | 381 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3003 | 3007 | 3003 | OK
1335 | 381 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3027 | 3029 | 3027 | OK
1336 | 381 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2964 | 2969 | 2964 | OK
1337 | 381 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3015 | 3011 | 3011 | OK
1338 | 381 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3046 | 3043 | 3043 | OK
1339 | 381 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3063 | 3062 | 3062 | OK
1340 | 381 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3015 | 3011 | 3011 | OK
1341 | 384 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2872 | 2878 | 2872 | OK
1342 | 384 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2896 | 2901 | 2896 | OK
1343 | 384 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2912 | 2914 | 2912 | OK
1344 | 384 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2872 | 2878 | 2872 | OK
1345 | 384 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2816 | 2823 | 2816 | OK
1346 | 384 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2850 | 2856 | 2850 | OK
1347 | 384 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2871 | 2873 | 2871 | OK
1348 | 384 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2816 | 2823 | 2816 | OK
1349 | 384 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2866 | 2864 | 2864 | OK
1350 | 384 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2891 | 2889 | 2889 | OK
1351 | 384 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2905 | 2904 | 2904 | OK
1352 | 384 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2866 | 2864 | 2864 | OK
1353 | 385 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3287 | 3282 | 3282 | OK
1354 | 385 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3259 | 3256 | 3256 | OK
1355 | 385 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3242 | 3241 | 3241 | OK
1356 | 385 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3287 | 3282 | 3282 | OK
1357 | 385 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3259 | 3255 | 3255 | OK
1358 | 385 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3235 | 3232 | 3232 | OK
1359 | 385 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3221 | 3219 | 3219 | OK
1360 | 385 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3259 | 3255 | 3255 | OK
1361 | 385 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3294 | 3292 | 3292 | OK
1362 | 385 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3266 | 3265 | 3265 | OK
1363 | 385 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3249 | 3249 | 3249 | OK
1364 | 385 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3294 | 3292 | 3292 | OK
1365 | 386 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3226 | 3231 | 3226 | OK
1366 | 386 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3224 | 3228 | 3224 | OK
1367 | 386 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3224 | 3225 | 3224 | OK
1368 | 386 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3226 | 3231 | 3226 | OK
1369 | 386 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3240 | 3243 | 3240 | OK
1370 | 386 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3236 | 3239 | 3236 | OK
1371 | 386 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3235 | 3236 | 3235 | OK
1372 | 386 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3240 | 3243 | 3240 | OK
1373 | 386 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3230 | 3232 | 3230 | OK
1374 | 386 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3228 | 3230 | 3228 | OK
1375 | 386 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3227 | 3227 | 3227 | OK
1376 | 386 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3230 | 3232 | 3230 | OK
1377 | 387 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3036 | 3046 | 3036 | OK
1378 | 387 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3060 | 3067 | 3060 | OK
1379 | 387 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3076 | 3079 | 3076 | OK
1380 | 387 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3036 | 3046 | 3036 | OK
1381 | 387 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3042 | 3052 | 3042 | OK
1382 | 387 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3068 | 3076 | 3068 | OK
1383 | 387 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3085 | 3088 | 3085 | OK
1384 | 387 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3042 | 3052 | 3042 | OK
1385 | 387 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3027 | 3025 | 3025 | OK
1386 | 387 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3053 | 3051 | 3051 | OK
1387 | 387 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3068 | 3068 | 3068 | OK
1388 | 387 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3027 | 3025 | 3025 | OK
1389 | 388 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2994 | 2985 | 2985 | OK
1390 | 388 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2959 | 2951 | 2951 | OK
1391 | 388 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2936 | 2932 | 2932 | OK
1392 | 388 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2994 | 2985 | 2985 | OK
1393 | 388 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2784 | 2775 | 2775 | OK
1394 | 388 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2778 | 2769 | 2769 | OK
1395 | 388 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2772 | 2768 | 2768 | OK
1396 | 388 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2784 | 2775 | 2775 | OK
1397 | 388 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2749 | 2769 | 2749 | OK
1398 | 388 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2747 | 2761 | 2747 | OK
1399 | 388 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2748 | 2753 | 2748 | OK
1400 | 388 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2749 | 2769 | 2749 | OK
1401 | 389 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2201 | 2195 | 2195 | OK
1402 | 389 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2276 | 2275 | 2275 | OK
1403 | 389 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2324 | 2324 | 2324 | OK
1404 | 389 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2201 | 2195 | 2195 | OK
1405 | 389 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2702 | 2663 | 2663 | OK
1406 | 389 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2711 | 2684 | 2684 | OK
1407 | 389 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2712 | 2703 | 2703 | OK
1408 | 389 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2702 | 2663 | 2663 | OK
1409 | 389 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2643 | 2638 | 2638 | OK
1410 | 389 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2656 | 2657 | 2656 | OK
1411 | 389 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2666 | 2668 | 2666 | OK
1412 | 389 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2643 | 2638 | 2638 | OK
1413 | 390 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2906 | 2896 | 2896 | OK
1414 | 390 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2875 | 2866 | 2866 | OK
1415 | 390 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2854 | 2850 | 2850 | OK
1416 | 390 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2906 | 2896 | 2896 | OK
1417 | 390 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2679 | 2669 | 2669 | OK
1418 | 390 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2679 | 2669 | 2669 | OK
1419 | 390 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2677 | 2672 | 2672 | OK
1420 | 390 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2679 | 2669 | 2669 | OK
1421 | 390 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2636 | 2657 | 2636 | OK
1422 | 390 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2641 | 2655 | 2641 | OK
1423 | 390 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2646 | 2651 | 2646 | OK
1424 | 390 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2636 | 2657 | 2636 | OK
1425 | 391 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2279 | 2288 | 2279 | OK
1426 | 391 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2249 | 2255 | 2249 | OK
1427 | 391 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2232 | 2234 | 2232 | OK
1428 | 391 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2279 | 2288 | 2279 | OK
1429 | 391 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2185 | 2190 | 2185 | OK
1430 | 391 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2167 | 2171 | 2167 | OK
1431 | 391 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2157 | 2158 | 2157 | OK
1432 | 391 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2185 | 2190 | 2185 | OK
1433 | 391 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2081 | 2089 | 2081 | OK
1434 | 391 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2074 | 2080 | 2074 | OK
1435 | 391 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2070 | 2073 | 2070 | OK
1436 | 391 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2081 | 2089 | 2081 | OK
1437 | 391A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 706 | 709 | 706 | OK
1438 | 391A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 741 | 743 | 741 | OK
1439 | 391A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 762 | 764 | 762 | OK
1440 | 391A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 706 | 709 | 706 | OK
1441 | 391A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 805 | 811 | 805 | OK
1442 | 391A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 826 | 831 | 826 | OK
1443 | 391A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 841 | 843 | 841 | OK
1444 | 391A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 805 | 811 | 805 | OK
1445 | 391A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 918 | 911 | 911 | OK
1446 | 391A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 927 | 922 | 922 | OK
1447 | 391A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 932 | 930 | 930 | OK
1448 | 391A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 918 | 911 | 911 | OK
1449 | 391A | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 394 | 411 | 394 | OK
1450 | 391A | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 478 | 490 | 478 | OK
1451 | 391A | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 531 | 535 | 531 | OK
1452 | 391A | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 394 | 411 | 394 | OK
1453 | 391A | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 402 | 418 | 402 | OK
1454 | 391A | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 486 | 497 | 486 | OK
1455 | 391A | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 538 | 542 | 538 | OK
1456 | 391A | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 402 | 418 | 402 | OK
1457 | 391A | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 624 | 626 | 624 | OK
1458 | 391A | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 676 | 677 | 676 | OK
1459 | 391A | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 707 | 708 | 707 | OK
1460 | 391A | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 624 | 626 | 624 | OK
1461 | 392A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3222 | 3198 | 3198 | OK
1462 | 392A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3092 | 3075 | 3075 | OK
1463 | 392A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3011 | 3005 | 3005 | OK
1464 | 392A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3222 | 3198 | 3198 | OK
1465 | 392A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3186 | 3163 | 3163 | OK
1466 | 392A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3058 | 3042 | 3042 | OK
1467 | 392A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2978 | 2972 | 2972 | OK
1468 | 392A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3186 | 3163 | 3163 | OK
1469 | 392A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2986 | 2984 | 2984 | OK
1470 | 392A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2888 | 2887 | 2887 | OK
1471 | 392A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2829 | 2829 | 2829 | OK
1472 | 392A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2986 | 2984 | 2984 | OK
1473 | 393A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2904 | 2911 | 2904 | OK
1474 | 393A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2949 | 2954 | 2949 | OK
1475 | 393A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2976 | 2978 | 2976 | OK
1476 | 393A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2904 | 2911 | 2904 | OK
1477 | 393A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2936 | 2943 | 2936 | OK
1478 | 393A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2980 | 2985 | 2980 | OK
1479 | 393A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3008 | 3009 | 3008 | OK
1480 | 393A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2936 | 2943 | 2936 | OK
1481 | 393A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2907 | 2908 | 2907 | OK
1482 | 393A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2953 | 2953 | 2953 | OK
1483 | 393A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2979 | 2980 | 2979 | OK
1484 | 393A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2907 | 2908 | 2907 | OK
1485 | 394A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3516 | 3517 | 3516 | OK
1486 | 394A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3491 | 3492 | 3491 | OK
1487 | 394A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3477 | 3477 | 3477 | OK
1488 | 394A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3516 | 3517 | 3516 | OK
1489 | 394A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3502 | 3503 | 3502 | OK
1490 | 394A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3477 | 3478 | 3477 | OK
1491 | 394A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3463 | 3463 | 3463 | OK
1492 | 394A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3502 | 3503 | 3502 | OK
1493 | 394A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3515 | 3515 | 3515 | OK
1494 | 394A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3490 | 3490 | 3490 | OK
1495 | 394A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3476 | 3476 | 3476 | OK
1496 | 394A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3515 | 3515 | 3515 | OK
1497 | 395A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3118 | 3116 | 3116 | OK
1498 | 395A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3133 | 3132 | 3132 | OK
1499 | 395A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3141 | 3141 | 3141 | OK
1500 | 395A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3118 | 3116 | 3116 | OK
1501 | 395A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3128 | 3128 | 3128 | OK
1502 | 395A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3143 | 3143 | 3143 | OK
1503 | 395A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3152 | 3152 | 3152 | OK
1504 | 395A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3128 | 3128 | 3128 | OK
1505 | 395A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3117 | 3117 | 3117 | OK
1506 | 395A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3132 | 3132 | 3132 | OK
1507 | 395A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3142 | 3142 | 3142 | OK
1508 | 395A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3117 | 3117 | 3117 | OK
1509 | 396A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3435 | 3437 | 3435 | OK
1510 | 396A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3402 | 3403 | 3402 | OK
1511 | 396A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3382 | 3382 | 3382 | OK
1512 | 396A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3435 | 3437 | 3435 | OK
1513 | 396A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3374 | 3374 | 3374 | OK
1514 | 396A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3350 | 3349 | 3349 | OK
1515 | 396A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3335 | 3335 | 3335 | OK
1516 | 396A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3374 | 3374 | 3374 | OK
1517 | 396A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3348 | 3347 | 3347 | OK
1518 | 396A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3326 | 3325 | 3325 | OK
1519 | 396A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3313 | 3312 | 3312 | OK
1520 | 396A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3348 | 3347 | 3347 | OK
1521 | 397A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3181 | 3180 | 3180 | OK
1522 | 397A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3237 | 3236 | 3236 | OK
1523 | 397A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3270 | 3270 | 3270 | OK
1524 | 397A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3181 | 3180 | 3180 | OK
1525 | 397A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3303 | 3303 | 3303 | OK
1526 | 397A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3338 | 3338 | 3338 | OK
1527 | 397A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3360 | 3360 | 3360 | OK
1528 | 397A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3303 | 3303 | 3303 | OK
1529 | 397A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3360 | 3361 | 3360 | OK
1530 | 397A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3391 | 3391 | 3391 | OK
1531 | 397A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3409 | 3409 | 3409 | OK
1532 | 397A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3360 | 3361 | 3360 | OK
1533 | 398A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3293 | 3294 | 3293 | OK
1534 | 398A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3275 | 3276 | 3275 | OK
1535 | 398A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3265 | 3265 | 3265 | OK
1536 | 398A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3293 | 3294 | 3293 | OK
1537 | 398A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3241 | 3241 | 3241 | OK
1538 | 398A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3233 | 3233 | 3233 | OK
1539 | 398A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3228 | 3228 | 3228 | OK
1540 | 398A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3241 | 3241 | 3241 | OK
1541 | 398A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3205 | 3203 | 3203 | OK
1542 | 398A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3199 | 3198 | 3198 | OK
1543 | 398A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3195 | 3195 | 3195 | OK
1544 | 398A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3205 | 3203 | 3203 | OK
1545 | 399A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3452 | 3452 | 3452 | OK
1546 | 399A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3422 | 3423 | 3422 | OK
1547 | 399A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3405 | 3405 | 3405 | OK
1548 | 399A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3452 | 3452 | 3452 | OK
1549 | 399A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3459 | 3458 | 3458 | OK
1550 | 399A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3428 | 3427 | 3427 | OK
1551 | 399A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3409 | 3409 | 3409 | OK
1552 | 399A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3459 | 3458 | 3458 | OK
1553 | 399A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3450 | 3451 | 3450 | OK
1554 | 399A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3422 | 3423 | 3422 | OK
1555 | 399A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3405 | 3405 | 3405 | OK
1556 | 399A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3450 | 3451 | 3450 | OK
1557 | 400 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3021 | 3018 | 3018 | OK
1558 | 400 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3060 | 3058 | 3058 | OK
1559 | 400 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3083 | 3082 | 3082 | OK
1560 | 400 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3021 | 3018 | 3018 | OK
1561 | 400 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3059 | 3059 | 3059 | OK
1562 | 400 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3094 | 3094 | 3094 | OK
1563 | 400 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3116 | 3116 | 3116 | OK
1564 | 400 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3059 | 3059 | 3059 | OK
1565 | 400 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3005 | 3007 | 3005 | OK
1566 | 400 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3046 | 3047 | 3046 | OK
1567 | 400 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3071 | 3072 | 3071 | OK
1568 | 400 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3005 | 3007 | 3005 | OK
1569 | 401 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3225 | 3228 | 3225 | OK
1570 | 401 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3235 | 3237 | 3235 | OK
1571 | 401 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3241 | 3241 | 3241 | OK
1572 | 401 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3225 | 3228 | 3225 | OK
1573 | 401 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3199 | 3199 | 3199 | OK
1574 | 401 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3213 | 3213 | 3213 | OK
1575 | 401 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3221 | 3221 | 3221 | OK
1576 | 401 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3199 | 3199 | 3199 | OK
1577 | 401 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3233 | 3233 | OK
1578 | 401 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3243 | 3241 | 3241 | OK
1579 | 401 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3247 | 3247 | 3247 | OK
1580 | 401 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3235 | 3233 | 3233 | OK
1581 | 402 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3400 | 3404 | 3400 | OK
1582 | 402 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3376 | 3379 | 3376 | OK
1583 | 402 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3362 | 3363 | 3362 | OK
1584 | 402 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3400 | 3404 | 3400 | OK
1585 | 402 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3374 | 3379 | 3374 | OK
1586 | 402 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3354 | 3357 | 3354 | OK
1587 | 402 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3342 | 3343 | 3342 | OK
1588 | 402 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3374 | 3379 | 3374 | OK
1589 | 402 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3404 | 3405 | 3404 | OK
1590 | 402 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 3380 | 3381 | 3380 | OK
1591 | 402 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 3366 | 3366 | 3366 | OK
1592 | 402 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 3404 | 3405 | 3404 | OK
1593 | 403 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2572 | 2558 | 2558 | OK
1594 | 403 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2522 | 2511 | 2511 | OK
1595 | 403 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2489 | 2485 | 2485 | OK
1596 | 403 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2572 | 2558 | 2558 | OK
1597 | 403 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2505 | 2490 | 2490 | OK
1598 | 403 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2465 | 2454 | 2454 | OK
1599 | 403 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2439 | 2434 | 2434 | OK
1600 | 403 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2505 | 2490 | 2490 | OK
1601 | 403 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2431 | 2429 | 2429 | OK
1602 | 403 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2399 | 2398 | 2398 | OK
1603 | 403 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2380 | 2379 | 2379 | OK
1604 | 403 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2431 | 2429 | 2429 | OK
1605 | 404 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 588 | 597 | 588 | OK
1606 | 404 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 651 | 657 | 651 | OK
1607 | 404 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 690 | 693 | 690 | OK
1608 | 404 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 588 | 597 | 588 | OK
1609 | 404 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 673 | 683 | 673 | OK
1610 | 404 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 722 | 729 | 722 | OK
1611 | 404 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 754 | 756 | 754 | OK
1612 | 404 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 673 | 683 | 673 | OK
1613 | 404 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 737 | 738 | 737 | OK
1614 | 404 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 780 | 781 | 780 | OK
1615 | 404 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 806 | 806 | 806 | OK
1616 | 404 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 737 | 738 | 737 | OK
1617 | 404 | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 990 | 990 | 990 | OK
1618 | 404 | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1007 | 1006 | 1006 | OK
1619 | 404 | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1016 | 1016 | 1016 | OK
1620 | 404 | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 990 | 990 | 990 | OK
1621 | 404 | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1021 | 1021 | 1021 | OK
1622 | 404 | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1032 | 1032 | 1032 | OK
1623 | 404 | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1039 | 1039 | 1039 | OK
1624 | 404 | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1021 | 1021 | 1021 | OK
1625 | 404 | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1078 | 1064 | 1064 | OK
1626 | 404 | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1076 | 1067 | 1067 | OK
1627 | 404 | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1073 | 1070 | 1070 | OK
1628 | 404 | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1078 | 1064 | 1064 | OK
1629 | 404A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2083 | 2068 | 2068 | OK
1630 | 404A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2051 | 2041 | 2041 | OK
1631 | 404A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2030 | 2027 | 2027 | OK
1632 | 404A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2083 | 2068 | 2068 | OK
1633 | 404A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2078 | 2063 | 2063 | OK
1634 | 404A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2047 | 2036 | 2036 | OK
1635 | 404A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2026 | 2023 | 2023 | OK
1636 | 404A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2078 | 2063 | 2063 | OK
1637 | 404A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2203 | 2205 | 2203 | OK
1638 | 404A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2157 | 2158 | 2157 | OK
1639 | 404A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2130 | 2131 | 2130 | OK
1640 | 404A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2203 | 2205 | 2203 | OK
1641 | 405 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1825 | 1844 | 1825 | OK
1642 | 405 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1905 | 1917 | 1905 | OK
1643 | 405 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1955 | 1959 | 1955 | OK
1644 | 405 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1825 | 1844 | 1825 | OK
1645 | 405 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2217 | 2246 | 2217 | OK
1646 | 405 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2237 | 2256 | 2237 | OK
1647 | 405 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2252 | 2259 | 2252 | OK
1648 | 405 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2217 | 2246 | 2217 | OK
1649 | 405 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2182 | 2211 | 2182 | OK
1650 | 405 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2207 | 2227 | 2207 | OK
1651 | 405 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2226 | 2233 | 2226 | OK
1652 | 405 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2182 | 2211 | 2182 | OK
1653 | 406 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2589 | 2574 | 2574 | OK
1654 | 406 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2570 | 2560 | 2560 | OK
1655 | 406 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2557 | 2553 | 2553 | OK
1656 | 406 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2589 | 2574 | 2574 | OK
1657 | 406 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2595 | 2579 | 2579 | OK
1658 | 406 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2576 | 2565 | 2565 | OK
1659 | 406 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2562 | 2558 | 2558 | OK
1660 | 406 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2595 | 2579 | 2579 | OK
1661 | 406 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2777 | 2775 | 2775 | OK
1662 | 406 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2731 | 2730 | 2730 | OK
1663 | 406 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2703 | 2702 | 2702 | OK
1664 | 406 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2777 | 2775 | 2775 | OK
1665 | 407 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2672 | 2674 | 2672 | OK
1666 | 407 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2673 | 2675 | 2673 | OK
1667 | 407 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2674 | 2674 | 2674 | OK
1668 | 407 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2672 | 2674 | 2672 | OK
1669 | 407 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2670 | 2681 | 2670 | OK
1670 | 407 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2672 | 2680 | 2672 | OK
1671 | 407 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2674 | 2677 | 2674 | OK
1672 | 407 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2670 | 2681 | 2670 | OK
1673 | 407 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2672 | 2667 | 2667 | OK
1674 | 407 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2672 | 2668 | 2668 | OK
1675 | 407 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2670 | 2669 | 2669 | OK
1676 | 407 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2672 | 2667 | 2667 | OK
1677 | 408 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2729 | 2748 | 2729 | OK
1678 | 408 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2716 | 2730 | 2716 | OK
1679 | 408 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2711 | 2716 | 2711 | OK
1680 | 408 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2729 | 2748 | 2729 | OK
1681 | 408 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2746 | 2740 | 2740 | OK
1682 | 408 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2730 | 2725 | 2725 | OK
1683 | 408 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2720 | 2718 | 2718 | OK
1684 | 408 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2746 | 2740 | 2740 | OK
1685 | 408 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2733 | 2750 | 2733 | OK
1686 | 408 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2719 | 2731 | 2719 | OK
1687 | 408 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2713 | 2718 | 2713 | OK
1688 | 408 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2733 | 2750 | 2733 | OK
1689 | 409 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2332 | 2332 | 2332 | OK
1690 | 409 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2360 | 2358 | 2358 | OK
1691 | 409 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2375 | 2374 | 2374 | OK
1692 | 409 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2332 | 2332 | 2332 | OK
1693 | 409 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2324 | 2327 | 2324 | OK
1694 | 409 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2353 | 2353 | 2353 | OK
1695 | 409 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2369 | 2369 | 2369 | OK
1696 | 409 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2324 | 2327 | 2324 | OK
1697 | 409 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2307 | 2328 | 2307 | OK
1698 | 409 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2338 | 2352 | 2338 | OK
1699 | 409 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2358 | 2363 | 2358 | OK
1700 | 409 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2307 | 2328 | 2307 | OK
1701 | 410 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2588 | 2535 | 2535 | OK
1702 | 410 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2577 | 2543 | 2543 | OK
1703 | 410 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2567 | 2555 | 2555 | OK
1704 | 410 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2588 | 2535 | 2535 | OK
1705 | 410 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2560 | 2505 | 2505 | OK
1706 | 410 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2553 | 2517 | 2517 | OK
1707 | 410 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2544 | 2531 | 2531 | OK
1708 | 410 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2560 | 2505 | 2505 | OK
1709 | 410 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2598 | 2553 | 2553 | OK
1710 | 410 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2586 | 2555 | 2555 | OK
1711 | 410 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2574 | 2564 | 2564 | OK
1712 | 410 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2598 | 2553 | 2553 | OK
1713 | 411 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2315 | 2345 | 2315 | OK
1714 | 411 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2353 | 2374 | 2353 | OK
1715 | 411 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2379 | 2386 | 2379 | OK
1716 | 411 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2315 | 2345 | 2315 | OK
1717 | 411 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2257 | 2268 | 2257 | OK
1718 | 411 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2304 | 2311 | 2304 | OK
1719 | 411 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2331 | 2334 | 2331 | OK
1720 | 411 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2257 | 2268 | 2257 | OK
1721 | 411 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2350 | 2378 | 2350 | OK
1722 | 411 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2384 | 2403 | 2384 | OK
1723 | 411 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2406 | 2413 | 2406 | OK
1724 | 411 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2350 | 2378 | 2350 | OK
1725 | 411 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 504 | 504 | 504 | OK
1726 | 411 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 533 | 534 | 533 | OK
1727 | 411 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 543 | 543 | 543 | OK
1728 | 411 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 504 | 504 | 504 | OK
1729 | 412A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2369 | 2373 | 2369 | OK
1730 | 412A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2380 | 2382 | 2380 | OK
1731 | 412A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2386 | 2387 | 2386 | OK
1732 | 412A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2369 | 2373 | 2369 | OK
1733 | 412A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2268 | 2275 | 2268 | OK
1734 | 412A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2294 | 2299 | 2294 | OK
1735 | 412A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2310 | 2312 | 2310 | OK
1736 | 412A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2268 | 2275 | 2268 | OK
1737 | 412A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2376 | 2367 | 2367 | OK
1738 | 412A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2385 | 2378 | 2378 | OK
1739 | 412A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2388 | 2386 | 2386 | OK
1740 | 412A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2376 | 2367 | 2367 | OK
1741 | 412A | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 934 | 933 | 933 | OK
1742 | 412A | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 961 | 961 | 961 | OK
1743 | 412A | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 978 | 978 | 978 | OK
1744 | 412A | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 934 | 933 | 933 | OK
1745 | 415 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1962 | 1963 | 1962 | OK
1746 | 415 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1956 | 1957 | 1956 | OK
1747 | 415 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1953 | 1953 | 1953 | OK
1748 | 415 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1962 | 1963 | 1962 | OK
1749 | 415 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1894 | 1899 | 1894 | OK
1750 | 415 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1900 | 1904 | 1900 | OK
1751 | 415 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1904 | 1905 | 1904 | OK
1752 | 415 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1894 | 1899 | 1894 | OK
1753 | 415 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1969 | 1963 | 1963 | OK
1754 | 415 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1963 | 1958 | 1958 | OK
1755 | 415 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1957 | 1956 | 1956 | OK
1756 | 415 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1969 | 1963 | 1963 | OK
1757 | 415 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 815 | 814 | 814 | OK
1758 | 415 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 828 | 828 | 828 | OK
1759 | 415 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 836 | 836 | 836 | OK
1760 | 415 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 815 | 814 | 814 | OK
1761 | 415A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 998 | 995 | 995 | OK
1762 | 415A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1017 | 1015 | 1015 | OK
1763 | 415A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1028 | 1028 | 1028 | OK
1764 | 415A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 998 | 995 | 995 | OK
1765 | 415A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 897 | 889 | 889 | OK
1766 | 415A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 927 | 921 | 921 | OK
1767 | 415A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 943 | 941 | 941 | OK
1768 | 415A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 897 | 889 | 889 | OK
1769 | 415A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 995 | 1006 | 995 | OK
1770 | 415A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1015 | 1023 | 1015 | OK
1771 | 415A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1029 | 1032 | 1029 | OK
1772 | 415A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 995 | 1006 | 995 | OK
1773 | 415A | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 305 | 302 | 302 | OK
1774 | 415A | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 336 | 334 | 334 | OK
1775 | 415A | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 354 | 354 | 354 | OK
1776 | 415A | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 305 | 302 | 302 | OK
1777 | 415B | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1229 | 1231 | 1229 | OK
1778 | 415B | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1232 | 1233 | 1232 | OK
1779 | 415B | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1233 | 1234 | 1233 | OK
1780 | 415B | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1229 | 1231 | 1229 | OK
1781 | 415B | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1371 | 1377 | 1371 | OK
1782 | 415B | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1358 | 1362 | 1358 | OK
1783 | 415B | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1351 | 1353 | 1351 | OK
1784 | 415B | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1371 | 1377 | 1371 | OK
1785 | 415B | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1222 | 1213 | 1213 | OK
1786 | 415B | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1225 | 1218 | 1218 | OK
1787 | 415B | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1225 | 1222 | 1222 | OK
1788 | 415B | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1222 | 1213 | 1213 | OK
1789 | 415B | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 741 | 744 | 741 | OK
1790 | 415B | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 711 | 713 | 711 | OK
1791 | 415B | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 694 | 694 | 694 | OK
1792 | 415B | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 741 | 744 | 741 | OK
1793 | 416 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2250 | 2254 | 2250 | OK
1794 | 416 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2246 | 2249 | 2246 | OK
1795 | 416 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2244 | 2245 | 2244 | OK
1796 | 416 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2250 | 2254 | 2250 | OK
1797 | 416 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2225 | 2227 | 2225 | OK
1798 | 416 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2224 | 2226 | 2224 | OK
1799 | 416 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2223 | 2224 | 2223 | OK
1800 | 416 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2225 | 2227 | 2225 | OK
1801 | 416 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2253 | 2257 | 2253 | OK
1802 | 416 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2249 | 2252 | 2249 | OK
1803 | 416 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2247 | 2248 | 2247 | OK
1804 | 416 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2253 | 2257 | 2253 | OK
1805 | 416 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1005 | 1004 | 1004 | OK
1806 | 416 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1008 | 1007 | 1007 | OK
1807 | 416 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1010 | 1009 | 1009 | OK
1808 | 416 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1005 | 1004 | 1004 | OK
1809 | 417 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2376 | 2376 | 2376 | OK
1810 | 417 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2369 | 2369 | 2369 | OK
1811 | 417 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2365 | 2365 | 2365 | OK
1812 | 417 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2376 | 2376 | 2376 | OK
1813 | 417 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2363 | 2355 | 2355 | OK
1814 | 417 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2357 | 2351 | 2351 | OK
1815 | 417 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2352 | 2350 | 2350 | OK
1816 | 417 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2363 | 2355 | 2355 | OK
1817 | 417 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2377 | 2373 | 2373 | OK
1818 | 417 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2371 | 2367 | 2367 | OK
1819 | 417 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2366 | 2365 | 2365 | OK
1820 | 417 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2377 | 2373 | 2373 | OK
1821 | 417 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1083 | 1083 | 1083 | OK
1822 | 417 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1081 | 1081 | 1081 | OK
1823 | 417 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1080 | 1080 | 1080 | OK
1824 | 417 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1083 | 1083 | 1083 | OK
1825 | 417A | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2139 | 2121 | 2121 | OK
1826 | 417A | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2142 | 2129 | 2129 | OK
1827 | 417A | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2142 | 2137 | 2137 | OK
1828 | 417A | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2139 | 2121 | 2121 | OK
1829 | 417A | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2316 | 2328 | 2316 | OK
1830 | 417A | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2295 | 2304 | 2295 | OK
1831 | 417A | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2285 | 2288 | 2285 | OK
1832 | 417A | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2316 | 2328 | 2316 | OK
1833 | 417A | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1971 | 1975 | 1971 | OK
1834 | 417A | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2002 | 2005 | 2002 | OK
1835 | 417A | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2022 | 2023 | 2022 | OK
1836 | 417A | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1971 | 1975 | 1971 | OK
1837 | 417A | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 964 | 964 | 964 | OK
1838 | 417A | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 966 | 966 | 966 | OK
1839 | 417A | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 967 | 967 | 967 | OK
1840 | 417A | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 964 | 964 | 964 | OK
1841 | 418 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1797 | 1787 | 1787 | OK
1842 | 418 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1826 | 1819 | 1819 | OK
1843 | 418 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1842 | 1839 | 1839 | OK
1844 | 418 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1797 | 1787 | 1787 | OK
1845 | 418 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2061 | 2086 | 2061 | OK
1846 | 418 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2052 | 2070 | 2052 | OK
1847 | 418 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2050 | 2057 | 2050 | OK
1848 | 418 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2061 | 2086 | 2061 | OK
1849 | 418 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2173 | 2173 | 2173 | OK
1850 | 418 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 2146 | 2146 | 2146 | OK
1851 | 418 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 2130 | 2130 | 2130 | OK
1852 | 418 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 2173 | 2173 | 2173 | OK
1853 | 418 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 922 | 922 | 922 | OK
1854 | 418 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 926 | 926 | 926 | OK
1855 | 418 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 928 | 928 | 928 | OK
1856 | 418 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 922 | 922 | 922 | OK
1857 | 419 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1022 | 1026 | 1022 | OK
1858 | 419 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1037 | 1039 | 1037 | OK
1859 | 419 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1046 | 1047 | 1046 | OK
1860 | 419 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1022 | 1026 | 1022 | OK
1861 | 419 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 925 | 916 | 916 | OK
1862 | 419 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 954 | 947 | 947 | OK
1863 | 419 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 969 | 967 | 967 | OK
1864 | 419 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 925 | 916 | 916 | OK
1865 | 419 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 988 | 987 | 987 | OK
1866 | 419 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1005 | 1005 | 1005 | OK
1867 | 419 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1015 | 1015 | 1015 | OK
1868 | 419 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 988 | 987 | 987 | OK
1869 | 419 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 446 | 446 | 446 | OK
1870 | 419 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 450 | 450 | 450 | OK
1871 | 419 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 453 | 453 | 453 | OK
1872 | 419 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 446 | 446 | 446 | OK
1873 | 419 | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1058 | 1058 | 1058 | OK
1874 | 419 | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 980 | 980 | 980 | OK
1875 | 419 | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 933 | 933 | 933 | OK
1876 | 419 | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1058 | 1058 | 1058 | OK
1877 | 419 | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 852 | 852 | 852 | OK
1878 | 419 | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 807 | 807 | 807 | OK
1879 | 419 | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 780 | 780 | 780 | OK
1880 | 419 | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 852 | 852 | 852 | OK
1881 | 419 | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1190 | 1190 | 1190 | OK
1882 | 419 | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1088 | 1088 | 1088 | OK
1883 | 419 | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1027 | 1027 | 1027 | OK
1884 | 419 | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1190 | 1190 | 1190 | OK
1885 | 419 | 14 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 577 | 577 | 577 | OK
1886 | 419 | 14 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 535 | 535 | 535 | OK
1887 | 419 | 14 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 509 | 509 | 509 | OK
1888 | 419 | 14 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 577 | 577 | 577 | OK
1889 | 420 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 46 | 46 | 46 | OK
1890 | 420 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 124 | 124 | 124 | OK
1891 | 420 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 171 | 171 | 171 | OK
1892 | 420 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 46 | 46 | 46 | OK
1893 | 420 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 250 | 250 | 250 | OK
1894 | 420 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 295 | 295 | 295 | OK
1895 | 420 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 322 | 322 | 322 | OK
1896 | 420 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 250 | 250 | 250 | OK
1897 | 420 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -84 | -84 | -84 | NG
1898 | 420 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 18 | 18 | 18 | OK
1899 | 420 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 79 | 79 | 79 | OK
1900 | 420 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -84 | -84 | -84 | NG
1901 | 420 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -53 | -53 | -53 | NG
1902 | 420 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -11 | -11 | -11 | NG
1903 | 420 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 15 | 15 | 15 | OK
1904 | 420 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -53 | -53 | -53 | NG
1905 | 420 | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 69 | 64 | 64 | OK
1906 | 420 | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 133 | 128 | 128 | OK
1907 | 420 | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 169 | 167 | 167 | OK
1908 | 420 | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 69 | 64 | 64 | OK
1909 | 420 | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 125 | 121 | 121 | OK
1910 | 420 | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 182 | 178 | 178 | OK
1911 | 420 | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 214 | 212 | 212 | OK
1912 | 420 | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 125 | 121 | 121 | OK
1913 | 420 | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 191 | 193 | 191 | OK
1914 | 420 | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 237 | 236 | 236 | OK
1915 | 420 | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 263 | 262 | 262 | OK
1916 | 420 | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 191 | 193 | 191 | OK
1917 | 420 | 14 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -30 | -30 | -30 | NG
1918 | 420 | 14 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 12 | 12 | 12 | OK
1919 | 420 | 14 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 37 | 37 | 37 | OK
1920 | 420 | 14 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -30 | -30 | -30 | NG
1921 | 421 | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1773 | 1808 | 1773 | OK
1922 | 421 | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1635 | 1661 | 1635 | OK
1923 | 421 | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1560 | 1570 | 1560 | OK
1924 | 421 | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1773 | 1808 | 1773 | OK
1925 | 421 | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1459 | 1472 | 1459 | OK
1926 | 421 | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1363 | 1374 | 1363 | OK
1927 | 421 | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1309 | 1314 | 1309 | OK
1928 | 421 | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1459 | 1472 | 1459 | OK
1929 | 421 | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1581 | 1606 | 1581 | OK
1930 | 421 | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 1466 | 1485 | 1466 | OK
1931 | 421 | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 1403 | 1411 | 1403 | OK
1932 | 421 | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 1581 | 1606 | 1581 | OK
1933 | 421 | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 834 | 834 | 834 | OK
1934 | 421 | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 761 | 761 | 761 | OK
1935 | 421 | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 717 | 717 | 717 | OK
1936 | 421 | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 834 | 834 | 834 | OK
1937 | 421C | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -235 | -266 | -266 | NG
1938 | 421C | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -162 | -183 | -183 | NG
1939 | 421C | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | -123 | -130 | -130 | NG
1940 | 421C | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -235 | -266 | -266 | NG
1941 | 421C | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -132 | -154 | -154 | NG
1942 | 421C | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -75 | -89 | -89 | NG
1943 | 421C | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | -44 | -49 | -49 | NG
1944 | 421C | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -132 | -154 | -154 | NG
1945 | 421C | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -77 | -92 | -92 | NG
1946 | 421C | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -27 | -37 | -37 | NG
1947 | 421C | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 0 | -4 | -4 | NG
1948 | 421C | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -77 | -92 | -92 | NG
1949 | 421C | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -53 | -53 | -53 | NG
1950 | 421C | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -22 | -22 | -22 | NG
1951 | 421C | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | -4 | -4 | -4 | NG
1952 | 421C | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -53 | -53 | -53 | NG
1953 | 421C | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 523 | 522 | 522 | OK
1954 | 421C | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 538 | 538 | 538 | OK
1955 | 421C | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 548 | 548 | 548 | OK
1956 | 421C | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 523 | 522 | 522 | OK
1957 | 421C | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 414 | 414 | 414 | OK
1958 | 421C | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 444 | 444 | 444 | OK
1959 | 421C | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 461 | 461 | 461 | OK
1960 | 421C | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 414 | 414 | 414 | OK
1961 | 421C | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 815 | 815 | 815 | OK
1962 | 421C | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 791 | 791 | 791 | OK
1963 | 421C | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 777 | 777 | 777 | OK
1964 | 421C | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 815 | 815 | 815 | OK
1965 | 421C | 14 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 157 | 157 | 157 | OK
1966 | 421C | 14 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 175 | 175 | 175 | OK
1967 | 421C | 14 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 186 | 186 | 186 | OK
1968 | 421C | 14 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 157 | 157 | 157 | OK
1969 | 421B | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 454 | 455 | 454 | OK
1970 | 421B | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 478 | 478 | 478 | OK
1971 | 421B | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 492 | 492 | 492 | OK
1972 | 421B | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 454 | 455 | 454 | OK
1973 | 421B | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 747 | 747 | 747 | OK
1974 | 421B | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 731 | 731 | 731 | OK
1975 | 421B | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 722 | 722 | 722 | OK
1976 | 421B | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 747 | 747 | 747 | OK
1977 | 421B | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 855 | 855 | 855 | OK
1978 | 421B | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 826 | 826 | 826 | OK
1979 | 421B | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 808 | 808 | 808 | OK
1980 | 421B | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 855 | 855 | 855 | OK
1981 | 421B | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 458 | 458 | 458 | OK
1982 | 421B | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 440 | 440 | 440 | OK
1983 | 421B | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 429 | 429 | 429 | OK
1984 | 421B | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 458 | 458 | 458 | OK
1985 | 421B | 11 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -208 | -204 | -208 | NG
1986 | 421B | 11 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | -177 | -174 | -177 | NG
1987 | 421B | 11 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | -159 | -159 | -159 | NG
1988 | 421B | 11 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -208 | -204 | -208 | NG
1989 | 421B | 12 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 133 | 136 | 133 | OK
1990 | 421B | 12 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 139 | 141 | 139 | OK
1991 | 421B | 12 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 142 | 143 | 142 | OK
1992 | 421B | 12 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 133 | 136 | 133 | OK
1993 | 421B | 13 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 363 | 362 | 362 | OK
1994 | 421B | 13 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 350 | 350 | 350 | OK
1995 | 421B | 13 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 344 | 343 | 343 | OK
1996 | 421B | 13 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 363 | 362 | 362 | OK
1997 | 421B | 14 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 203 | 203 | 203 | OK
1998 | 421B | 14 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 187 | 187 | 187 | OK
1999 | 421B | 14 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 178 | 178 | 178 | OK
2000 | 421B | 14 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 203 | 203 | 203 | OK
2001 | 421B | 15 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 237 | 237 | 237 | OK
2002 | 421B | 15 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 216 | 216 | 216 | OK
2003 | 421B | 15 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 204 | 204 | 204 | OK
2004 | 421B | 15 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 237 | 237 | 237 | OK
2005 | BNG | 1 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 272 | 269 | 269 | OK
2006 | BNG | 1 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 266 | 265 | 265 | OK
2007 | BNG | 1 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 263 | 262 | 262 | OK
2008 | BNG | 1 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 272 | 269 | 269 | OK
2009 | BNG | 2 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 43 | 43 | 43 | OK
2010 | BNG | 2 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 55 | 56 | 55 | OK
2011 | BNG | 2 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 62 | 62 | 62 | OK
2012 | BNG | 2 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 43 | 43 | 43 | OK
2013 | BNG | 3 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 615 | 611 | 611 | OK
2014 | BNG | 3 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 583 | 581 | 581 | OK
2015 | BNG | 3 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 566 | 566 | 566 | OK
2016 | BNG | 3 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 615 | 611 | 611 | OK
2017 | BNG | 4 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 20 | 20 | 20 | OK
2018 | BNG | 4 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 36 | 36 | 36 | OK
2019 | BNG | 4 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 45 | 45 | 45 | OK
2020 | BNG | 4 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | 20 | 20 | 20 | OK
2021 | BNG | 5 | 1 | 1 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -14 | -14 | -14 | NG
2022 | BNG | 5 | 1 | 2 | Medium insulator swing (T50°C & 300Pa) | Creep FE | 0 | 7 | 7 | 7 | OK
2023 | BNG | 5 | 1 | 3 | Minimum insulator swing (T50°C & 100Pa) | Creep FE | 0 | 19 | 19 | 19 | OK
2024 | BNG | 5 | 1 | 4 | Maximum insulator swing (T50°C & 500Pa) | Creep FE | 0 | -14 | -14 | -14 | NG

## Tab_4
rowtext | str_no | structure_name | load_case | maximum_usage | element_label | element_type
1 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 60.50 | 1 | Concrete Pole
2 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 11.86 | 2 | Suspension
3 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 63.73 | 1 | Concrete Pole
4 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 11.70 | 3 | Suspension
5 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 60.50 | 1 | Concrete Pole
6 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 11.86 | 2 | Suspension
7 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 63.73 | 1 | Concrete Pole
8 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 11.70 | 3 | Suspension
9 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 62.37 | 1 | Concrete Pole
10 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 9.82 | 2 | Suspension
11 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 62.10 | 1 | Concrete Pole
12 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 9.73 | 3 | Suspension
13 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 62.37 | 1 | Concrete Pole
14 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 9.82 | 2 | Suspension
15 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 62.10 | 1 | Concrete Pole
16 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 9.73 | 3 | Suspension
17 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 60.36 | 1 | Concrete Pole
18 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 11.80 | 2 | Suspension
19 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 63.48 | 1 | Concrete Pole
20 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 11.64 | 3 | Suspension
21 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 60.36 | 1 | Concrete Pole
22 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 11.80 | 2 | Suspension
23 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 63.48 | 1 | Concrete Pole
24 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 11.64 | 3 | Suspension
25 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 64.79 | 1 | Concrete Pole
26 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 11.29 | 2 | Suspension
27 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 60.78 | 1 | Concrete Pole
28 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 11.13 | 3 | Suspension
29 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 64.79 | 1 | Concrete Pole
30 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 11.29 | 2 | Suspension
31 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 60.78 | 1 | Concrete Pole
32 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 11.13 | 3 | Suspension
33 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 53.92 | 1 | Concrete Pole
34 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 10.64 | 2 | Suspension
35 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 57.01 | 1 | Concrete Pole
36 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 10.31 | 2 | Suspension
37 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 53.92 | 1 | Concrete Pole
38 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 10.64 | 2 | Suspension
39 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 57.01 | 1 | Concrete Pole
40 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 10.31 | 2 | Suspension
41 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 55.25 | 1 | Concrete Pole
42 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.33 | 2 | Suspension
43 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 54.71 | 1 | Concrete Pole
44 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 7.95 | 3 | Suspension
45 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 55.25 | 1 | Concrete Pole
46 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.33 | 2 | Suspension
47 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 54.71 | 1 | Concrete Pole
48 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 7.95 | 3 | Suspension
49 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 53.78 | 1 | Concrete Pole
50 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 10.57 | 2 | Suspension
51 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 56.74 | 1 | Concrete Pole
52 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 10.25 | 2 | Suspension
53 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 53.78 | 1 | Concrete Pole
54 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 10.57 | 2 | Suspension
55 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 56.75 | 1 | Concrete Pole
56 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 10.25 | 2 | Suspension
57 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 56.94 | 1 | Concrete Pole
58 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 10.00 | 2 | Suspension
59 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 53.17 | 1 | Concrete Pole
60 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 9.65 | 2 | Suspension
61 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 56.93 | 1 | Concrete Pole
62 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 10.00 | 2 | Suspension
63 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 53.17 | 1 | Concrete Pole
64 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 9.65 | 2 | Suspension
65 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 54.04 | 1 | Concrete Pole
66 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 9.62 | 2 | Suspension
67 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 56.01 | 1 | Concrete Pole
68 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.26 | 2 | Suspension
69 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 54.04 | 1 | Concrete Pole
70 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 9.62 | 2 | Suspension
71 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 56.01 | 1 | Concrete Pole
72 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.26 | 2 | Suspension
73 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 37.62 | X-arm_M | X-Arm
74 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 6.52 | 2 | Suspension
75 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 37.62 | X-arm_M | X-Arm
76 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 6.52 | 2 | Suspension
77 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 48.11 | X-arm_B | X-Arm
78 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.96 | 1 | Suspension
79 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 45.89 | 1 | Concrete Pole
80 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.94 | 1 | Suspension
81 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 54.39 | X-arm_M | X-Arm
82 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 10.18 | 2 | Suspension
83 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 58.08 | X-arm_M | X-Arm
84 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 10.13 | 2 | Suspension
85 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 42.07 | X-arm_M | X-Arm
86 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.97 | 3 | Suspension
87 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 44.88 | X-arm_M | X-Arm
88 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 10.00 | 3 | Suspension
89 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 48.88 | 1 | Concrete Pole
90 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 9.56 | 2 | Suspension
91 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 51.37 | 1 | Concrete Pole
92 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.28 | 2 | Suspension
93 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 61.67 | 1 | Concrete Pole
94 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 11.70 | 2 | Suspension
95 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 65.60 | 1 | Concrete Pole
96 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 11.62 | 3 | Suspension
97 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 61.67 | 1 | Concrete Pole
98 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 11.70 | 2 | Suspension
99 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 65.60 | 1 | Concrete Pole
100 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 11.62 | 3 | Suspension
101 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 62.34 | 1 | Concrete Pole
102 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 9.64 | 2 | Suspension
103 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 62.62 | 1 | Concrete Pole
104 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 9.67 | 3 | Suspension
105 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 62.34 | 1 | Concrete Pole
106 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 9.64 | 2 | Suspension
107 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 62.62 | 1 | Concrete Pole
108 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 9.67 | 3 | Suspension
109 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 61.47 | 1 | Concrete Pole
110 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 11.64 | 2 | Suspension
111 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 65.28 | 1 | Concrete Pole
112 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 11.56 | 3 | Suspension
113 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 61.47 | 1 | Concrete Pole
114 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 11.64 | 2 | Suspension
115 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 65.28 | 1 | Concrete Pole
116 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 11.56 | 3 | Suspension
117 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 63.29 | 1 | Concrete Pole
118 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 11.12 | 2 | Suspension
119 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 60.03 | 1 | Concrete Pole
120 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 11.06 | 3 | Suspension
121 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 63.29 | 1 | Concrete Pole
122 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 11.12 | 2 | Suspension
123 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 60.03 | 1 | Concrete Pole
124 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 11.06 | 3 | Suspension
125 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 53.22 | 1 | Concrete Pole
126 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 10.51 | 2 | Suspension
127 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 57.15 | 1 | Concrete Pole
128 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 10.27 | 2 | Suspension
129 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 53.22 | 1 | Concrete Pole
130 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 10.51 | 2 | Suspension
131 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 57.15 | 1 | Concrete Pole
132 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 10.27 | 2 | Suspension
133 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 54.54 | 1 | Concrete Pole
134 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.19 | 2 | Suspension
135 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 54.83 | 1 | Concrete Pole
136 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 7.92 | 3 | Suspension
137 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 54.54 | 1 | Concrete Pole
138 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.19 | 2 | Suspension
139 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 54.83 | 1 | Concrete Pole
140 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 7.92 | 3 | Suspension
141 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 53.07 | 1 | Concrete Pole
142 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 10.45 | 2 | Suspension
143 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 56.88 | 1 | Concrete Pole
144 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 10.20 | 2 | Suspension
145 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 53.07 | 1 | Concrete Pole
146 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 10.45 | 2 | Suspension
147 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 56.88 | 1 | Concrete Pole
148 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 10.20 | 2 | Suspension
149 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 56.12 | 1 | Concrete Pole
150 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 9.87 | 2 | Suspension
151 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 52.77 | 1 | Concrete Pole
152 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 9.61 | 2 | Suspension
153 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 56.12 | 1 | Concrete Pole
154 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 9.87 | 2 | Suspension
155 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 52.77 | 1 | Concrete Pole
156 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 9.61 | 2 | Suspension
157 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 53.33 | 1 | Concrete Pole
158 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 9.49 | 2 | Suspension
159 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 56.14 | 1 | Concrete Pole
160 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.22 | 2 | Suspension
161 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 53.33 | 1 | Concrete Pole
162 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 9.49 | 2 | Suspension
163 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 56.14 | 1 | Concrete Pole
164 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.22 | 2 | Suspension
165 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 37.39 | X-arm_M | X-Arm
166 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 6.47 | 2 | Suspension
167 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 37.39 | X-arm_M | X-Arm
168 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 6.47 | 2 | Suspension
169 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 47.83 | X-arm_B | X-Arm
170 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.88 | 1 | Suspension
171 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 45.56 | 1 | Concrete Pole
172 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.88 | 1 | Suspension
173 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 54.03 | X-arm_M | X-Arm
174 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 10.09 | 2 | Suspension
175 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 57.69 | X-arm_M | X-Arm
176 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 10.06 | 2 | Suspension
177 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 41.77 | X-arm_M | X-Arm
178 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.86 | 3 | Suspension
179 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 44.56 | X-arm_M | X-Arm
180 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.91 | 3 | Suspension
181 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 47.57 | 1 | Concrete Pole
182 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 9.44 | 2 | Suspension
183 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 50.81 | 1 | Concrete Pole
184 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.23 | 2 | Suspension
185 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 54.96 | 1 | Concrete Pole
186 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 10.10 | 2 | Suspension
187 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 57.86 | 1 | Concrete Pole
188 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 9.57 | 3 | Suspension
189 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 55.05 | 1 | Concrete Pole
190 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 10.10 | 2 | Suspension
191 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 57.88 | 1 | Concrete Pole
192 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 9.57 | 3 | Suspension
193 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 56.88 | 1 | Concrete Pole
194 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 7.99 | 2 | Suspension
195 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 56.05 | 1 | Concrete Pole
196 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 7.82 | 3 | Suspension
197 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 56.97 | 1 | Concrete Pole
198 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 7.99 | 2 | Suspension
199 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 56.07 | 1 | Concrete Pole
200 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 7.82 | 3 | Suspension
201 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 54.80 | 1 | Concrete Pole
202 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 10.04 | 2 | Suspension
203 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 57.56 | 1 | Concrete Pole
204 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 9.51 | 3 | Suspension
205 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 54.89 | 1 | Concrete Pole
206 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 10.03 | 2 | Suspension
207 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 57.57 | 1 | Concrete Pole
208 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 9.51 | 3 | Suspension
209 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 58.93 | 1 | Concrete Pole
210 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 9.47 | 2 | Suspension
211 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 54.51 | 1 | Concrete Pole
212 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 8.98 | 3 | Suspension
213 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 59.01 | 1 | Concrete Pole
214 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 9.47 | 2 | Suspension
215 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 54.52 | 1 | Concrete Pole
216 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 8.98 | 3 | Suspension
217 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 46.11 | 1 | Concrete Pole
218 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 9.28 | 2 | Suspension
219 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 49.02 | 1 | Concrete Pole
220 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 8.55 | 3 | Suspension
221 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 46.19 | 1 | Concrete Pole
222 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 9.28 | 2 | Suspension
223 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 49.03 | 1 | Concrete Pole
224 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 8.55 | 3 | Suspension
225 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 48.32 | 1 | Concrete Pole
226 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 6.96 | 2 | Suspension
227 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 47.53 | 1 | Concrete Pole
228 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 6.57 | 3 | Suspension
229 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 48.40 | 1 | Concrete Pole
230 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 6.96 | 2 | Suspension
231 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 47.55 | 1 | Concrete Pole
232 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 6.57 | 3 | Suspension
233 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 46.09 | 1 | Concrete Pole
234 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 9.21 | 2 | Suspension
235 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 48.85 | 1 | Concrete Pole
236 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 8.48 | 3 | Suspension
237 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 46.17 | 1 | Concrete Pole
238 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 9.21 | 2 | Suspension
239 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 48.87 | 1 | Concrete Pole
240 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 8.48 | 3 | Suspension
241 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 50.51 | 1 | Concrete Pole
242 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 8.60 | 2 | Suspension
243 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 46.16 | 1 | Concrete Pole
244 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 7.89 | 3 | Suspension
245 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 50.58 | 1 | Concrete Pole
246 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 8.60 | 2 | Suspension
247 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 46.18 | 1 | Concrete Pole
248 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 7.89 | 3 | Suspension
249 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 46.73 | 1 | Concrete Pole
250 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 8.27 | 2 | Suspension
251 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 48.48 | 1 | Concrete Pole
252 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 7.68 | 3 | Suspension
253 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 46.81 | 1 | Concrete Pole
254 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 8.27 | 2 | Suspension
255 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 48.50 | 1 | Concrete Pole
256 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 7.68 | 3 | Suspension
257 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 32.83 | X-arm_M | X-Arm
258 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 5.66 | 2 | Suspension
259 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 32.83 | X-arm_M | X-Arm
260 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 5.66 | 2 | Suspension
261 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 42.40 | X-arm_B | X-Arm
262 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 8.68 | 1 | Suspension
263 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 40.54 | 1 | Concrete Pole
264 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 8.58 | 1 | Suspension
265 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 47.18 | X-arm_M | X-Arm
266 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 8.82 | 2 | Suspension
267 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 49.89 | X-arm_M | X-Arm
268 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 8.70 | 2 | Suspension
269 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 36.74 | X-arm_M | X-Arm
270 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 8.03 | 3 | Suspension
271 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 38.82 | X-arm_M | X-Arm
272 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 8.11 | 3 | Suspension
273 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 41.21 | 1 | Concrete Pole
274 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 8.28 | 2 | Suspension
275 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 42.36 | 1 | Concrete Pole
276 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 7.67 | 3 | Suspension
277 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 52.43 | 1 | Concrete Pole
278 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 10.24 | 2 | Suspension
279 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 68.91 | 1 | Concrete Pole
280 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 11.67 | 3 | Suspension
281 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 52.77 | 1 | Concrete Pole
282 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 10.24 | 2 | Suspension
283 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 68.97 | 1 | Concrete Pole
284 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 11.67 | 3 | Suspension
285 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 54.54 | 1 | Concrete Pole
286 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 8.22 | 2 | Suspension
287 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 67.24 | 1 | Concrete Pole
288 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 10.19 | 3 | Suspension
289 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 54.85 | 1 | Concrete Pole
290 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 8.22 | 2 | Suspension
291 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 67.30 | 1 | Concrete Pole
292 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 10.19 | 3 | Suspension
293 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 52.40 | 1 | Concrete Pole
294 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 10.18 | 2 | Suspension
295 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 68.63 | 1 | Concrete Pole
296 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 11.62 | 3 | Suspension
297 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 52.73 | 1 | Concrete Pole
298 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 10.18 | 2 | Suspension
299 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 68.69 | 1 | Concrete Pole
300 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 11.62 | 3 | Suspension
301 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 56.63 | 1 | Concrete Pole
302 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 9.63 | 2 | Suspension
303 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 65.81 | 1 | Concrete Pole
304 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 11.18 | 3 | Suspension
305 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 56.93 | 1 | Concrete Pole
306 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 9.63 | 2 | Suspension
307 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 65.86 | 1 | Concrete Pole
308 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 11.18 | 3 | Suspension
309 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 46.12 | 1 | Concrete Pole
310 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 9.22 | 2 | Suspension
311 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 60.41 | 1 | Concrete Pole
312 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 10.29 | 3 | Suspension
313 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 45.91 | 1 | Concrete Pole
314 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 9.22 | 2 | Suspension
315 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 60.47 | 1 | Concrete Pole
316 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 10.29 | 3 | Suspension
317 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 47.51 | 1 | Concrete Pole
318 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 6.93 | 2 | Suspension
319 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 58.92 | 1 | Concrete Pole
320 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 8.59 | 3 | Suspension
321 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 47.14 | 1 | Concrete Pole
322 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 6.93 | 2 | Suspension
323 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 58.98 | 1 | Concrete Pole
324 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 8.59 | 3 | Suspension
325 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 46.00 | 1 | Concrete Pole
326 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 9.15 | 2 | Suspension
327 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 60.21 | 1 | Concrete Pole
328 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 10.23 | 3 | Suspension
329 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 45.80 | 1 | Concrete Pole
330 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 9.15 | 2 | Suspension
331 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 60.26 | 1 | Concrete Pole
332 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 10.23 | 3 | Suspension
333 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 49.27 | 1 | Concrete Pole
334 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 8.54 | 2 | Suspension
335 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 57.59 | 1 | Concrete Pole
336 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 9.73 | 3 | Suspension
337 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 49.46 | 1 | Concrete Pole
338 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 8.54 | 2 | Suspension
339 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 57.64 | 1 | Concrete Pole
340 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 9.73 | 3 | Suspension
341 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 46.27 | 1 | Concrete Pole
342 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 8.22 | 2 | Suspension
343 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 59.85 | 1 | Concrete Pole
344 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.53 | 3 | Suspension
345 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 46.09 | 1 | Concrete Pole
346 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 8.22 | 2 | Suspension
347 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 59.90 | 1 | Concrete Pole
348 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.53 | 3 | Suspension
349 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 35.65 | X-arm_M | X-Arm
350 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 6.02 | 2 | Suspension
351 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 35.65 | X-arm_M | X-Arm
352 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 6.02 | 2 | Suspension
353 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 42.80 | X-arm_B | X-Arm
354 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.02 | 1 | Suspension
355 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 43.29 | X-arm_M | X-Arm
356 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.22 | 1 | Suspension
357 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 51.47 | X-arm_M | X-Arm
358 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.27 | 2 | Suspension
359 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 54.93 | X-arm_M | X-Arm
360 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.42 | 2 | Suspension
361 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 39.94 | X-arm_M | X-Arm
362 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 8.76 | 3 | Suspension
363 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 42.61 | X-arm_M | X-Arm
364 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.10 | 3 | Suspension
365 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 42.98 | 1 | Concrete Pole
366 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 8.31 | 2 | Suspension
367 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 53.39 | 1 | Concrete Pole
368 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.25 | 3 | Suspension
369 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 67.23 | 1 | Concrete Pole
370 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 11.59 | 2 | Suspension
371 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 70.57 | 1 | Concrete Pole
372 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 11.44 | 3 | Suspension
373 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 67.24 | 1 | Concrete Pole
374 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 11.59 | 2 | Suspension
375 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 70.56 | 1 | Concrete Pole
376 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 11.44 | 3 | Suspension
377 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 68.83 | 1 | Concrete Pole
378 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 9.81 | 2 | Suspension
379 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 68.75 | 1 | Concrete Pole
380 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 9.76 | 3 | Suspension
381 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 68.83 | 1 | Concrete Pole
382 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 9.81 | 2 | Suspension
383 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 68.75 | 1 | Concrete Pole
384 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 9.75 | 3 | Suspension
385 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 66.99 | 1 | Concrete Pole
386 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 11.53 | 2 | Suspension
387 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 70.20 | 1 | Concrete Pole
388 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 11.38 | 3 | Suspension
389 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 67.00 | 1 | Concrete Pole
390 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 11.53 | 2 | Suspension
391 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 70.20 | 1 | Concrete Pole
392 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 11.38 | 3 | Suspension
393 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 70.62 | 1 | Concrete Pole
394 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 11.05 | 2 | Suspension
395 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 67.27 | 1 | Concrete Pole
396 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 10.91 | 3 | Suspension
397 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 70.62 | 1 | Concrete Pole
398 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 11.05 | 2 | Suspension
399 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 67.26 | 1 | Concrete Pole
400 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 10.91 | 3 | Suspension
401 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 53.60 | 1 | Concrete Pole
402 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 10.35 | 2 | Suspension
403 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 56.97 | 1 | Concrete Pole
404 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 10.06 | 2 | Suspension
405 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 53.60 | 1 | Concrete Pole
406 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 10.35 | 2 | Suspension
407 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 56.97 | 1 | Concrete Pole
408 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 10.06 | 2 | Suspension
409 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 55.67 | 1 | Concrete Pole
410 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.32 | 2 | Suspension
411 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 55.65 | 1 | Concrete Pole
412 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 7.99 | 3 | Suspension
413 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 55.67 | 1 | Concrete Pole
414 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.32 | 2 | Suspension
415 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 55.64 | 1 | Concrete Pole
416 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 7.99 | 3 | Suspension
417 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 53.57 | 1 | Concrete Pole
418 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 10.29 | 2 | Suspension
419 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 56.82 | 1 | Concrete Pole
420 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 9.99 | 2 | Suspension
421 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 53.57 | 1 | Concrete Pole
422 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 10.29 | 2 | Suspension
423 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 56.81 | 1 | Concrete Pole
424 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 9.99 | 2 | Suspension
425 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 57.71 | 1 | Concrete Pole
426 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 9.74 | 2 | Suspension
427 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 54.42 | 1 | Concrete Pole
428 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 9.43 | 2 | Suspension
429 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 57.72 | 1 | Concrete Pole
430 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 9.74 | 2 | Suspension
431 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 54.42 | 1 | Concrete Pole
432 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 9.43 | 2 | Suspension
433 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 54.17 | 1 | Concrete Pole
434 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 9.45 | 2 | Suspension
435 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 56.49 | 1 | Concrete Pole
436 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.13 | 2 | Suspension
437 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 54.17 | 1 | Concrete Pole
438 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 9.45 | 2 | Suspension
439 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 56.49 | 1 | Concrete Pole
440 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.13 | 2 | Suspension
441 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 35.94 | X-arm_M | X-Arm
442 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 6.20 | 2 | Suspension
443 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 35.94 | X-arm_M | X-Arm
444 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 6.20 | 2 | Suspension
445 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 45.36 | X-arm_B | X-Arm
446 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.35 | 1 | Suspension
447 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 43.60 | X-arm_M | X-Arm
448 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.33 | 1 | Suspension
449 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 51.65 | X-arm_M | X-Arm
450 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.65 | 2 | Suspension
451 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 55.34 | X-arm_M | X-Arm
452 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.61 | 2 | Suspension
453 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 40.05 | X-arm_M | X-Arm
454 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.38 | 3 | Suspension
455 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 42.87 | X-arm_M | X-Arm
456 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.42 | 3 | Suspension
457 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 49.61 | 1 | Concrete Pole
458 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 9.35 | 2 | Suspension
459 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 51.58 | 1 | Concrete Pole
460 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.10 | 2 | Suspension
461 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 51.49 | X-arm_B | X-Arm
462 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 12.62 | 2 | Suspension
463 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 59.62 | X-arm_M | X-Arm
464 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 12.48 | 3 | Suspension
465 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 51.49 | X-arm_B | X-Arm
466 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 12.62 | 2 | Suspension
467 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 59.62 | X-arm_M | X-Arm
468 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 12.48 | 3 | Suspension
469 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 44.29 | 1 | Concrete Pole
470 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 10.11 | 2 | Suspension
471 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 44.21 | 1 | Concrete Pole
472 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 10.01 | 3 | Suspension
473 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 44.30 | 1 | Concrete Pole
474 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 10.11 | 2 | Suspension
475 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 44.21 | 1 | Concrete Pole
476 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 10.01 | 3 | Suspension
477 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 50.57 | X-arm_B | X-Arm
478 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 12.56 | 2 | Suspension
479 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 58.46 | X-arm_M | X-Arm
480 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 12.41 | 3 | Suspension
481 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 50.57 | X-arm_B | X-Arm
482 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 12.56 | 2 | Suspension
483 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 58.46 | X-arm_M | X-Arm
484 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 12.41 | 3 | Suspension
485 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 51.51 | X-arm_M | X-Arm
486 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 12.00 | 2 | Suspension
487 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 43.38 | 1 | Concrete Pole
488 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 11.86 | 3 | Suspension
489 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 51.51 | X-arm_M | X-Arm
490 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 12.00 | 2 | Suspension
491 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 43.37 | 1 | Concrete Pole
492 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 11.86 | 3 | Suspension
493 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 47.95 | X-arm_B | X-Arm
494 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 11.44 | 2 | Suspension
495 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 56.03 | X-arm_M | X-Arm
496 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 11.15 | 2 | Suspension
497 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 47.94 | X-arm_B | X-Arm
498 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 11.44 | 2 | Suspension
499 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 56.03 | X-arm_M | X-Arm
500 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 11.15 | 2 | Suspension
501 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 38.02 | 1 | Concrete Pole
502 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.62 | 2 | Suspension
503 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 37.98 | 1 | Concrete Pole
504 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 8.26 | 3 | Suspension
505 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 38.02 | 1 | Concrete Pole
506 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.62 | 2 | Suspension
507 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 37.98 | 1 | Concrete Pole
508 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 8.26 | 3 | Suspension
509 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 47.01 | X-arm_B | X-Arm
510 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 11.36 | 2 | Suspension
511 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 54.84 | X-arm_M | X-Arm
512 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 11.07 | 2 | Suspension
513 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 47.01 | X-arm_B | X-Arm
514 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 11.36 | 2 | Suspension
515 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 54.84 | X-arm_M | X-Arm
516 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 11.07 | 2 | Suspension
517 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 46.83 | X-arm_M | X-Arm
518 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 10.75 | 2 | Suspension
519 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 38.58 | X-arm_B | X-Arm
520 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 10.45 | 2 | Suspension
521 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 46.83 | X-arm_M | X-Arm
522 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 10.75 | 2 | Suspension
523 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 38.58 | X-arm_B | X-Arm
524 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 10.45 | 2 | Suspension
525 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 38.35 | X-arm_B | X-Arm
526 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 10.20 | 2 | Suspension
527 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 44.91 | X-arm_M | X-Arm
528 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.88 | 2 | Suspension
529 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 38.35 | X-arm_B | X-Arm
530 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 10.20 | 2 | Suspension
531 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 44.91 | X-arm_M | X-Arm
532 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.88 | 2 | Suspension
533 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 41.09 | X-arm_M | X-Arm
534 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 7.17 | 1 | Suspension
535 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 41.09 | X-arm_M | X-Arm
536 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 7.17 | 1 | Suspension
537 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 53.74 | X-arm_B | X-Arm
538 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 11.21 | 1 | Suspension
539 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 49.98 | X-arm_M | X-Arm
540 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 11.18 | 1 | Suspension
541 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 59.92 | X-arm_M | X-Arm
542 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 11.20 | 2 | Suspension
543 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 63.71 | X-arm_M | X-Arm
544 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 11.15 | 2 | Suspension
545 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 46.18 | X-arm_M | X-Arm
546 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 11.10 | 3 | Suspension
547 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 49.07 | X-arm_M | X-Arm
548 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 11.12 | 3 | Suspension
549 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 40.98 | X-arm_B | X-Arm
550 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 10.21 | 2 | Suspension
551 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 47.48 | X-arm_M | X-Arm
552 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.95 | 2 | Suspension
553 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 66.03 | 1 | Concrete Pole
554 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 12.41 | 2 | Suspension
555 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 70.52 | 1 | Concrete Pole
556 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 12.23 | 3 | Suspension
557 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 66.02 | 1 | Concrete Pole
558 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 12.41 | 2 | Suspension
559 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 70.53 | 1 | Concrete Pole
560 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 12.23 | 3 | Suspension
561 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 68.08 | 1 | Concrete Pole
562 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 9.60 | 2 | Suspension
563 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 68.26 | 1 | Concrete Pole
564 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 9.66 | 3 | Suspension
565 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 68.07 | 1 | Concrete Pole
566 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 9.60 | 2 | Suspension
567 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 68.27 | 1 | Concrete Pole
568 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 9.66 | 3 | Suspension
569 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 65.78 | 1 | Concrete Pole
570 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 12.32 | 2 | Suspension
571 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 70.12 | 1 | Concrete Pole
572 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 12.15 | 3 | Suspension
573 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 65.77 | 1 | Concrete Pole
574 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 12.32 | 2 | Suspension
575 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 70.13 | 1 | Concrete Pole
576 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 12.15 | 3 | Suspension
577 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 70.30 | 1 | Concrete Pole
578 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 11.57 | 2 | Suspension
579 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 66.34 | 1 | Concrete Pole
580 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 11.43 | 3 | Suspension
581 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 70.30 | 1 | Concrete Pole
582 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 11.57 | 2 | Suspension
583 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 66.35 | 1 | Concrete Pole
584 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 11.42 | 3 | Suspension
585 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 52.47 | 1 | Concrete Pole
586 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 11.26 | 2 | Suspension
587 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 56.92 | 1 | Concrete Pole
588 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 10.85 | 2 | Suspension
589 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 52.47 | 1 | Concrete Pole
590 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 11.26 | 2 | Suspension
591 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 56.93 | 1 | Concrete Pole
592 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 10.85 | 2 | Suspension
593 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 55.05 | 1 | Concrete Pole
594 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.13 | 2 | Suspension
595 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 55.23 | 1 | Concrete Pole
596 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 7.89 | 3 | Suspension
597 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 55.05 | 1 | Concrete Pole
598 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.13 | 2 | Suspension
599 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 55.24 | 1 | Concrete Pole
600 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 7.89 | 3 | Suspension
601 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 52.44 | 1 | Concrete Pole
602 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 11.16 | 2 | Suspension
603 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 56.74 | 1 | Concrete Pole
604 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 10.75 | 2 | Suspension
605 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 52.43 | 1 | Concrete Pole
606 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 11.16 | 2 | Suspension
607 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 56.75 | 1 | Concrete Pole
608 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 10.75 | 2 | Suspension
609 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 57.57 | 1 | Concrete Pole
610 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 10.33 | 2 | Suspension
611 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 53.65 | 1 | Concrete Pole
612 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 9.92 | 3 | Suspension
613 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 57.56 | 1 | Concrete Pole
614 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 10.33 | 2 | Suspension
615 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 53.66 | 1 | Concrete Pole
616 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 9.92 | 3 | Suspension
617 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 53.19 | 1 | Concrete Pole
618 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 9.91 | 2 | Suspension
619 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 56.32 | 1 | Concrete Pole
620 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.56 | 3 | Suspension
621 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 53.19 | 1 | Concrete Pole
622 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 9.91 | 2 | Suspension
623 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 56.33 | 1 | Concrete Pole
624 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.56 | 3 | Suspension
625 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 41.73 | X-arm_M | X-Arm
626 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 7.31 | 2 | Suspension
627 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 41.73 | X-arm_M | X-Arm
628 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 7.31 | 2 | Suspension
629 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 52.12 | X-arm_B | X-Arm
630 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 10.85 | 1 | Suspension
631 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 50.45 | X-arm_M | X-Arm
632 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 10.83 | 1 | Suspension
633 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 60.56 | X-arm_M | X-Arm
634 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 11.35 | 2 | Suspension
635 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 64.08 | X-arm_M | X-Arm
636 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 11.28 | 2 | Suspension
637 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 46.87 | X-arm_M | X-Arm
638 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 10.90 | 3 | Suspension
639 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 49.57 | X-arm_M | X-Arm
640 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 10.98 | 3 | Suspension
641 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 47.00 | 1 | Concrete Pole
642 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 9.99 | 2 | Suspension
643 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 50.37 | 1 | Concrete Pole
644 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.64 | 2 | Suspension
645 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 64.30 | 1 | Concrete Pole
646 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 11.64 | 2 | Suspension
647 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 68.84 | 1 | Concrete Pole
648 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 11.58 | 3 | Suspension
649 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 64.63 | 1 | Concrete Pole
650 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 11.64 | 2 | Suspension
651 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 69.01 | 1 | Concrete Pole
652 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 11.58 | 3 | Suspension
653 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 66.15 | 1 | Concrete Pole
654 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 9.55 | 2 | Suspension
655 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 67.02 | 1 | Concrete Pole
656 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 9.65 | 3 | Suspension
657 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 66.46 | 1 | Concrete Pole
658 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 9.55 | 2 | Suspension
659 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 67.18 | 1 | Concrete Pole
660 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 9.65 | 3 | Suspension
661 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 64.12 | 1 | Concrete Pole
662 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 11.56 | 2 | Suspension
663 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 68.51 | 1 | Concrete Pole
664 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 11.50 | 3 | Suspension
665 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 64.45 | 1 | Concrete Pole
666 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 11.56 | 2 | Suspension
667 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 68.67 | 1 | Concrete Pole
668 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 11.51 | 3 | Suspension
669 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 68.12 | 1 | Concrete Pole
670 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 10.90 | 2 | Suspension
671 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 65.49 | 1 | Concrete Pole
672 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 10.87 | 3 | Suspension
673 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 68.42 | 1 | Concrete Pole
674 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 10.90 | 2 | Suspension
675 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 65.64 | 1 | Concrete Pole
676 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 10.87 | 3 | Suspension
677 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 53.42 | 1 | Concrete Pole
678 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 10.45 | 2 | Suspension
679 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 58.13 | 1 | Concrete Pole
680 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 10.27 | 2 | Suspension
681 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 53.75 | 1 | Concrete Pole
682 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 10.45 | 2 | Suspension
683 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 58.29 | 1 | Concrete Pole
684 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 10.27 | 2 | Suspension
685 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 55.56 | 1 | Concrete Pole
686 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.10 | 2 | Suspension
687 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 56.61 | 1 | Concrete Pole
688 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 7.89 | 3 | Suspension
689 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 55.87 | 1 | Concrete Pole
690 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.10 | 2 | Suspension
691 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 56.76 | 1 | Concrete Pole
692 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 7.89 | 3 | Suspension
693 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 53.37 | 1 | Concrete Pole
694 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 10.37 | 2 | Suspension
695 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 57.92 | 1 | Concrete Pole
696 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 10.18 | 2 | Suspension
697 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 53.69 | 1 | Concrete Pole
698 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 10.36 | 2 | Suspension
699 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 58.08 | 1 | Concrete Pole
700 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 10.18 | 2 | Suspension
701 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 57.68 | 1 | Concrete Pole
702 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 9.62 | 2 | Suspension
703 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 55.24 | 1 | Concrete Pole
704 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 9.43 | 2 | Suspension
705 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 57.98 | 1 | Concrete Pole
706 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 9.62 | 2 | Suspension
707 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 55.38 | 1 | Concrete Pole
708 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 9.43 | 2 | Suspension
709 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 54.00 | 1 | Concrete Pole
710 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 9.42 | 2 | Suspension
711 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 57.55 | 1 | Concrete Pole
712 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.22 | 2 | Suspension
713 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 54.32 | 1 | Concrete Pole
714 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 9.42 | 2 | Suspension
715 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 57.71 | 1 | Concrete Pole
716 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.22 | 2 | Suspension
717 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 38.02 | X-arm_M | X-Arm
718 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 6.55 | 2 | Suspension
719 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 38.02 | X-arm_M | X-Arm
720 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 6.55 | 2 | Suspension
721 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 47.53 | X-arm_B | X-Arm
722 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.85 | 1 | Suspension
723 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 45.96 | X-arm_M | X-Arm
724 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.84 | 1 | Suspension
725 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 54.50 | X-arm_M | X-Arm
726 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 10.10 | 2 | Suspension
727 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 58.11 | X-arm_M | X-Arm
728 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 10.07 | 2 | Suspension
729 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 42.66 | X-arm_M | X-Arm
730 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.80 | 3 | Suspension
731 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 45.43 | X-arm_M | X-Arm
732 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.85 | 3 | Suspension
733 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 46.97 | 1 | Concrete Pole
734 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 9.40 | 2 | Suspension
735 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 50.70 | 1 | Concrete Pole
736 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.24 | 2 | Suspension
737 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 65.36 | 1 | Concrete Pole
738 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 10.68 | 2 | Suspension
739 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 68.47 | 1 | Concrete Pole
740 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 10.79 | 3 | Suspension
741 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 66.06 | 1 | Concrete Pole
742 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 10.69 | 2 | Suspension
743 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 68.83 | 1 | Concrete Pole
744 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 10.80 | 3 | Suspension
745 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 66.37 | 1 | Concrete Pole
746 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 9.89 | 2 | Suspension
747 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 67.40 | 1 | Concrete Pole
748 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 10.01 | 3 | Suspension
749 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 67.03 | 1 | Concrete Pole
750 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 9.89 | 2 | Suspension
751 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 67.74 | 1 | Concrete Pole
752 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 10.01 | 3 | Suspension
753 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 65.22 | 1 | Concrete Pole
754 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 10.63 | 2 | Suspension
755 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 68.17 | 1 | Concrete Pole
756 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 10.74 | 3 | Suspension
757 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 65.90 | 1 | Concrete Pole
758 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 10.63 | 2 | Suspension
759 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 68.52 | 1 | Concrete Pole
760 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 10.74 | 3 | Suspension
761 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 67.51 | 1 | Concrete Pole
762 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 10.23 | 2 | Suspension
763 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 66.60 | 1 | Concrete Pole
764 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 10.35 | 3 | Suspension
765 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 68.16 | 1 | Concrete Pole
766 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 10.23 | 2 | Suspension
767 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 66.93 | 1 | Concrete Pole
768 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 10.35 | 3 | Suspension
769 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 55.34 | 1 | Concrete Pole
770 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 9.30 | 2 | Suspension
771 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 56.78 | 1 | Concrete Pole
772 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 9.16 | 3 | Suspension
773 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 54.21 | 1 | Concrete Pole
774 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 9.30 | 2 | Suspension
775 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 56.77 | 1 | Concrete Pole
776 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 9.16 | 3 | Suspension
777 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 55.69 | 1 | Concrete Pole
778 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.36 | 2 | Suspension
779 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 55.60 | 1 | Concrete Pole
780 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 8.18 | 3 | Suspension
781 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 54.91 | 1 | Concrete Pole
782 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.36 | 2 | Suspension
783 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 55.94 | 1 | Concrete Pole
784 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 8.18 | 3 | Suspension
785 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 55.19 | 1 | Concrete Pole
786 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 9.24 | 2 | Suspension
787 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 56.54 | 1 | Concrete Pole
788 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 9.10 | 3 | Suspension
789 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 54.09 | 1 | Concrete Pole
790 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 9.24 | 2 | Suspension
791 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 56.62 | 1 | Concrete Pole
792 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 9.10 | 3 | Suspension
793 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 56.21 | 1 | Concrete Pole
794 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 8.77 | 2 | Suspension
795 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 54.91 | 1 | Concrete Pole
796 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 8.61 | 3 | Suspension
797 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 56.33 | 1 | Concrete Pole
798 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 8.77 | 2 | Suspension
799 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 55.25 | 1 | Concrete Pole
800 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 8.61 | 3 | Suspension
801 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 55.33 | 1 | Concrete Pole
802 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 8.87 | 2 | Suspension
803 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 56.22 | 1 | Concrete Pole
804 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 8.71 | 3 | Suspension
805 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 54.30 | 1 | Concrete Pole
806 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 8.88 | 2 | Suspension
807 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 56.43 | 1 | Concrete Pole
808 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 8.72 | 3 | Suspension
809 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 28.95 | X-arm_M | X-Arm
810 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 4.90 | 3 | Suspension
811 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 28.95 | X-arm_M | X-Arm
812 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 4.90 | 3 | Suspension
813 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 36.56 | X-arm_B | X-Arm
814 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.34 | 1 | Suspension
815 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 34.82 | X-arm_M | X-Arm
816 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.34 | 1 | Suspension
817 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 39.82 | X-arm_M | X-Arm
818 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.43 | 2 | Suspension
819 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 43.50 | X-arm_M | X-Arm
820 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.39 | 2 | Suspension
821 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 31.56 | X-arm_M | X-Arm
822 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.41 | 3 | Suspension
823 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 34.29 | X-arm_M | X-Arm
824 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.49 | 3 | Suspension
825 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 51.33 | 1 | Concrete Pole
826 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 8.63 | 2 | Suspension
827 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 52.39 | 1 | Concrete Pole
828 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 8.48 | 3 | Suspension
829 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 51.52 | X-arm_B | X-Arm
830 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 12.76 | 2 | Suspension
831 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 59.75 | X-arm_M | X-Arm
832 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 12.67 | 3 | Suspension
833 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 51.65 | X-arm_B | X-Arm
834 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 12.76 | 2 | Suspension
835 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 59.91 | X-arm_M | X-Arm
836 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 12.66 | 3 | Suspension
837 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 43.71 | 1 | Concrete Pole
838 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 10.16 | 2 | Suspension
839 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 43.36 | 1 | Concrete Pole
840 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 10.12 | 3 | Suspension
841 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 43.87 | 1 | Concrete Pole
842 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 10.16 | 2 | Suspension
843 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 43.60 | 1 | Concrete Pole
844 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 10.12 | 3 | Suspension
845 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 50.48 | X-arm_B | X-Arm
846 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 12.68 | 2 | Suspension
847 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 58.44 | X-arm_M | X-Arm
848 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 12.58 | 3 | Suspension
849 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 50.61 | X-arm_B | X-Arm
850 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 12.68 | 2 | Suspension
851 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 58.60 | X-arm_M | X-Arm
852 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 12.58 | 3 | Suspension
853 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 50.32 | X-arm_M | X-Arm
854 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 11.97 | 2 | Suspension
855 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 42.57 | 1 | Concrete Pole
856 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 11.87 | 3 | Suspension
857 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 50.43 | X-arm_M | X-Arm
858 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 11.96 | 2 | Suspension
859 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 42.80 | 1 | Concrete Pole
860 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 11.87 | 3 | Suspension
861 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 48.40 | X-arm_B | X-Arm
862 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 11.56 | 2 | Suspension
863 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 56.96 | X-arm_M | X-Arm
864 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 11.32 | 2 | Suspension
865 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 48.32 | X-arm_B | X-Arm
866 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 11.55 | 2 | Suspension
867 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 57.00 | X-arm_M | X-Arm
868 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 11.32 | 2 | Suspension
869 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 38.28 | 1 | Concrete Pole
870 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.63 | 2 | Suspension
871 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 37.95 | 1 | Concrete Pole
872 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 8.32 | 2 | Suspension
873 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 38.43 | 1 | Concrete Pole
874 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.63 | 2 | Suspension
875 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 38.18 | 1 | Concrete Pole
876 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 8.32 | 2 | Suspension
877 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 47.32 | X-arm_B | X-Arm
878 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 11.46 | 2 | Suspension
879 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 55.60 | X-arm_M | X-Arm
880 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 11.23 | 2 | Suspension
881 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 47.24 | X-arm_B | X-Arm
882 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 11.46 | 2 | Suspension
883 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 55.64 | X-arm_M | X-Arm
884 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 11.23 | 2 | Suspension
885 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 46.32 | X-arm_M | X-Arm
886 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 10.67 | 2 | Suspension
887 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 37.53 | X-arm_B | X-Arm
888 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 10.42 | 2 | Suspension
889 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 46.43 | X-arm_M | X-Arm
890 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 10.67 | 2 | Suspension
891 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 37.63 | X-arm_B | X-Arm
892 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 10.42 | 2 | Suspension
893 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 38.76 | X-arm_B | X-Arm
894 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 10.28 | 2 | Suspension
895 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 45.50 | X-arm_M | X-Arm
896 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 10.02 | 2 | Suspension
897 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 38.69 | X-arm_B | X-Arm
898 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 10.28 | 2 | Suspension
899 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 45.59 | X-arm_M | X-Arm
900 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 10.02 | 2 | Suspension
901 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 42.25 | X-arm_M | X-Arm
902 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 7.37 | 2 | Suspension
903 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 42.25 | X-arm_M | X-Arm
904 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 7.37 | 2 | Suspension
905 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 54.07 | X-arm_B | X-Arm
906 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 11.29 | 1 | Suspension
907 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 51.19 | X-arm_M | X-Arm
908 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 11.27 | 1 | Suspension
909 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 61.23 | X-arm_M | X-Arm
910 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 11.43 | 2 | Suspension
911 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 65.04 | X-arm_M | X-Arm
912 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 11.40 | 2 | Suspension
913 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 47.40 | X-arm_M | X-Arm
914 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 11.30 | 3 | Suspension
915 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 50.29 | X-arm_M | X-Arm
916 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 11.33 | 3 | Suspension
917 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 41.36 | X-arm_B | X-Arm
918 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 10.31 | 2 | Suspension
919 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 48.35 | X-arm_M | X-Arm
920 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 10.11 | 2 | Suspension
921 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 62.84 | 1 | Concrete Pole
922 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 11.86 | 2 | Suspension
923 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 65.81 | 1 | Concrete Pole
924 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 11.77 | 3 | Suspension
925 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 63.19 | 1 | Concrete Pole
926 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 11.86 | 2 | Suspension
927 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 66.35 | 1 | Concrete Pole
928 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 11.77 | 3 | Suspension
929 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 64.88 | 1 | Concrete Pole
930 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 9.86 | 2 | Suspension
931 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 64.32 | 1 | Concrete Pole
932 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 9.86 | 3 | Suspension
933 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 65.21 | 1 | Concrete Pole
934 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 9.86 | 2 | Suspension
935 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 64.82 | 1 | Concrete Pole
936 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 9.86 | 3 | Suspension
937 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 62.75 | 1 | Concrete Pole
938 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 11.78 | 2 | Suspension
939 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 65.61 | 1 | Concrete Pole
940 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 11.69 | 3 | Suspension
941 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 63.10 | 1 | Concrete Pole
942 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 11.78 | 2 | Suspension
943 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 66.12 | 1 | Concrete Pole
944 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 11.69 | 3 | Suspension
945 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 66.94 | 1 | Concrete Pole
946 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 11.13 | 2 | Suspension
947 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 62.98 | 1 | Concrete Pole
948 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 11.06 | 3 | Suspension
949 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 67.26 | 1 | Concrete Pole
950 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 11.13 | 2 | Suspension
951 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 63.46 | 1 | Concrete Pole
952 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 11.06 | 3 | Suspension
953 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 54.40 | 1 | Concrete Pole
954 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 10.63 | 2 | Suspension
955 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 57.40 | 1 | Concrete Pole
956 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 10.39 | 2 | Suspension
957 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 54.76 | 1 | Concrete Pole
958 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 10.63 | 2 | Suspension
959 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 57.94 | 1 | Concrete Pole
960 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 10.39 | 2 | Suspension
961 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 56.55 | 1 | Concrete Pole
962 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 8.36 | 2 | Suspension
963 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 56.03 | 1 | Concrete Pole
964 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 8.07 | 3 | Suspension
965 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 56.88 | 1 | Concrete Pole
966 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 8.36 | 2 | Suspension
967 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 56.53 | 1 | Concrete Pole
968 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 8.07 | 3 | Suspension
969 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 54.37 | 1 | Concrete Pole
970 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 10.54 | 2 | Suspension
971 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 57.24 | 1 | Concrete Pole
972 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 10.30 | 2 | Suspension
973 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 54.71 | 1 | Concrete Pole
974 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 10.54 | 2 | Suspension
975 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 57.77 | 1 | Concrete Pole
976 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 10.30 | 2 | Suspension
977 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 58.66 | 1 | Concrete Pole
978 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 9.82 | 2 | Suspension
979 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 54.75 | 1 | Concrete Pole
980 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 9.56 | 2 | Suspension
981 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 58.98 | 1 | Concrete Pole
982 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 9.82 | 2 | Suspension
983 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 55.24 | 1 | Concrete Pole
984 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 9.56 | 2 | Suspension
985 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 55.00 | 1 | Concrete Pole
986 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 9.63 | 2 | Suspension
987 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 56.91 | 1 | Concrete Pole
988 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 9.37 | 2 | Suspension
989 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 55.34 | 1 | Concrete Pole
990 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 9.63 | 2 | Suspension
991 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 57.42 | 1 | Concrete Pole
992 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 9.37 | 2 | Suspension
993 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 37.94 | X-arm_M | X-Arm
994 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 6.56 | 2 | Suspension
995 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 37.94 | X-arm_M | X-Arm
996 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 6.56 | 2 | Suspension
997 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 47.85 | X-arm_B | X-Arm
998 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.93 | 1 | Suspension
999 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 45.88 | X-arm_M | X-Arm
1000 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.91 | 1 | Suspension
1001 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 54.32 | X-arm_M | X-Arm
1002 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 10.13 | 2 | Suspension
1003 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 58.03 | X-arm_M | X-Arm
1004 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 10.09 | 2 | Suspension
1005 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 42.29 | X-arm_M | X-Arm
1006 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 9.91 | 3 | Suspension
1007 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 45.12 | X-arm_M | X-Arm
1008 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 9.95 | 3 | Suspension
1009 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 48.78 | 1 | Concrete Pole
1010 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 9.58 | 2 | Suspension
1011 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 51.29 | 1 | Concrete Pole
1012 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 9.37 | 2 | Suspension
1013 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 60.32 | 1 | Concrete Pole
1014 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 9.84 | 2 | Suspension
1015 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 66.06 | 1 | Concrete Pole
1016 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 9.75 | 3 | Suspension
1017 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 60.48 | 1 | Concrete Pole
1018 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 9.84 | 2 | Suspension
1019 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 65.70 | 1 | Concrete Pole
1020 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 9.75 | 3 | Suspension
1021 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 61.98 | 1 | Concrete Pole
1022 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 7.72 | 2 | Suspension
1023 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 64.12 | 1 | Concrete Pole
1024 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 7.82 | 3 | Suspension
1025 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 62.12 | 1 | Concrete Pole
1026 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 7.72 | 2 | Suspension
1027 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 63.79 | 1 | Concrete Pole
1028 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 7.82 | 3 | Suspension
1029 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 60.20 | 1 | Concrete Pole
1030 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 9.76 | 2 | Suspension
1031 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 65.82 | 1 | Concrete Pole
1032 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 9.67 | 3 | Suspension
1033 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 60.36 | 1 | Concrete Pole
1034 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 9.75 | 2 | Suspension
1035 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 65.47 | 1 | Concrete Pole
1036 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 9.67 | 3 | Suspension
1037 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 63.97 | 1 | Concrete Pole
1038 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 9.03 | 2 | Suspension
1039 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 62.39 | 1 | Concrete Pole
1040 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 8.98 | 3 | Suspension
1041 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 63.83 | 1 | Concrete Pole
1042 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 9.03 | 2 | Suspension
1043 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 62.07 | 1 | Concrete Pole
1044 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 8.98 | 3 | Suspension
1045 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 57.92 | 1 | Concrete Pole
1046 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 9.09 | 2 | Suspension
1047 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 60.81 | 1 | Concrete Pole
1048 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 8.82 | 2 | Suspension
1049 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 58.09 | 1 | Concrete Pole
1050 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 9.09 | 2 | Suspension
1051 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 60.59 | 1 | Concrete Pole
1052 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 8.82 | 2 | Suspension
1053 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 58.89 | 1 | Concrete Pole
1054 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 6.76 | 2 | Suspension
1055 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 58.69 | 1 | Concrete Pole
1056 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 6.62 | 3 | Suspension
1057 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 59.05 | 1 | Concrete Pole
1058 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 6.76 | 2 | Suspension
1059 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 58.35 | 1 | Concrete Pole
1060 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 6.62 | 3 | Suspension
1061 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 57.75 | 1 | Concrete Pole
1062 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 9.00 | 2 | Suspension
1063 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 60.55 | 1 | Concrete Pole
1064 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 8.73 | 2 | Suspension
1065 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 57.91 | 1 | Concrete Pole
1066 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 9.00 | 2 | Suspension
1067 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 60.38 | 1 | Concrete Pole
1068 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 8.73 | 2 | Suspension
1069 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 60.09 | 1 | Concrete Pole
1070 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 8.21 | 2 | Suspension
1071 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 57.09 | 1 | Concrete Pole
1072 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 7.93 | 3 | Suspension
1073 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 60.24 | 1 | Concrete Pole
1074 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 8.21 | 2 | Suspension
1075 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 57.03 | 1 | Concrete Pole
1076 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 7.93 | 3 | Suspension
1077 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 58.07 | 1 | Concrete Pole
1078 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 8.08 | 2 | Suspension
1079 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 59.86 | 1 | Concrete Pole
1080 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 7.85 | 3 | Suspension
1081 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 58.23 | 1 | Concrete Pole
1082 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 8.08 | 2 | Suspension
1083 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 59.85 | 1 | Concrete Pole
1084 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 7.84 | 3 | Suspension
1085 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 33.27 | X-arm_M | X-Arm
1086 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 5.71 | 2 | Suspension
1087 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 33.27 | X-arm_M | X-Arm
1088 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 5.71 | 2 | Suspension
1089 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 41.53 | X-arm_B | X-Arm
1090 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 8.46 | 1 | Suspension
1091 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 43.84 | 1 | Concrete Pole
1092 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 8.45 | 1 | Suspension
1093 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 47.53 | X-arm_M | X-Arm
1094 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 8.75 | 2 | Suspension
1095 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 50.27 | X-arm_M | X-Arm
1096 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 8.72 | 2 | Suspension
1097 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 37.44 | X-arm_M | X-Arm
1098 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 8.39 | 3 | Suspension
1099 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 39.33 | X-arm_M | X-Arm
1100 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 8.45 | 3 | Suspension
1101 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 52.85 | 1 | Concrete Pole
1102 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 8.13 | 2 | Suspension
1103 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 54.02 | 1 | Concrete Pole
1104 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 7.89 | 2 | Suspension
1105 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 62.40 | 1 | Concrete Pole
1106 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 8.79 | 2 | Suspension
1107 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 65.83 | 1 | Concrete Pole
1108 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 8.60 | 3 | Suspension
1109 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 62.34 | 1 | Concrete Pole
1110 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 8.79 | 2 | Suspension
1111 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 65.67 | 1 | Concrete Pole
1112 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 8.60 | 3 | Suspension
1113 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 63.72 | 1 | Concrete Pole
1114 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 7.41 | 2 | Suspension
1115 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 64.20 | 1 | Concrete Pole
1116 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 7.26 | 3 | Suspension
1117 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 63.66 | 1 | Concrete Pole
1118 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 7.41 | 2 | Suspension
1119 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 64.05 | 1 | Concrete Pole
1120 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 7.26 | 3 | Suspension
1121 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 62.25 | 1 | Concrete Pole
1122 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 8.71 | 2 | Suspension
1123 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 65.49 | 1 | Concrete Pole
1124 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 8.53 | 3 | Suspension
1125 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 62.19 | 1 | Concrete Pole
1126 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 8.71 | 2 | Suspension
1127 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 65.34 | 1 | Concrete Pole
1128 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 8.52 | 3 | Suspension
1129 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 65.17 | 1 | Concrete Pole
1130 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 8.11 | 2 | Suspension
1131 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 62.88 | 1 | Concrete Pole
1132 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 7.93 | 3 | Suspension
1133 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 65.11 | 1 | Concrete Pole
1134 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 8.11 | 2 | Suspension
1135 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 62.74 | 1 | Concrete Pole
1136 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 7.93 | 3 | Suspension
1137 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 55.46 | 1 | Concrete Pole
1138 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 8.06 | 2 | Suspension
1139 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 58.56 | 1 | Concrete Pole
1140 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 7.71 | 2 | Suspension
1141 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 55.42 | 1 | Concrete Pole
1142 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 8.06 | 2 | Suspension
1143 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 58.39 | 1 | Concrete Pole
1144 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 7.71 | 2 | Suspension
1145 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 56.67 | 1 | Concrete Pole
1146 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 6.55 | 2 | Suspension
1147 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 57.19 | 1 | Concrete Pole
1148 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 6.16 | 3 | Suspension
1149 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 56.61 | 1 | Concrete Pole
1150 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 6.55 | 2 | Suspension
1151 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 57.04 | 1 | Concrete Pole
1152 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 6.16 | 3 | Suspension
1153 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 55.43 | 1 | Concrete Pole
1154 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 7.98 | 2 | Suspension
1155 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 58.35 | 1 | Concrete Pole
1156 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 7.62 | 2 | Suspension
1157 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 55.39 | 1 | Concrete Pole
1158 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 7.98 | 2 | Suspension
1159 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 58.19 | 1 | Concrete Pole
1160 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 7.62 | 2 | Suspension
1161 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 58.46 | 1 | Concrete Pole
1162 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 7.33 | 2 | Suspension
1163 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 56.00 | 1 | Concrete Pole
1164 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 6.94 | 2 | Suspension
1165 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 58.44 | 1 | Concrete Pole
1166 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 7.33 | 2 | Suspension
1167 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 55.86 | 1 | Concrete Pole
1168 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 6.94 | 2 | Suspension
1169 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 55.77 | 1 | Concrete Pole
1170 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 7.40 | 2 | Suspension
1171 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 58.02 | 1 | Concrete Pole
1172 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 7.02 | 3 | Suspension
1173 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 55.75 | 1 | Concrete Pole
1174 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 7.40 | 2 | Suspension
1175 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 57.87 | 1 | Concrete Pole
1176 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 7.02 | 3 | Suspension
1177 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 28.44 | X-arm_M | X-Arm
1178 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 4.78 | 2 | Suspension
1179 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 28.44 | X-arm_M | X-Arm
1180 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 4.78 | 2 | Suspension
1181 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 35.37 | X-arm_B | X-Arm
1182 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.15 | 1 | Suspension
1183 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 39.14 | 1 | Concrete Pole
1184 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.11 | 1 | Suspension
1185 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 39.54 | X-arm_M | X-Arm
1186 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.26 | 2 | Suspension
1187 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 42.30 | X-arm_M | X-Arm
1188 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.21 | 2 | Suspension
1189 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 31.29 | X-arm_M | X-Arm
1190 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.14 | 3 | Suspension
1191 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 33.49 | X-arm_M | X-Arm
1192 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.15 | 3 | Suspension
1193 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 51.74 | 1 | Concrete Pole
1194 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 7.31 | 2 | Suspension
1195 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 52.82 | 1 | Concrete Pole
1196 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 6.99 | 2 | Suspension
1197 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 63.97 | 1 | Concrete Pole
1198 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 9.02 | 2 | Suspension
1199 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 66.38 | 1 | Concrete Pole
1200 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 8.87 | 3 | Suspension
1201 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 64.02 | 1 | Concrete Pole
1202 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 9.02 | 2 | Suspension
1203 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 66.51 | 1 | Concrete Pole
1204 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 8.87 | 3 | Suspension
1205 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 64.44 | 1 | Concrete Pole
1206 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 7.14 | 2 | Suspension
1207 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 63.45 | 1 | Concrete Pole
1208 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 7.07 | 3 | Suspension
1209 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 64.49 | 1 | Concrete Pole
1210 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 7.14 | 2 | Suspension
1211 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 63.57 | 1 | Concrete Pole
1212 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 7.07 | 3 | Suspension
1213 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 63.65 | 1 | Concrete Pole
1214 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 8.94 | 2 | Suspension
1215 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 65.93 | 1 | Concrete Pole
1216 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 8.79 | 3 | Suspension
1217 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 63.70 | 1 | Concrete Pole
1218 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 8.94 | 2 | Suspension
1219 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 66.05 | 1 | Concrete Pole
1220 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 8.79 | 3 | Suspension
1221 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 65.29 | 1 | Concrete Pole
1222 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 8.23 | 2 | Suspension
1223 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 61.03 | 1 | Concrete Pole
1224 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 8.10 | 3 | Suspension
1225 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 65.34 | 1 | Concrete Pole
1226 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 8.23 | 2 | Suspension
1227 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 61.15 | 1 | Concrete Pole
1228 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 8.10 | 3 | Suspension
1229 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 56.94 | 1 | Concrete Pole
1230 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 8.40 | 2 | Suspension
1231 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 61.02 | 1 | Concrete Pole
1232 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 8.15 | 2 | Suspension
1233 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 56.99 | 1 | Concrete Pole
1234 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 8.40 | 2 | Suspension
1235 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 60.99 | 1 | Concrete Pole
1236 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 8.15 | 2 | Suspension
1237 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 57.70 | 1 | Concrete Pole
1238 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 6.36 | 2 | Suspension
1239 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 56.75 | 1 | Concrete Pole
1240 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 6.05 | 3 | Suspension
1241 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 57.74 | 1 | Concrete Pole
1242 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 6.36 | 2 | Suspension
1243 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 56.86 | 1 | Concrete Pole
1244 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 6.05 | 3 | Suspension
1245 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 56.75 | 1 | Concrete Pole
1246 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 8.31 | 2 | Suspension
1247 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 59.85 | 1 | Concrete Pole
1248 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 8.05 | 2 | Suspension
1249 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 56.79 | 1 | Concrete Pole
1250 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 8.31 | 2 | Suspension
1251 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 59.82 | 1 | Concrete Pole
1252 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 8.05 | 2 | Suspension
1253 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 58.71 | 1 | Concrete Pole
1254 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 7.55 | 2 | Suspension
1255 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 54.49 | 1 | Concrete Pole
1256 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 7.27 | 2 | Suspension
1257 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 58.75 | 1 | Concrete Pole
1258 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 7.55 | 2 | Suspension
1259 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 54.60 | 1 | Concrete Pole
1260 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 7.27 | 2 | Suspension
1261 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 57.01 | 1 | Concrete Pole
1262 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 7.51 | 2 | Suspension
1263 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 58.39 | 1 | Concrete Pole
1264 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 7.23 | 2 | Suspension
1265 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 57.06 | 1 | Concrete Pole
1266 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 7.51 | 2 | Suspension
1267 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 58.51 | 1 | Concrete Pole
1268 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 7.23 | 2 | Suspension
1269 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 30.77 | X-arm_M | X-Arm
1270 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 5.21 | 2 | Suspension
1271 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 30.77 | X-arm_M | X-Arm
1272 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 5.21 | 2 | Suspension
1273 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 38.12 | X-arm_B | X-Arm
1274 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.80 | 1 | Suspension
1275 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 40.34 | 1 | Concrete Pole
1276 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.78 | 1 | Suspension
1277 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 43.37 | X-arm_M | X-Arm
1278 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.94 | 2 | Suspension
1279 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 46.11 | X-arm_M | X-Arm
1280 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.91 | 2 | Suspension
1281 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 34.15 | X-arm_M | X-Arm
1282 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 7.77 | 3 | Suspension
1283 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 36.25 | X-arm_M | X-Arm
1284 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 7.78 | 3 | Suspension
1285 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 48.96 | 1 | Concrete Pole
1286 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 7.55 | 2 | Suspension
1287 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 51.17 | 1 | Concrete Pole
1288 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 7.32 | 2 | Suspension

## Tab_5
rowtext | str_no | structure_name | load_case | joint_label | long_defl | tran_defl | vert_defl | resultant_defl | long_rot | tran_rot | twist
1 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | -0.63 | 15.79 | -0.08 | 15.80 | -0.04 | -0.64 | -0.03
2 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | -0.60 | -17.56 | -0.10 | 17.57 | -0.04 | 0.75 | 0.03
3 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | -0.63 | 15.79 | -0.08 | 15.80 | -0.04 | -0.64 | -0.03
4 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | -0.61 | -17.56 | -0.10 | 17.57 | -0.04 | 0.75 | 0.03
5 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 0.35 | 16.61 | -0.09 | 16.61 | 0.01 | -0.69 | -0.03
6 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 0.51 | -16.56 | -0.09 | 16.57 | 0.01 | 0.69 | 0.03
7 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 0.35 | 16.61 | -0.09 | 16.61 | 0.01 | -0.69 | -0.03
8 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 0.50 | -16.56 | -0.09 | 16.57 | 0.01 | 0.69 | 0.03
9 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | -0.54 | 15.77 | -0.08 | 15.78 | -0.04 | -0.64 | -0.03
10 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | -0.53 | -17.48 | -0.10 | 17.49 | -0.04 | 0.75 | 0.03
11 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | -0.54 | 15.77 | -0.08 | 15.78 | -0.04 | -0.64 | -0.03
12 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | -0.53 | -17.48 | -0.10 | 17.49 | -0.04 | 0.75 | 0.03
13 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 1.64 | 17.45 | -0.09 | 17.52 | 0.07 | -0.75 | -0.03
14 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 1.56 | -15.64 | -0.08 | 15.71 | 0.07 | 0.64 | 0.03
15 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 1.64 | 17.45 | -0.09 | 17.52 | 0.07 | -0.75 | -0.03
16 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 1.56 | -15.64 | -0.08 | 15.71 | 0.07 | 0.64 | 0.03
17 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -1.55 | 13.75 | -0.07 | 13.84 | -0.08 | -0.55 | -0.02
18 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | -1.38 | -15.53 | -0.08 | 15.59 | -0.08 | 0.67 | 0.02
19 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -1.56 | 13.75 | -0.07 | 13.84 | -0.08 | -0.55 | -0.02
20 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | -1.38 | -15.53 | -0.08 | 15.59 | -0.08 | 0.67 | 0.02
21 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | -0.73 | 14.58 | -0.07 | 14.60 | -0.03 | -0.61 | -0.02
22 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | -0.59 | -14.55 | -0.07 | 14.56 | -0.03 | 0.61 | 0.02
23 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | -0.74 | 14.58 | -0.07 | 14.60 | -0.03 | -0.61 | -0.02
24 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | -0.60 | -14.55 | -0.07 | 14.56 | -0.03 | 0.61 | 0.02
25 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -1.43 | 13.75 | -0.06 | 13.82 | -0.07 | -0.55 | -0.02
26 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | -1.27 | -15.46 | -0.08 | 15.51 | -0.07 | 0.66 | 0.02
27 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -1.43 | 13.75 | -0.06 | 13.82 | -0.07 | -0.55 | -0.02
28 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | -1.27 | -15.46 | -0.08 | 15.51 | -0.07 | 0.66 | 0.02
29 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 0.88 | 15.42 | -0.07 | 15.45 | 0.04 | -0.66 | -0.03
30 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 1.00 | -13.64 | -0.06 | 13.68 | 0.05 | 0.55 | 0.02
31 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 0.88 | 15.42 | -0.07 | 15.45 | 0.04 | -0.66 | -0.03
32 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 1.00 | -13.64 | -0.06 | 13.68 | 0.05 | 0.55 | 0.02
33 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | -1.08 | 13.98 | -0.07 | 14.03 | -0.06 | -0.57 | -0.02
34 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | -0.92 | -15.20 | -0.08 | 15.23 | -0.05 | 0.65 | 0.02
35 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | -1.08 | 13.98 | -0.07 | 14.03 | -0.06 | -0.57 | -0.02
36 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | -0.92 | -15.20 | -0.08 | 15.23 | -0.05 | 0.65 | 0.02
37 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -1.17 | -0.94 | -0.01 | 1.50 | -0.07 | 0.06 | 0.00
38 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -1.17 | -0.94 | -0.01 | 1.50 | -0.07 | 0.06 | 0.00
39 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.48 | 0.28 | -0.01 | 1.51 | -0.08 | 0.02 | -0.00
40 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.41 | -3.08 | -0.02 | 3.39 | -0.08 | 0.16 | 0.01
41 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.53 | 0.28 | -0.01 | 1.55 | -0.09 | 0.02 | -0.00
42 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.45 | -3.18 | -0.02 | 3.50 | -0.08 | 0.16 | 0.01
43 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.48 | 0.89 | -0.01 | 1.73 | -0.08 | -0.02 | -0.00
44 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.45 | -2.49 | -0.02 | 2.88 | -0.08 | 0.12 | 0.00
45 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -1.51 | 12.54 | -0.06 | 12.64 | -0.08 | -0.51 | -0.02
46 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -1.35 | -13.98 | -0.07 | 14.05 | -0.07 | 0.60 | 0.02
47 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | -3.08 | 15.51 | -0.08 | 15.82 | -0.14 | -0.63 | -0.03
48 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | -3.18 | -17.46 | -0.10 | 17.75 | -0.15 | 0.75 | 0.03
49 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | -3.08 | 15.51 | -0.08 | 15.82 | -0.14 | -0.63 | -0.03
50 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | -3.18 | -17.46 | -0.10 | 17.75 | -0.15 | 0.75 | 0.03
51 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | -1.62 | 16.34 | -0.09 | 16.42 | -0.07 | -0.68 | -0.03
52 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | -1.73 | -16.47 | -0.09 | 16.56 | -0.07 | 0.69 | 0.02
53 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | -1.62 | 16.34 | -0.09 | 16.42 | -0.07 | -0.68 | -0.03
54 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | -1.73 | -16.47 | -0.09 | 16.56 | -0.07 | 0.69 | 0.02
55 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | -2.91 | 15.50 | -0.08 | 15.77 | -0.13 | -0.63 | -0.03
56 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | -3.00 | -17.39 | -0.10 | 17.65 | -0.14 | 0.75 | 0.03
57 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | -2.91 | 15.50 | -0.08 | 15.77 | -0.13 | -0.63 | -0.03
58 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | -3.00 | -17.39 | -0.10 | 17.65 | -0.14 | 0.75 | 0.03
59 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | -0.44 | 17.17 | -0.09 | 17.18 | -0.01 | -0.73 | -0.03
60 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | -0.56 | -15.55 | -0.07 | 15.56 | -0.01 | 0.63 | 0.02
61 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | -0.44 | 17.17 | -0.09 | 17.18 | -0.01 | -0.73 | -0.03
62 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | -0.56 | -15.55 | -0.07 | 15.56 | -0.01 | 0.63 | 0.02
63 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -1.59 | 13.54 | -0.06 | 13.63 | -0.08 | -0.54 | -0.02
64 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | -1.71 | -15.49 | -0.08 | 15.58 | -0.09 | 0.67 | 0.02
65 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -1.60 | 13.54 | -0.06 | 13.63 | -0.08 | -0.54 | -0.02
66 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | -1.71 | -15.49 | -0.08 | 15.58 | -0.09 | 0.67 | 0.02
67 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | -0.78 | 14.37 | -0.07 | 14.39 | -0.03 | -0.60 | -0.02
68 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | -0.90 | -14.51 | -0.07 | 14.54 | -0.04 | 0.61 | 0.02
69 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | -0.78 | 14.37 | -0.07 | 14.39 | -0.03 | -0.60 | -0.02
70 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | -0.90 | -14.51 | -0.07 | 14.54 | -0.04 | 0.61 | 0.02
71 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -1.47 | 13.53 | -0.06 | 13.61 | -0.08 | -0.54 | -0.02
72 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | -1.58 | -15.42 | -0.08 | 15.50 | -0.08 | 0.66 | 0.02
73 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -1.47 | 13.53 | -0.06 | 13.61 | -0.08 | -0.54 | -0.02
74 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | -1.58 | -15.42 | -0.08 | 15.50 | -0.08 | 0.66 | 0.02
75 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 0.83 | 15.21 | -0.07 | 15.23 | 0.04 | -0.65 | -0.02
76 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 0.71 | -13.60 | -0.06 | 13.62 | 0.03 | 0.55 | 0.02
77 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 0.83 | 15.21 | -0.07 | 15.23 | 0.04 | -0.65 | -0.02
78 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 0.71 | -13.60 | -0.06 | 13.62 | 0.03 | 0.55 | 0.02
79 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | -1.12 | 13.77 | -0.06 | 13.82 | -0.06 | -0.56 | -0.02
80 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | -1.23 | -15.16 | -0.08 | 15.21 | -0.06 | 0.65 | 0.02
81 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | -1.12 | 13.77 | -0.06 | 13.82 | -0.06 | -0.56 | -0.02
82 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | -1.23 | -15.16 | -0.08 | 15.21 | -0.06 | 0.65 | 0.02
83 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -1.38 | -0.98 | -0.01 | 1.70 | -0.07 | 0.06 | 0.00
84 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -1.38 | -0.98 | -0.01 | 1.70 | -0.07 | 0.06 | 0.00
85 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.09 | 0.20 | -0.01 | 2.09 | -0.10 | 0.02 | -0.00
86 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -2.07 | -3.12 | -0.02 | 3.75 | -0.10 | 0.16 | 0.00
87 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.08 | 0.20 | -0.01 | 2.09 | -0.11 | 0.02 | -0.00
88 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -2.06 | -3.22 | -0.02 | 3.82 | -0.11 | 0.17 | 0.00
89 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.07 | 0.80 | -0.01 | 2.22 | -0.11 | -0.02 | -0.00
90 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -2.07 | -2.53 | -0.02 | 3.27 | -0.11 | 0.12 | 0.00
91 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -0.76 | 12.35 | -0.05 | 12.37 | -0.04 | -0.50 | -0.02
92 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -0.90 | -13.93 | -0.07 | 13.96 | -0.05 | 0.60 | 0.02
93 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 5.33 | 12.84 | -0.07 | 13.90 | 0.20 | -0.51 | -0.01
94 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 6.33 | -14.24 | -0.08 | 15.58 | 0.23 | 0.61 | 0.03
95 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 5.44 | 12.84 | -0.07 | 13.94 | 0.20 | -0.51 | -0.01
96 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 6.34 | -14.24 | -0.08 | 15.59 | 0.23 | 0.61 | 0.03
97 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 6.00 | 13.69 | -0.07 | 14.95 | 0.23 | -0.57 | -0.01
98 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 6.91 | -13.27 | -0.07 | 14.96 | 0.27 | 0.55 | 0.03
99 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 6.10 | 13.69 | -0.07 | 14.99 | 0.24 | -0.57 | -0.01
100 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 6.92 | -13.27 | -0.07 | 14.97 | 0.27 | 0.55 | 0.03
101 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 5.24 | 12.83 | -0.06 | 13.86 | 0.19 | -0.51 | -0.01
102 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 6.20 | -14.18 | -0.08 | 15.47 | 0.23 | 0.61 | 0.03
103 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 5.34 | 12.83 | -0.06 | 13.90 | 0.20 | -0.52 | -0.01
104 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 6.22 | -14.18 | -0.08 | 15.48 | 0.23 | 0.61 | 0.03
105 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 6.71 | 14.55 | -0.08 | 16.02 | 0.27 | -0.62 | -0.01
106 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 7.56 | -12.37 | -0.07 | 14.50 | 0.30 | 0.50 | 0.03
107 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 6.80 | 14.55 | -0.08 | 16.06 | 0.28 | -0.62 | -0.01
108 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 7.58 | -12.37 | -0.07 | 14.50 | 0.31 | 0.50 | 0.03
109 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | 0.54 | 11.54 | -0.05 | 11.55 | 0.01 | -0.46 | -0.01
110 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | 1.53 | -12.94 | -0.06 | 13.03 | 0.04 | 0.56 | 0.02
111 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | 0.63 | 11.54 | -0.05 | 11.55 | 0.01 | -0.46 | -0.01
112 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | 1.55 | -12.94 | -0.06 | 13.03 | 0.04 | 0.56 | 0.02
113 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 1.57 | 12.39 | -0.05 | 12.49 | 0.06 | -0.51 | -0.02
114 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 2.47 | -11.99 | -0.05 | 12.24 | 0.09 | 0.50 | 0.02
115 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 1.66 | 12.39 | -0.05 | 12.50 | 0.06 | -0.51 | -0.02
116 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 2.48 | -11.99 | -0.05 | 12.24 | 0.09 | 0.50 | 0.02
117 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | 0.59 | 11.53 | -0.05 | 11.55 | 0.01 | -0.46 | -0.01
118 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 1.55 | -12.88 | -0.06 | 12.97 | 0.04 | 0.55 | 0.02
119 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | 0.68 | 11.53 | -0.05 | 11.55 | 0.01 | -0.46 | -0.01
120 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | 1.57 | -12.88 | -0.06 | 12.97 | 0.05 | 0.55 | 0.02
121 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 2.48 | 13.24 | -0.06 | 13.47 | 0.11 | -0.57 | -0.02
122 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 3.32 | -11.10 | -0.04 | 11.58 | 0.14 | 0.44 | 0.02
123 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 2.56 | 13.24 | -0.06 | 13.49 | 0.11 | -0.57 | -0.02
124 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 3.33 | -11.10 | -0.04 | 11.59 | 0.14 | 0.44 | 0.02
125 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | 0.88 | 11.78 | -0.05 | 11.81 | 0.02 | -0.48 | -0.01
126 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 1.82 | -12.63 | -0.06 | 12.76 | 0.06 | 0.54 | 0.02
127 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | 0.97 | 11.78 | -0.05 | 11.82 | 0.03 | -0.48 | -0.01
128 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 1.84 | -12.63 | -0.06 | 12.76 | 0.06 | 0.54 | 0.02
129 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -1.04 | -0.78 | -0.01 | 1.30 | -0.06 | 0.05 | 0.00
130 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -1.04 | -0.78 | -0.01 | 1.30 | -0.06 | 0.05 | 0.00
131 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.39 | 0.21 | -0.01 | 1.40 | -0.07 | 0.02 | -0.00
132 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.18 | -2.42 | -0.01 | 2.69 | -0.07 | 0.13 | 0.00
133 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.40 | 0.23 | -0.01 | 1.42 | -0.08 | 0.02 | -0.00
134 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.18 | -2.47 | -0.01 | 2.74 | -0.07 | 0.13 | 0.00
135 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.39 | 0.65 | -0.01 | 1.53 | -0.08 | -0.01 | -0.00
136 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.20 | -1.98 | -0.01 | 2.32 | -0.07 | 0.10 | 0.00
137 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -1.14 | 10.46 | -0.04 | 10.52 | -0.06 | -0.42 | -0.02
138 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -0.53 | -11.60 | -0.05 | 11.61 | -0.04 | 0.50 | 0.02
139 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 0.46 | 13.32 | -0.06 | 13.33 | 0.00 | -0.54 | -0.02
140 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 4.32 | -17.83 | -0.11 | 18.34 | 0.15 | 0.76 | 0.03
141 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 0.85 | 13.32 | -0.06 | 13.35 | 0.02 | -0.54 | -0.02
142 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 4.41 | -17.82 | -0.11 | 18.36 | 0.15 | 0.76 | 0.03
143 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 1.51 | 14.12 | -0.07 | 14.20 | 0.06 | -0.59 | -0.02
144 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 5.06 | -16.88 | -0.10 | 17.62 | 0.19 | 0.71 | 0.03
145 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 1.87 | 14.12 | -0.07 | 14.25 | 0.07 | -0.59 | -0.02
146 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 5.14 | -16.88 | -0.10 | 17.64 | 0.20 | 0.71 | 0.03
147 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 0.52 | 13.32 | -0.06 | 13.33 | 0.01 | -0.54 | -0.02
148 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 4.26 | -17.75 | -0.11 | 18.26 | 0.15 | 0.76 | 0.03
149 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 0.90 | 13.32 | -0.06 | 13.35 | 0.02 | -0.54 | -0.02
150 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 4.34 | -17.75 | -0.11 | 18.27 | 0.15 | 0.76 | 0.03
151 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 2.42 | 14.93 | -0.07 | 15.13 | 0.10 | -0.64 | -0.02
152 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 5.80 | -16.01 | -0.09 | 17.02 | 0.23 | 0.65 | 0.03
153 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 2.76 | 14.93 | -0.07 | 15.19 | 0.12 | -0.64 | -0.02
154 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 5.87 | -16.00 | -0.09 | 17.05 | 0.24 | 0.65 | 0.03
155 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -1.29 | 11.63 | -0.05 | 11.70 | -0.07 | -0.46 | -0.02
156 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | 1.88 | -16.05 | -0.09 | 16.16 | 0.06 | 0.69 | 0.03
157 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -1.03 | 11.63 | -0.05 | 11.67 | -0.06 | -0.46 | -0.02
158 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | 1.96 | -16.05 | -0.09 | 16.17 | 0.06 | 0.69 | 0.03
159 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | -0.62 | 12.43 | -0.05 | 12.45 | -0.03 | -0.52 | -0.02
160 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 2.81 | -15.12 | -0.08 | 15.38 | 0.10 | 0.63 | 0.02
161 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | -0.19 | 12.43 | -0.05 | 12.43 | -0.01 | -0.52 | -0.02
162 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 2.88 | -15.12 | -0.08 | 15.39 | 0.11 | 0.63 | 0.02
163 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -1.17 | 11.62 | -0.05 | 11.68 | -0.06 | -0.46 | -0.02
164 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 1.90 | -15.98 | -0.08 | 16.10 | 0.06 | 0.68 | 0.03
165 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -0.93 | 11.63 | -0.05 | 11.66 | -0.05 | -0.46 | -0.02
166 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | 1.98 | -15.98 | -0.08 | 16.10 | 0.06 | 0.68 | 0.03
167 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 0.87 | 13.24 | -0.06 | 13.27 | 0.04 | -0.57 | -0.02
168 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 3.65 | -14.26 | -0.07 | 14.72 | 0.15 | 0.58 | 0.02
169 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 1.09 | 13.24 | -0.06 | 13.29 | 0.05 | -0.57 | -0.02
170 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 3.72 | -14.25 | -0.07 | 14.73 | 0.15 | 0.58 | 0.02
171 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | -0.86 | 11.85 | -0.05 | 11.88 | -0.05 | -0.48 | -0.02
172 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 2.16 | -15.74 | -0.08 | 15.89 | 0.07 | 0.67 | 0.03
173 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | -0.63 | 11.85 | -0.05 | 11.87 | -0.04 | -0.48 | -0.02
174 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 2.24 | -15.74 | -0.08 | 15.89 | 0.07 | 0.67 | 0.03
175 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -0.91 | -1.64 | -0.01 | 1.88 | -0.05 | 0.09 | 0.00
176 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -0.91 | -1.64 | -0.01 | 1.88 | -0.05 | 0.09 | 0.00
177 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.37 | -0.87 | -0.01 | 1.62 | -0.08 | 0.06 | 0.00
178 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.90 | -3.99 | -0.02 | 4.09 | -0.06 | 0.19 | 0.01
179 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.36 | -0.90 | -0.01 | 1.63 | -0.08 | 0.07 | 0.00
180 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.87 | -4.10 | -0.02 | 4.19 | -0.06 | 0.20 | 0.01
181 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.33 | -0.36 | -0.01 | 1.38 | -0.07 | 0.03 | 0.00
182 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.87 | -3.49 | -0.02 | 3.59 | -0.06 | 0.16 | 0.01
183 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -2.27 | 10.68 | -0.04 | 10.92 | -0.10 | -0.43 | -0.02
184 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | 1.26 | -14.32 | -0.07 | 14.37 | 0.03 | 0.61 | 0.02
185 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 7.55 | 15.80 | -0.10 | 17.51 | 0.28 | -0.64 | -0.01
186 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 7.71 | -17.48 | -0.12 | 19.10 | 0.29 | 0.75 | 0.04
187 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 7.56 | 15.80 | -0.10 | 17.51 | 0.28 | -0.64 | -0.01
188 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 7.71 | -17.48 | -0.12 | 19.10 | 0.29 | 0.75 | 0.04
189 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 8.07 | 16.56 | -0.10 | 18.42 | 0.32 | -0.69 | -0.01
190 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 8.20 | -16.56 | -0.11 | 18.48 | 0.32 | 0.69 | 0.03
191 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 8.07 | 16.56 | -0.10 | 18.42 | 0.32 | -0.69 | -0.01
192 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 8.20 | -16.56 | -0.11 | 18.48 | 0.32 | 0.69 | 0.03
193 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 7.39 | 15.79 | -0.10 | 17.43 | 0.28 | -0.64 | -0.01
194 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 7.54 | -17.41 | -0.11 | 18.97 | 0.28 | 0.75 | 0.04
195 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 7.39 | 15.79 | -0.10 | 17.43 | 0.28 | -0.64 | -0.01
196 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 7.54 | -17.41 | -0.11 | 18.97 | 0.28 | 0.75 | 0.04
197 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 8.69 | 17.33 | -0.11 | 19.39 | 0.35 | -0.74 | -0.01
198 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 8.81 | -15.71 | -0.10 | 18.01 | 0.35 | 0.64 | 0.03
199 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 8.69 | 17.33 | -0.11 | 19.39 | 0.35 | -0.74 | -0.01
200 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 8.81 | -15.71 | -0.10 | 18.01 | 0.35 | 0.64 | 0.03
201 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -0.01 | 13.81 | -0.07 | 13.81 | -0.02 | -0.56 | -0.02
202 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | 0.17 | -15.50 | -0.08 | 15.50 | -0.01 | 0.66 | 0.03
203 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -0.01 | 13.81 | -0.07 | 13.81 | -0.02 | -0.56 | -0.02
204 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | 0.17 | -15.50 | -0.08 | 15.50 | -0.01 | 0.66 | 0.03
205 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 1.10 | 14.57 | -0.07 | 14.61 | 0.04 | -0.61 | -0.02
206 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 1.25 | -14.59 | -0.07 | 14.64 | 0.04 | 0.61 | 0.02
207 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 1.10 | 14.57 | -0.07 | 14.61 | 0.04 | -0.61 | -0.02
208 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 1.25 | -14.59 | -0.07 | 14.64 | 0.04 | 0.61 | 0.02
209 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | 0.06 | 13.80 | -0.06 | 13.80 | -0.01 | -0.56 | -0.02
210 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 0.24 | -15.43 | -0.08 | 15.43 | -0.01 | 0.66 | 0.03
211 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | 0.07 | 13.80 | -0.06 | 13.80 | -0.01 | -0.56 | -0.02
212 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | 0.24 | -15.43 | -0.08 | 15.43 | -0.01 | 0.66 | 0.03
213 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 2.05 | 15.35 | -0.08 | 15.48 | 0.09 | -0.66 | -0.02
214 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 2.19 | -13.75 | -0.06 | 13.92 | 0.09 | 0.56 | 0.02
215 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 2.06 | 15.35 | -0.08 | 15.48 | 0.09 | -0.66 | -0.02
216 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 2.19 | -13.75 | -0.06 | 13.92 | 0.09 | 0.56 | 0.02
217 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | 0.37 | 14.02 | -0.07 | 14.02 | 0.00 | -0.57 | -0.02
218 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 0.54 | -15.19 | -0.08 | 15.20 | 0.01 | 0.65 | 0.03
219 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | 0.37 | 14.02 | -0.07 | 14.02 | 0.00 | -0.57 | -0.02
220 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 0.53 | -15.19 | -0.08 | 15.20 | 0.01 | 0.65 | 0.03
221 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -0.90 | -0.90 | -0.01 | 1.28 | -0.05 | 0.06 | 0.00
222 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -0.90 | -0.90 | -0.01 | 1.28 | -0.05 | 0.06 | 0.00
223 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.20 | 0.32 | -0.01 | 1.24 | -0.07 | 0.01 | 0.00
224 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.13 | -3.00 | -0.02 | 3.20 | -0.07 | 0.15 | 0.01
225 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.23 | 0.32 | -0.01 | 1.27 | -0.07 | 0.02 | 0.00
226 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.16 | -3.10 | -0.02 | 3.31 | -0.07 | 0.16 | 0.01
227 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.22 | 0.88 | -0.01 | 1.51 | -0.07 | -0.02 | -0.00
228 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.15 | -2.44 | -0.01 | 2.70 | -0.07 | 0.12 | 0.00
229 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -2.10 | 12.60 | -0.06 | 12.77 | -0.10 | -0.51 | -0.02
230 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -1.53 | -13.97 | -0.07 | 14.06 | -0.08 | 0.60 | 0.02
231 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 2.22 | 10.53 | -0.04 | 10.76 | 0.07 | -0.39 | -0.01
232 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 2.39 | -11.67 | -0.05 | 11.91 | 0.07 | 0.45 | 0.02
233 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 2.23 | 10.53 | -0.04 | 10.77 | 0.07 | -0.39 | -0.01
234 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 2.38 | -11.67 | -0.05 | 11.91 | 0.07 | 0.45 | 0.02
235 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 2.90 | 11.08 | -0.04 | 11.45 | 0.10 | -0.42 | -0.01
236 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 3.04 | -11.05 | -0.04 | 11.46 | 0.11 | 0.42 | 0.02
237 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 2.90 | 11.08 | -0.04 | 11.45 | 0.10 | -0.42 | -0.01
238 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 3.04 | -11.05 | -0.04 | 11.46 | 0.11 | 0.42 | 0.02
239 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 2.21 | 10.52 | -0.04 | 10.75 | 0.07 | -0.39 | -0.01
240 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 2.37 | -11.63 | -0.05 | 11.87 | 0.07 | 0.45 | 0.02
241 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 2.22 | 10.52 | -0.04 | 10.75 | 0.07 | -0.39 | -0.01
242 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 2.37 | -11.63 | -0.05 | 11.87 | 0.07 | 0.45 | 0.02
243 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 3.55 | 11.63 | -0.05 | 12.16 | 0.14 | -0.45 | -0.01
244 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 3.69 | -10.47 | -0.04 | 11.10 | 0.14 | 0.39 | 0.02
245 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 3.56 | 11.63 | -0.05 | 12.17 | 0.14 | -0.45 | -0.01
246 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 3.69 | -10.47 | -0.04 | 11.10 | 0.14 | 0.39 | 0.02
247 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -0.30 | 9.40 | -0.04 | 9.41 | -0.02 | -0.34 | -0.01
248 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | -0.21 | -10.54 | -0.04 | 10.54 | -0.02 | 0.41 | 0.01
249 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -0.30 | 9.40 | -0.04 | 9.41 | -0.02 | -0.34 | -0.01
250 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | -0.21 | -10.54 | -0.04 | 10.54 | -0.02 | 0.41 | 0.01
251 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 0.41 | 9.95 | -0.03 | 9.96 | 0.01 | -0.38 | -0.01
252 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 0.58 | -9.93 | -0.04 | 9.95 | 0.02 | 0.38 | 0.01
253 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 0.41 | 9.95 | -0.03 | 9.96 | 0.01 | -0.38 | -0.01
254 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 0.58 | -9.93 | -0.04 | 9.95 | 0.02 | 0.38 | 0.01
255 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -0.25 | 9.40 | -0.03 | 9.40 | -0.02 | -0.34 | -0.01
256 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | -0.17 | -10.50 | -0.04 | 10.50 | -0.02 | 0.41 | 0.01
257 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -0.25 | 9.40 | -0.03 | 9.40 | -0.02 | -0.34 | -0.01
258 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | -0.17 | -10.50 | -0.04 | 10.50 | -0.02 | 0.41 | 0.01
259 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 1.16 | 10.50 | -0.04 | 10.56 | 0.05 | -0.41 | -0.01
260 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 1.30 | -9.35 | -0.03 | 9.44 | 0.05 | 0.34 | 0.01
261 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 1.16 | 10.50 | -0.04 | 10.57 | 0.05 | -0.41 | -0.01
262 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 1.30 | -9.35 | -0.03 | 9.44 | 0.05 | 0.34 | 0.01
263 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | -0.13 | 9.55 | -0.03 | 9.55 | -0.01 | -0.35 | -0.01
264 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 0.05 | -10.34 | -0.04 | 10.34 | -0.01 | 0.40 | 0.01
265 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | -0.13 | 9.55 | -0.03 | 9.55 | -0.01 | -0.35 | -0.01
266 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 0.05 | -10.34 | -0.04 | 10.34 | -0.01 | 0.40 | 0.01
267 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -0.60 | -0.57 | -0.01 | 0.83 | -0.03 | 0.03 | 0.00
268 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -0.60 | -0.57 | -0.01 | 0.83 | -0.03 | 0.03 | 0.00
269 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.85 | 0.26 | -0.01 | 0.89 | -0.04 | 0.01 | -0.00
270 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.78 | -1.99 | -0.01 | 2.13 | -0.04 | 0.09 | 0.00
271 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.84 | 0.26 | -0.01 | 0.88 | -0.04 | 0.01 | -0.00
272 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.76 | -2.04 | -0.01 | 2.18 | -0.04 | 0.10 | 0.00
273 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.84 | 0.64 | -0.01 | 1.06 | -0.04 | -0.01 | -0.00
274 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.77 | -1.62 | -0.01 | 1.79 | -0.04 | 0.07 | 0.00
275 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -0.64 | 8.43 | -0.03 | 8.46 | -0.03 | -0.31 | -0.01
276 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -0.56 | -9.36 | -0.03 | 9.38 | -0.03 | 0.36 | 0.01
277 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 8.38 | 15.13 | -0.10 | 17.30 | 0.31 | -0.61 | -0.01
278 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 8.51 | -17.34 | -0.12 | 19.31 | 0.31 | 0.75 | 0.04
279 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 8.37 | 15.13 | -0.10 | 17.30 | 0.31 | -0.61 | -0.01
280 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 8.53 | -17.34 | -0.12 | 19.32 | 0.31 | 0.75 | 0.04
281 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 8.99 | 16.11 | -0.10 | 18.45 | 0.35 | -0.67 | -0.01
282 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 9.10 | -16.19 | -0.11 | 18.57 | 0.35 | 0.68 | 0.03
283 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 8.99 | 16.11 | -0.10 | 18.45 | 0.35 | -0.67 | -0.01
284 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 9.11 | -16.19 | -0.11 | 18.58 | 0.35 | 0.68 | 0.03
285 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 8.19 | 15.13 | -0.09 | 17.20 | 0.31 | -0.61 | -0.01
286 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 8.32 | -17.26 | -0.12 | 19.16 | 0.31 | 0.74 | 0.04
287 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 8.19 | 15.13 | -0.09 | 17.20 | 0.31 | -0.61 | -0.01
288 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 8.33 | -17.26 | -0.12 | 19.17 | 0.31 | 0.74 | 0.04
289 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 9.71 | 17.09 | -0.12 | 19.66 | 0.40 | -0.73 | -0.01
290 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 9.81 | -15.11 | -0.10 | 18.02 | 0.39 | 0.61 | 0.03
291 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 9.71 | 17.09 | -0.12 | 19.65 | 0.40 | -0.73 | -0.01
292 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 9.82 | -15.11 | -0.10 | 18.02 | 0.40 | 0.61 | 0.03
293 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | 0.88 | 13.16 | -0.06 | 13.19 | 0.02 | -0.52 | -0.01
294 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | 0.99 | -15.36 | -0.08 | 15.39 | 0.02 | 0.66 | 0.03
295 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | 0.87 | 13.16 | -0.06 | 13.19 | 0.02 | -0.52 | -0.01
296 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | 1.00 | -15.36 | -0.08 | 15.39 | 0.02 | 0.66 | 0.03
297 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 2.16 | 14.14 | -0.07 | 14.30 | 0.08 | -0.59 | -0.02
298 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 2.25 | -14.23 | -0.07 | 14.41 | 0.08 | 0.60 | 0.02
299 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 2.16 | 14.13 | -0.07 | 14.30 | 0.08 | -0.59 | -0.02
300 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 2.26 | -14.23 | -0.07 | 14.41 | 0.08 | 0.60 | 0.02
301 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | 0.93 | 13.16 | -0.06 | 13.19 | 0.02 | -0.53 | -0.01
302 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 1.03 | -15.28 | -0.08 | 15.32 | 0.02 | 0.66 | 0.03
303 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | 0.92 | 13.16 | -0.06 | 13.19 | 0.02 | -0.53 | -0.01
304 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | 1.05 | -15.28 | -0.08 | 15.32 | 0.02 | 0.66 | 0.03
305 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 3.28 | 15.11 | -0.07 | 15.46 | 0.14 | -0.65 | -0.02
306 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 3.34 | -13.17 | -0.06 | 13.59 | 0.14 | 0.53 | 0.02
307 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 3.27 | 15.11 | -0.07 | 15.46 | 0.14 | -0.65 | -0.02
308 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 3.36 | -13.17 | -0.06 | 13.59 | 0.14 | 0.53 | 0.02
309 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | 1.29 | 13.43 | -0.06 | 13.50 | 0.04 | -0.54 | -0.01
310 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 1.39 | -14.98 | -0.08 | 15.05 | 0.04 | 0.64 | 0.03
311 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | 1.28 | 13.43 | -0.06 | 13.50 | 0.04 | -0.54 | -0.02
312 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 1.40 | -14.98 | -0.08 | 15.05 | 0.04 | 0.64 | 0.03
313 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -1.34 | -1.07 | -0.01 | 1.72 | -0.07 | 0.07 | 0.00
314 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -1.34 | -1.07 | -0.01 | 1.72 | -0.07 | 0.07 | 0.00
315 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.99 | 0.06 | -0.01 | 1.99 | -0.10 | 0.03 | -0.00
316 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.93 | -3.22 | -0.02 | 3.75 | -0.10 | 0.17 | 0.00
317 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.00 | 0.05 | -0.01 | 2.00 | -0.11 | 0.03 | -0.00
318 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.97 | -3.32 | -0.02 | 3.86 | -0.11 | 0.17 | 0.00
319 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.96 | 0.69 | -0.01 | 2.08 | -0.10 | -0.01 | -0.00
320 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.93 | -2.59 | -0.02 | 3.23 | -0.10 | 0.13 | 0.00
321 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -1.26 | 12.02 | -0.05 | 12.09 | -0.07 | -0.48 | -0.02
322 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -1.17 | -13.81 | -0.07 | 13.86 | -0.07 | 0.60 | 0.02
323 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 5.66 | 15.38 | -0.09 | 16.38 | 0.21 | -0.62 | -0.01
324 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 6.12 | -17.40 | -0.11 | 18.44 | 0.22 | 0.75 | 0.03
325 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 6.04 | 15.38 | -0.09 | 16.52 | 0.22 | -0.62 | -0.01
326 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 6.31 | -17.40 | -0.11 | 18.51 | 0.23 | 0.75 | 0.03
327 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 6.37 | 16.19 | -0.09 | 17.40 | 0.25 | -0.67 | -0.01
328 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 6.78 | -16.41 | -0.10 | 17.76 | 0.26 | 0.69 | 0.03
329 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 6.72 | 16.19 | -0.10 | 17.53 | 0.26 | -0.67 | -0.01
330 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 6.96 | -16.41 | -0.10 | 17.83 | 0.27 | 0.69 | 0.03
331 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 5.56 | 15.37 | -0.09 | 16.34 | 0.20 | -0.62 | -0.01
332 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 6.00 | -17.32 | -0.11 | 18.33 | 0.22 | 0.74 | 0.03
333 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 5.93 | 15.37 | -0.09 | 16.47 | 0.22 | -0.62 | -0.01
334 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 6.19 | -17.32 | -0.11 | 18.39 | 0.23 | 0.74 | 0.03
335 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 7.11 | 17.02 | -0.10 | 18.44 | 0.29 | -0.73 | -0.02
336 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 7.50 | -15.51 | -0.09 | 17.22 | 0.30 | 0.63 | 0.03
337 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 7.45 | 17.02 | -0.11 | 18.58 | 0.30 | -0.73 | -0.02
338 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 7.67 | -15.51 | -0.09 | 17.30 | 0.31 | 0.63 | 0.03
339 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | 1.28 | 13.40 | -0.06 | 13.46 | 0.03 | -0.54 | -0.02
340 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | 1.95 | -15.41 | -0.08 | 15.54 | 0.06 | 0.66 | 0.03
341 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | 1.67 | 13.40 | -0.06 | 13.50 | 0.05 | -0.54 | -0.02
342 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | 2.14 | -15.41 | -0.08 | 15.56 | 0.06 | 0.66 | 0.03
343 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 2.34 | 14.22 | -0.07 | 14.41 | 0.09 | -0.59 | -0.02
344 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 2.95 | -14.45 | -0.07 | 14.75 | 0.11 | 0.60 | 0.02
345 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 2.70 | 14.22 | -0.07 | 14.47 | 0.10 | -0.59 | -0.02
346 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 3.12 | -14.45 | -0.07 | 14.78 | 0.12 | 0.60 | 0.02
347 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | 1.32 | 13.39 | -0.06 | 13.46 | 0.04 | -0.54 | -0.02
348 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 1.97 | -15.34 | -0.08 | 15.47 | 0.06 | 0.66 | 0.03
349 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | 1.69 | 13.39 | -0.06 | 13.50 | 0.05 | -0.54 | -0.02
350 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | 2.15 | -15.34 | -0.08 | 15.49 | 0.07 | 0.66 | 0.03
351 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 3.29 | 15.04 | -0.07 | 15.40 | 0.14 | -0.64 | -0.02
352 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 3.85 | -13.55 | -0.06 | 14.09 | 0.16 | 0.55 | 0.02
353 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 3.62 | 15.04 | -0.07 | 15.47 | 0.15 | -0.64 | -0.02
354 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 4.01 | -13.55 | -0.06 | 14.13 | 0.16 | 0.55 | 0.02
355 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | 1.62 | 13.63 | -0.06 | 13.72 | 0.05 | -0.55 | -0.02
356 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 2.25 | -15.09 | -0.08 | 15.26 | 0.07 | 0.64 | 0.03
357 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | 1.99 | 13.63 | -0.06 | 13.77 | 0.07 | -0.55 | -0.02
358 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 2.44 | -15.09 | -0.08 | 15.28 | 0.08 | 0.64 | 0.03
359 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | 0.35 | -1.01 | -0.01 | 1.07 | -0.00 | 0.06 | 0.00
360 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | 0.35 | -1.01 | -0.01 | 1.07 | -0.00 | 0.06 | 0.00
361 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | 0.90 | 0.17 | -0.01 | 0.92 | 0.01 | 0.02 | 0.00
362 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | 1.03 | -3.13 | -0.02 | 3.30 | 0.02 | 0.16 | 0.01
363 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | 0.95 | 0.16 | -0.01 | 0.97 | 0.02 | 0.02 | 0.00
364 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | 1.08 | -3.23 | -0.02 | 3.41 | 0.02 | 0.17 | 0.01
365 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | 0.91 | 0.75 | -0.01 | 1.18 | 0.01 | -0.01 | 0.00
366 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | 1.04 | -2.56 | -0.01 | 2.76 | 0.02 | 0.12 | 0.01
367 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -0.45 | 12.24 | -0.05 | 12.24 | -0.03 | -0.49 | -0.02
368 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | 0.01 | -13.88 | -0.07 | 13.88 | -0.02 | 0.60 | 0.02
369 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 4.08 | 16.26 | -0.09 | 16.77 | 0.15 | -0.67 | -0.02
370 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 4.62 | -17.51 | -0.11 | 18.11 | 0.17 | 0.74 | 0.03
371 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 4.89 | 16.26 | -0.09 | 16.98 | 0.18 | -0.67 | -0.01
372 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 5.03 | -17.52 | -0.11 | 18.22 | 0.18 | 0.74 | 0.03
373 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 4.54 | 16.71 | -0.09 | 17.31 | 0.18 | -0.70 | -0.02
374 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 5.04 | -16.94 | -0.10 | 17.68 | 0.19 | 0.71 | 0.03
375 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 5.30 | 16.71 | -0.10 | 17.53 | 0.21 | -0.70 | -0.02
376 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 5.43 | -16.94 | -0.10 | 17.79 | 0.21 | 0.71 | 0.03
377 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 4.03 | 16.25 | -0.09 | 16.75 | 0.15 | -0.67 | -0.02
378 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 4.55 | -17.44 | -0.10 | 18.02 | 0.17 | 0.74 | 0.03
379 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 4.81 | 16.25 | -0.09 | 16.95 | 0.18 | -0.67 | -0.02
380 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 4.95 | -17.44 | -0.10 | 18.13 | 0.18 | 0.74 | 0.03
381 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 5.03 | 17.16 | -0.10 | 17.88 | 0.20 | -0.73 | -0.02
382 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 5.51 | -16.44 | -0.09 | 17.34 | 0.22 | 0.68 | 0.03
383 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 5.77 | 17.16 | -0.10 | 18.11 | 0.23 | -0.73 | -0.02
384 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 5.89 | -16.44 | -0.09 | 17.46 | 0.23 | 0.68 | 0.03
385 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -1.86 | 14.17 | -0.07 | 14.29 | -0.08 | -0.58 | -0.02
386 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | -0.57 | -15.44 | -0.08 | 15.45 | -0.04 | 0.66 | 0.02
387 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -0.62 | 14.17 | -0.07 | 14.18 | -0.04 | -0.58 | -0.02
388 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | -0.27 | -15.44 | -0.08 | 15.44 | -0.03 | 0.66 | 0.02
389 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | -1.03 | 14.62 | -0.07 | 14.66 | -0.04 | -0.61 | -0.02
390 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 0.07 | -14.87 | -0.07 | 14.87 | -0.00 | 0.62 | 0.02
391 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | -0.11 | 14.62 | -0.07 | 14.62 | -0.01 | -0.61 | -0.02
392 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 0.46 | -14.87 | -0.07 | 14.88 | 0.01 | 0.62 | 0.02
393 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -1.72 | 14.16 | -0.07 | 14.27 | -0.08 | -0.58 | -0.02
394 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | -0.49 | -15.37 | -0.08 | 15.38 | -0.03 | 0.65 | 0.02
395 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -0.52 | 14.16 | -0.07 | 14.17 | -0.03 | -0.58 | -0.02
396 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | -0.18 | -15.37 | -0.08 | 15.37 | -0.02 | 0.65 | 0.02
397 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | -0.36 | 15.08 | -0.07 | 15.09 | -0.01 | -0.64 | -0.02
398 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 0.70 | -14.36 | -0.07 | 14.38 | 0.03 | 0.59 | 0.02
399 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 0.73 | 15.09 | -0.07 | 15.11 | 0.03 | -0.64 | -0.02
400 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 1.08 | -14.36 | -0.07 | 14.41 | 0.04 | 0.59 | 0.02
401 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | -1.52 | 14.29 | -0.07 | 14.37 | -0.07 | -0.59 | -0.02
402 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | -0.40 | -15.23 | -0.08 | 15.23 | -0.03 | 0.64 | 0.02
403 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | -0.37 | 14.29 | -0.07 | 14.30 | -0.02 | -0.59 | -0.02
404 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 0.00 | -15.23 | -0.08 | 15.23 | -0.01 | 0.64 | 0.02
405 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -1.34 | -0.76 | -0.01 | 1.54 | -0.07 | 0.05 | 0.00
406 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -1.34 | -0.76 | -0.01 | 1.54 | -0.07 | 0.05 | 0.00
407 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.65 | 0.54 | -0.01 | 2.71 | -0.12 | -0.00 | -0.00
408 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.95 | -2.74 | -0.02 | 3.36 | -0.10 | 0.14 | 0.00
409 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.14 | 0.56 | -0.01 | 2.21 | -0.10 | -0.00 | -0.00
410 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.94 | -2.82 | -0.02 | 3.42 | -0.10 | 0.14 | 0.00
411 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.66 | 0.96 | -0.01 | 2.83 | -0.12 | -0.03 | -0.00
412 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.96 | -2.33 | -0.01 | 3.04 | -0.10 | 0.11 | 0.00
413 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -2.99 | 12.94 | -0.06 | 13.29 | -0.13 | -0.53 | -0.02
414 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -1.82 | -13.98 | -0.07 | 14.10 | -0.08 | 0.59 | 0.02
415 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 1.35 | 10.58 | -0.04 | 10.66 | 0.04 | -0.39 | -0.01
416 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 0.94 | -11.78 | -0.05 | 11.82 | 0.02 | 0.46 | 0.02
417 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 1.53 | 10.58 | -0.04 | 10.69 | 0.05 | -0.39 | -0.01
418 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 1.22 | -11.78 | -0.05 | 11.85 | 0.03 | 0.46 | 0.02
419 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 2.07 | 11.12 | -0.04 | 11.31 | 0.07 | -0.42 | -0.01
420 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 1.68 | -11.17 | -0.04 | 11.29 | 0.06 | 0.42 | 0.02
421 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 2.25 | 11.12 | -0.04 | 11.34 | 0.08 | -0.42 | -0.01
422 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 1.95 | -11.17 | -0.04 | 11.33 | 0.07 | 0.42 | 0.02
423 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 1.36 | 10.57 | -0.04 | 10.66 | 0.04 | -0.39 | -0.01
424 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 0.97 | -11.74 | -0.05 | 11.78 | 0.02 | 0.46 | 0.02
425 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 1.54 | 10.57 | -0.04 | 10.68 | 0.05 | -0.39 | -0.01
426 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 1.24 | -11.74 | -0.05 | 11.80 | 0.03 | 0.46 | 0.02
427 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 2.75 | 11.67 | -0.05 | 11.99 | 0.11 | -0.45 | -0.01
428 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 2.37 | -10.59 | -0.04 | 10.85 | 0.09 | 0.39 | 0.02
429 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 2.92 | 11.67 | -0.05 | 12.03 | 0.11 | -0.45 | -0.01
430 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 2.62 | -10.59 | -0.04 | 10.91 | 0.10 | 0.39 | 0.02
431 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -0.08 | 9.39 | -0.04 | 9.39 | -0.01 | -0.34 | -0.01
432 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | -0.42 | -10.60 | -0.04 | 10.61 | -0.03 | 0.41 | 0.02
433 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | 0.09 | 9.39 | -0.04 | 9.39 | -0.01 | -0.34 | -0.01
434 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | -0.21 | -10.60 | -0.04 | 10.60 | -0.02 | 0.41 | 0.02
435 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 0.71 | 9.94 | -0.04 | 9.96 | 0.02 | -0.37 | -0.01
436 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 0.33 | -9.99 | -0.04 | 9.99 | 0.01 | 0.38 | 0.01
437 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 0.88 | 9.94 | -0.04 | 9.97 | 0.03 | -0.37 | -0.01
438 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 0.59 | -9.99 | -0.04 | 10.01 | 0.02 | 0.38 | 0.01
439 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -0.04 | 9.39 | -0.03 | 9.39 | -0.01 | -0.34 | -0.01
440 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | -0.37 | -10.56 | -0.04 | 10.56 | -0.03 | 0.41 | 0.02
441 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | 0.13 | 9.39 | -0.03 | 9.39 | -0.00 | -0.34 | -0.01
442 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | -0.16 | -10.56 | -0.04 | 10.56 | -0.02 | 0.41 | 0.02
443 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 1.43 | 10.48 | -0.04 | 10.58 | 0.06 | -0.41 | -0.01
444 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 1.05 | -9.42 | -0.03 | 9.48 | 0.04 | 0.35 | 0.01
445 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 1.59 | 10.48 | -0.04 | 10.60 | 0.06 | -0.41 | -0.01
446 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 1.30 | -9.42 | -0.03 | 9.51 | 0.05 | 0.35 | 0.01
447 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | 0.18 | 9.54 | -0.03 | 9.55 | -0.00 | -0.35 | -0.01
448 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | -0.21 | -10.39 | -0.04 | 10.40 | -0.02 | 0.40 | 0.01
449 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | 0.35 | 9.54 | -0.03 | 9.55 | 0.01 | -0.35 | -0.01
450 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 0.06 | -10.39 | -0.04 | 10.39 | -0.01 | 0.40 | 0.02
451 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -0.41 | -0.60 | -0.01 | 0.72 | -0.03 | 0.03 | 0.00
452 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -0.41 | -0.60 | -0.01 | 0.72 | -0.03 | 0.03 | 0.00
453 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.42 | 0.24 | -0.01 | 0.48 | -0.03 | 0.01 | 0.00
454 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.48 | -2.02 | -0.01 | 2.08 | -0.03 | 0.09 | 0.00
455 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.39 | 0.24 | -0.01 | 0.45 | -0.03 | 0.01 | 0.00
456 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.46 | -2.08 | -0.01 | 2.13 | -0.03 | 0.10 | 0.00
457 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.44 | 0.62 | -0.01 | 0.76 | -0.03 | -0.01 | 0.00
458 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.51 | -1.65 | -0.01 | 1.73 | -0.03 | 0.07 | 0.00
459 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | -0.41 | 8.43 | -0.03 | 8.44 | -0.02 | -0.31 | -0.01
460 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -0.70 | -9.42 | -0.04 | 9.44 | -0.04 | 0.37 | 0.01
461 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 1.91 | 15.87 | -0.08 | 15.99 | 0.06 | -0.64 | -0.02
462 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 1.13 | -17.74 | -0.10 | 17.77 | 0.02 | 0.76 | 0.03
463 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 2.32 | 15.87 | -0.08 | 16.04 | 0.07 | -0.64 | -0.02
464 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 1.75 | -17.74 | -0.10 | 17.82 | 0.05 | 0.76 | 0.03
465 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 2.93 | 16.67 | -0.09 | 16.93 | 0.11 | -0.69 | -0.02
466 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 2.20 | -16.77 | -0.09 | 16.91 | 0.08 | 0.70 | 0.03
467 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 3.30 | 16.67 | -0.09 | 17.00 | 0.13 | -0.69 | -0.02
468 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 2.77 | -16.77 | -0.09 | 17.00 | 0.10 | 0.70 | 0.03
469 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 1.93 | 15.86 | -0.08 | 15.98 | 0.06 | -0.64 | -0.02
470 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 1.17 | -17.66 | -0.10 | 17.70 | 0.03 | 0.76 | 0.03
471 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 2.33 | 15.86 | -0.08 | 16.03 | 0.08 | -0.64 | -0.02
472 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 1.77 | -17.66 | -0.10 | 17.75 | 0.05 | 0.76 | 0.03
473 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 3.84 | 17.48 | -0.10 | 17.90 | 0.16 | -0.75 | -0.02
474 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 3.14 | -15.88 | -0.08 | 16.18 | 0.13 | 0.65 | 0.02
475 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 4.20 | 17.48 | -0.10 | 17.98 | 0.17 | -0.75 | -0.02
476 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 3.68 | -15.88 | -0.08 | 16.30 | 0.15 | 0.65 | 0.02
477 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | 0.68 | 13.82 | -0.07 | 13.84 | 0.01 | -0.56 | -0.02
478 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | -0.08 | -15.69 | -0.08 | 15.69 | -0.02 | 0.67 | 0.02
479 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | 1.10 | 13.82 | -0.07 | 13.87 | 0.03 | -0.56 | -0.02
480 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | 0.55 | -15.69 | -0.08 | 15.70 | 0.00 | 0.67 | 0.02
481 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 1.79 | 14.63 | -0.07 | 14.74 | 0.07 | -0.61 | -0.02
482 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 1.08 | -14.74 | -0.07 | 14.78 | 0.04 | 0.62 | 0.02
483 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 2.17 | 14.63 | -0.07 | 14.79 | 0.08 | -0.61 | -0.02
484 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 1.66 | -14.74 | -0.07 | 14.83 | 0.06 | 0.62 | 0.02
485 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | 0.74 | 13.82 | -0.06 | 13.84 | 0.01 | -0.56 | -0.02
486 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 0.00 | -15.62 | -0.08 | 15.62 | -0.02 | 0.67 | 0.02
487 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | 1.14 | 13.82 | -0.06 | 13.87 | 0.03 | -0.56 | -0.02
488 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | 0.61 | -15.62 | -0.08 | 15.63 | 0.00 | 0.67 | 0.02
489 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 2.76 | 15.44 | -0.08 | 15.69 | 0.12 | -0.66 | -0.02
490 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 2.07 | -13.86 | -0.06 | 14.01 | 0.09 | 0.56 | 0.02
491 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 3.12 | 15.44 | -0.08 | 15.75 | 0.13 | -0.66 | -0.02
492 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 2.62 | -13.86 | -0.06 | 14.10 | 0.11 | 0.56 | 0.02
493 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | 1.05 | 14.05 | -0.07 | 14.09 | 0.03 | -0.57 | -0.02
494 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 0.32 | -15.37 | -0.08 | 15.37 | -0.00 | 0.66 | 0.02
495 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | 1.44 | 14.05 | -0.07 | 14.12 | 0.04 | -0.57 | -0.02
496 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 0.92 | -15.37 | -0.08 | 15.40 | 0.02 | 0.66 | 0.02
497 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -0.74 | -0.98 | -0.01 | 1.23 | -0.05 | 0.06 | 0.00
498 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -0.74 | -0.98 | -0.01 | 1.23 | -0.05 | 0.06 | 0.00
499 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.77 | 0.25 | -0.01 | 0.81 | -0.05 | 0.02 | 0.00
500 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.93 | -3.13 | -0.02 | 3.27 | -0.06 | 0.16 | 0.01
501 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.72 | 0.24 | -0.01 | 0.76 | -0.05 | 0.02 | 0.00
502 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.89 | -3.23 | -0.02 | 3.35 | -0.06 | 0.17 | 0.01
503 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.77 | 0.84 | -0.01 | 1.14 | -0.05 | -0.02 | -0.00
504 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.91 | -2.55 | -0.01 | 2.71 | -0.06 | 0.12 | 0.00
505 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:t | 0.08 | 12.63 | -0.06 | 12.63 | -0.01 | -0.51 | -0.02
506 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:t | -0.51 | -14.15 | -0.07 | 14.16 | -0.04 | 0.61 | 0.02
507 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | -0.62 | 15.98 | -0.09 | 15.99 | -0.03 | -0.66 | -0.01
508 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 1.17 | -18.29 | -0.11 | 18.33 | 0.04 | 0.81 | 0.02
509 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | -0.80 | 15.98 | -0.09 | 16.00 | -0.04 | -0.66 | -0.01
510 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 0.77 | -18.29 | -0.11 | 18.31 | 0.02 | 0.81 | 0.02
511 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | -0.26 | 16.85 | -0.09 | 16.85 | -0.00 | -0.72 | -0.02
512 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 1.89 | -17.20 | -0.09 | 17.30 | 0.07 | 0.74 | 0.02
513 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | -0.42 | 16.85 | -0.09 | 16.85 | -0.01 | -0.72 | -0.02
514 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 1.53 | -17.20 | -0.09 | 17.27 | 0.06 | 0.74 | 0.02
515 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | -0.55 | 15.97 | -0.08 | 15.98 | -0.03 | -0.66 | -0.01
516 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 1.18 | -18.20 | -0.11 | 18.24 | 0.04 | 0.80 | 0.02
517 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | -0.72 | 15.97 | -0.08 | 15.99 | -0.03 | -0.66 | -0.01
518 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 0.80 | -18.20 | -0.11 | 18.22 | 0.02 | 0.80 | 0.02
519 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 1.02 | 17.72 | -0.10 | 17.75 | 0.05 | -0.78 | -0.02
520 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 2.53 | -16.19 | -0.08 | 16.39 | 0.11 | 0.68 | 0.01
521 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 0.87 | 17.72 | -0.10 | 17.74 | 0.05 | -0.78 | -0.02
522 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 2.19 | -16.19 | -0.08 | 16.34 | 0.10 | 0.68 | 0.01
523 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -2.87 | 14.75 | -0.08 | 15.03 | -0.12 | -0.61 | -0.01
524 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | 0.20 | -17.03 | -0.10 | 17.04 | -0.00 | 0.75 | 0.01
525 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -3.05 | 14.76 | -0.08 | 15.07 | -0.12 | -0.61 | -0.02
526 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | -0.07 | -17.03 | -0.10 | 17.03 | -0.01 | 0.75 | 0.01
527 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | -1.77 | 15.62 | -0.08 | 15.72 | -0.06 | -0.67 | -0.02
528 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 0.75 | -15.96 | -0.08 | 15.98 | 0.03 | 0.69 | 0.01
529 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | -1.94 | 15.62 | -0.08 | 15.74 | -0.07 | -0.67 | -0.02
530 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 0.38 | -15.96 | -0.08 | 15.97 | 0.02 | 0.69 | 0.01
531 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -2.72 | 14.75 | -0.07 | 15.00 | -0.11 | -0.61 | -0.01
532 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 0.25 | -16.95 | -0.09 | 16.95 | 0.00 | 0.75 | 0.01
533 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -2.90 | 14.75 | -0.07 | 15.03 | -0.12 | -0.61 | -0.02
534 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | -0.02 | -16.95 | -0.09 | 16.95 | -0.01 | 0.75 | 0.01
535 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | -0.92 | 16.49 | -0.09 | 16.52 | -0.02 | -0.72 | -0.02
536 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 1.53 | -14.97 | -0.07 | 15.05 | 0.07 | 0.63 | 0.01
537 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | -1.08 | 16.49 | -0.09 | 16.53 | -0.03 | -0.72 | -0.02
538 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 1.43 | -14.97 | -0.07 | 15.04 | 0.06 | 0.63 | 0.01
539 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | -2.44 | 15.00 | -0.08 | 15.19 | -0.10 | -0.63 | -0.01
540 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 0.22 | -16.67 | -0.09 | 16.67 | 0.00 | 0.73 | 0.01
541 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | -2.62 | 15.00 | -0.08 | 15.22 | -0.10 | -0.63 | -0.02
542 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 0.17 | -16.67 | -0.09 | 16.67 | -0.00 | 0.73 | 0.01
543 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -1.24 | -1.05 | -0.01 | 1.62 | -0.06 | 0.07 | 0.00
544 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -1.24 | -1.05 | -0.01 | 1.62 | -0.06 | 0.07 | 0.00
545 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.98 | 0.17 | -0.02 | 2.98 | -0.13 | 0.02 | -0.00
546 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.72 | -3.16 | -0.02 | 3.59 | -0.08 | 0.16 | 0.00
547 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -3.05 | 0.17 | -0.02 | 3.06 | -0.14 | 0.02 | -0.00
548 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.74 | -3.23 | -0.02 | 3.67 | -0.09 | 0.17 | 0.00
549 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -2.98 | 0.65 | -0.02 | 3.05 | -0.13 | -0.01 | -0.00
550 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.72 | -2.68 | -0.02 | 3.19 | -0.08 | 0.13 | 0.00
551 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:t | -3.44 | 13.37 | -0.07 | 13.81 | -0.14 | -0.56 | -0.02
552 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:t | -0.52 | -15.23 | -0.08 | 15.24 | -0.03 | 0.67 | 0.01
553 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | 3.81 | 15.80 | -0.09 | 16.25 | 0.15 | -0.66 | -0.01
554 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | 4.83 | -17.23 | -0.10 | 17.89 | 0.19 | 0.75 | 0.02
555 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | 3.74 | 15.80 | -0.09 | 16.23 | 0.15 | -0.66 | -0.01
556 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | 4.65 | -17.23 | -0.10 | 17.85 | 0.18 | 0.75 | 0.02
557 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | 4.18 | 16.42 | -0.09 | 16.95 | 0.17 | -0.70 | -0.01
558 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | 5.12 | -16.42 | -0.09 | 17.20 | 0.20 | 0.71 | 0.02
559 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | 4.12 | 16.42 | -0.09 | 16.93 | 0.17 | -0.70 | -0.01
560 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | 4.96 | -16.43 | -0.09 | 17.16 | 0.20 | 0.71 | 0.02
561 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | 3.73 | 15.79 | -0.09 | 16.22 | 0.15 | -0.66 | -0.01
562 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | 4.72 | -17.15 | -0.10 | 17.78 | 0.18 | 0.75 | 0.02
563 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | 3.66 | 15.79 | -0.08 | 16.21 | 0.14 | -0.66 | -0.01
564 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | 4.54 | -17.15 | -0.10 | 17.74 | 0.17 | 0.75 | 0.02
565 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | 4.61 | 17.06 | -0.10 | 17.67 | 0.19 | -0.74 | -0.01
566 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | 5.50 | -15.70 | -0.09 | 16.64 | 0.22 | 0.66 | 0.02
567 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | 4.55 | 17.06 | -0.10 | 17.65 | 0.19 | -0.74 | -0.01
568 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | 5.34 | -15.70 | -0.09 | 16.58 | 0.22 | 0.66 | 0.02
569 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -0.06 | 14.74 | -0.07 | 14.74 | -0.01 | -0.61 | -0.01
570 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | 0.64 | -16.17 | -0.09 | 16.18 | 0.01 | 0.71 | 0.02
571 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -0.11 | 14.74 | -0.07 | 14.74 | -0.01 | -0.61 | -0.01
572 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | 0.46 | -16.17 | -0.09 | 16.17 | 0.01 | 0.71 | 0.02
573 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | 0.26 | 15.37 | -0.08 | 15.37 | 0.01 | -0.65 | -0.01
574 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | 1.24 | -15.37 | -0.08 | 15.42 | 0.04 | 0.66 | 0.01
575 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | 0.19 | 15.37 | -0.08 | 15.37 | 0.01 | -0.65 | -0.01
576 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | 1.07 | -15.37 | -0.08 | 15.41 | 0.04 | 0.66 | 0.01
577 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -0.01 | 14.74 | -0.07 | 14.74 | -0.01 | -0.61 | -0.01
578 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | 0.67 | -16.09 | -0.09 | 16.10 | 0.01 | 0.70 | 0.02
579 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -0.06 | 14.74 | -0.07 | 14.74 | -0.01 | -0.61 | -0.01
580 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | 0.49 | -16.09 | -0.09 | 16.10 | 0.01 | 0.70 | 0.02
581 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | 1.09 | 16.00 | -0.08 | 16.04 | 0.05 | -0.70 | -0.01
582 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | 1.78 | -14.66 | -0.07 | 14.77 | 0.07 | 0.62 | 0.01
583 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | 1.06 | 16.00 | -0.08 | 16.04 | 0.05 | -0.70 | -0.01
584 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | 1.61 | -14.66 | -0.07 | 14.75 | 0.07 | 0.62 | 0.01
585 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | 0.08 | 14.92 | -0.07 | 14.92 | -0.00 | -0.63 | -0.01
586 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | 0.84 | -15.89 | -0.08 | 15.91 | 0.02 | 0.69 | 0.02
587 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | 0.05 | 14.91 | -0.07 | 14.92 | -0.00 | -0.63 | -0.01
588 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | 0.66 | -15.89 | -0.08 | 15.90 | 0.02 | 0.69 | 0.02
589 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -0.99 | -0.81 | -0.01 | 1.28 | -0.05 | 0.05 | 0.00
590 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -0.99 | -0.81 | -0.01 | 1.28 | -0.05 | 0.05 | 0.00
591 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.75 | 0.46 | -0.01 | 1.81 | -0.09 | 0.00 | 0.00
592 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.49 | -2.71 | -0.02 | 3.09 | -0.08 | 0.14 | 0.00
593 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.71 | 0.47 | -0.01 | 1.77 | -0.09 | 0.00 | 0.00
594 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.44 | -2.78 | -0.02 | 3.13 | -0.08 | 0.14 | 0.00
595 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -1.84 | 0.87 | -0.01 | 2.03 | -0.09 | -0.02 | -0.00
596 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -1.58 | -2.31 | -0.01 | 2.80 | -0.08 | 0.11 | 0.00
597 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:t | -2.90 | 13.31 | -0.06 | 13.63 | -0.13 | -0.56 | -0.01
598 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:t | -1.96 | -14.47 | -0.07 | 14.60 | -0.09 | 0.63 | 0.01
599 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:t | -8.34 | 15.26 | -0.10 | 17.39 | -0.35 | -0.63 | -0.02
600 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:t | -7.40 | -17.04 | -0.11 | 18.58 | -0.32 | 0.75 | 0.01
601 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:t | -8.40 | 15.26 | -0.10 | 17.42 | -0.35 | -0.63 | -0.02
602 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:t | -7.54 | -17.04 | -0.11 | 18.64 | -0.32 | 0.75 | 0.01
603 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:t | -6.88 | 16.02 | -0.10 | 17.44 | -0.29 | -0.68 | -0.02
604 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:t | -6.03 | -16.08 | -0.09 | 17.17 | -0.26 | 0.69 | 0.01
605 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:t | -6.93 | 16.02 | -0.10 | 17.46 | -0.29 | -0.68 | -0.02
606 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:t | -6.16 | -16.08 | -0.09 | 17.22 | -0.26 | 0.69 | 0.01
607 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:t | -8.02 | 15.25 | -0.10 | 17.23 | -0.34 | -0.63 | -0.02
608 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:t | -7.11 | -16.96 | -0.11 | 18.39 | -0.31 | 0.74 | 0.01
609 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:t | -8.07 | 15.25 | -0.10 | 17.26 | -0.34 | -0.63 | -0.02
610 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:t | -7.24 | -16.96 | -0.11 | 18.44 | -0.31 | 0.74 | 0.01
611 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:t | -5.83 | 16.79 | -0.10 | 17.77 | -0.24 | -0.73 | -0.02
612 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:t | -5.03 | -15.20 | -0.08 | 16.02 | -0.21 | 0.64 | 0.01
613 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:t | -5.88 | 16.79 | -0.10 | 17.79 | -0.24 | -0.73 | -0.02
614 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:t | -5.16 | -15.20 | -0.08 | 16.06 | -0.21 | 0.64 | 0.01
615 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:t | -3.91 | 14.32 | -0.07 | 14.85 | -0.17 | -0.59 | -0.01
616 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:t | -3.02 | -16.10 | -0.09 | 16.38 | -0.14 | 0.71 | 0.01
617 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:t | -3.97 | 14.32 | -0.08 | 14.86 | -0.17 | -0.59 | -0.01
618 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:t | -3.16 | -16.10 | -0.09 | 16.41 | -0.14 | 0.71 | 0.01
619 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:t | -2.82 | 15.09 | -0.08 | 15.35 | -0.12 | -0.64 | -0.02
620 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:t | -2.01 | -15.15 | -0.08 | 15.29 | -0.09 | 0.65 | 0.01
621 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:t | -2.87 | 15.09 | -0.08 | 15.36 | -0.12 | -0.64 | -0.02
622 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:t | -2.14 | -15.15 | -0.08 | 15.30 | -0.10 | 0.65 | 0.01
623 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:t | -3.73 | 14.32 | -0.07 | 14.80 | -0.16 | -0.59 | -0.01
624 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:t | -2.87 | -16.02 | -0.09 | 16.28 | -0.13 | 0.70 | 0.01
625 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:t | -3.78 | 14.32 | -0.07 | 14.81 | -0.16 | -0.59 | -0.01
626 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:t | -3.00 | -16.02 | -0.09 | 16.30 | -0.14 | 0.70 | 0.01
627 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:t | -1.98 | 15.86 | -0.08 | 15.98 | -0.08 | -0.69 | -0.02
628 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:t | -1.23 | -14.28 | -0.07 | 14.33 | -0.05 | 0.60 | 0.01
629 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:t | -2.03 | 15.86 | -0.08 | 15.99 | -0.08 | -0.69 | -0.02
630 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:t | -1.35 | -14.28 | -0.07 | 14.34 | -0.06 | 0.60 | 0.01
631 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:t | -3.46 | 14.54 | -0.07 | 14.95 | -0.15 | -0.61 | -0.01
632 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:t | -2.62 | -15.78 | -0.08 | 15.99 | -0.12 | 0.69 | 0.01
633 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:t | -3.52 | 14.54 | -0.07 | 14.96 | -0.15 | -0.61 | -0.01
634 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:t | -2.75 | -15.78 | -0.08 | 16.01 | -0.13 | 0.69 | 0.01
635 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:t | -0.44 | -0.89 | -0.01 | 0.99 | -0.03 | 0.06 | 0.00
636 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:t | -0.44 | -0.89 | -0.01 | 0.99 | -0.03 | 0.06 | 0.00
637 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.51 | 0.30 | -0.01 | 0.59 | -0.03 | 0.01 | 0.00
638 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.48 | -2.83 | -0.01 | 2.87 | -0.03 | 0.15 | 0.00
639 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.67 | 0.30 | -0.01 | 0.73 | -0.04 | 0.01 | 0.00
640 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.43 | -2.90 | -0.02 | 2.93 | -0.03 | 0.15 | 0.00
641 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:t | -0.51 | 0.75 | -0.01 | 0.91 | -0.03 | -0.01 | -0.00
642 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:t | -0.48 | -2.38 | -0.01 | 2.43 | -0.03 | 0.12 | 0.00
643 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:t | -1.03 | 12.93 | -0.06 | 12.97 | -0.05 | -0.54 | -0.01
644 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:t | -0.57 | -14.39 | -0.07 | 14.40 | -0.03 | 0.63 | 0.01

## Tab_6
rowtext | str_no | structure_name | load_case | foundation_description | axial_force | shear_force | resultant_force | bending_moment | foundation_usage
1 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 129.57 | 30.18 | 133.04 | 513.26 | 0.00
2 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 130.88 | 29.86 | 134.25 | 540.80 | 0.00
3 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 129.57 | 30.18 | 133.04 | 513.26 | 0.00
4 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 130.88 | 29.86 | 134.25 | 540.80 | 0.00
5 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 95.73 | 30.18 | 100.38 | 526.38 | 0.00
6 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.09 | 29.86 | 101.58 | 522.77 | 0.00
7 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 95.73 | 30.18 | 100.38 | 526.38 | 0.00
8 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.09 | 29.86 | 101.58 | 522.77 | 0.00
9 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 108.16 | 30.18 | 112.29 | 512.55 | 0.00
10 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 109.47 | 29.86 | 113.47 | 539.05 | 0.00
11 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 108.16 | 30.18 | 112.29 | 512.55 | 0.00
12 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 109.47 | 29.86 | 113.47 | 539.05 | 0.00
13 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 83.10 | 30.19 | 88.42 | 540.19 | 0.00
14 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 84.50 | 29.86 | 89.62 | 506.52 | 0.00
15 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 83.10 | 30.19 | 88.42 | 540.19 | 0.00
16 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 84.50 | 29.86 | 89.62 | 506.51 | 0.00
17 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 129.37 | 26.75 | 132.11 | 451.17 | 0.00
18 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 130.92 | 26.43 | 133.56 | 478.86 | 0.00
19 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 129.37 | 26.75 | 132.11 | 451.17 | 0.00
20 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 130.92 | 26.43 | 133.56 | 478.86 | 0.00
21 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.61 | 26.76 | 99.28 | 464.52 | 0.00
22 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.21 | 26.44 | 100.74 | 461.25 | 0.00
23 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.61 | 26.76 | 99.28 | 464.52 | 0.00
24 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.21 | 26.44 | 100.74 | 461.25 | 0.00
25 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 107.96 | 26.75 | 111.23 | 450.61 | 0.00
26 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 109.51 | 26.44 | 112.66 | 477.25 | 0.00
27 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 107.96 | 26.75 | 111.23 | 450.61 | 0.00
28 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 109.51 | 26.44 | 112.66 | 477.25 | 0.00
29 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 83.06 | 26.76 | 87.26 | 478.42 | 0.00
30 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 84.70 | 26.44 | 88.74 | 445.27 | 0.00
31 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 83.06 | 26.76 | 87.26 | 478.41 | 0.00
32 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 84.70 | 26.44 | 88.74 | 445.27 | 0.00
33 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 104.48 | 26.75 | 107.85 | 454.56 | 0.00
34 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 106.04 | 26.44 | 109.28 | 472.71 | 0.00
35 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 104.48 | 26.75 | 107.85 | 454.56 | 0.00
36 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 106.04 | 26.44 | 109.28 | 472.71 | 0.00
37 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 130.04 | 0.18 | 130.04 | 15.31 | 0.00
38 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 130.04 | 0.18 | 130.04 | 15.31 | 0.00
39 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 134.06 | 3.12 | 134.10 | 30.29 | 0.00
40 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.18 | 2.89 | 134.21 | 76.22 | 0.00
41 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 134.10 | 3.14 | 134.14 | 30.46 | 0.00
42 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.21 | 2.87 | 134.24 | 77.71 | 0.00
43 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 134.07 | 3.08 | 134.10 | 40.26 | 0.00
44 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.18 | 2.93 | 134.22 | 66.36 | 0.00
45 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 116.28 | 24.03 | 118.74 | 407.89 | 0.00
46 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 117.60 | 23.77 | 119.98 | 430.34 | 0.00
47 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 129.51 | 29.78 | 132.89 | 505.07 | 0.00
48 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 130.84 | 29.72 | 134.17 | 538.07 | 0.00
49 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 129.51 | 29.78 | 132.89 | 505.07 | 0.00
50 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 130.84 | 29.72 | 134.17 | 538.07 | 0.00
51 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 95.73 | 29.78 | 100.26 | 518.18 | 0.00
52 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.09 | 29.73 | 101.54 | 520.03 | 0.00
53 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 95.73 | 29.78 | 100.26 | 518.18 | 0.00
54 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.09 | 29.73 | 101.54 | 520.03 | 0.00
55 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 108.10 | 29.78 | 112.13 | 504.38 | 0.00
56 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 109.43 | 29.72 | 113.39 | 536.32 | 0.00
57 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 108.10 | 29.78 | 112.13 | 504.38 | 0.00
58 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 109.43 | 29.72 | 113.39 | 536.31 | 0.00
59 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 83.17 | 29.78 | 88.34 | 531.98 | 0.00
60 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 84.55 | 29.73 | 89.62 | 503.77 | 0.00
61 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 83.17 | 29.78 | 88.34 | 531.98 | 0.00
62 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 84.55 | 29.73 | 89.62 | 503.77 | 0.00
63 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 129.31 | 26.43 | 131.98 | 444.72 | 0.00
64 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 130.87 | 26.38 | 133.50 | 477.63 | 0.00
65 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 129.31 | 26.43 | 131.98 | 444.72 | 0.00
66 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 130.87 | 26.38 | 133.50 | 477.63 | 0.00
67 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.61 | 26.44 | 99.20 | 458.09 | 0.00
68 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.21 | 26.38 | 100.72 | 460.03 | 0.00
69 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.61 | 26.44 | 99.20 | 458.09 | 0.00
70 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.21 | 26.38 | 100.72 | 460.03 | 0.00
71 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 107.90 | 26.44 | 111.09 | 444.18 | 0.00
72 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 109.46 | 26.38 | 112.59 | 476.02 | 0.00
73 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 107.90 | 26.43 | 111.09 | 444.18 | 0.00
74 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 109.46 | 26.38 | 112.59 | 476.02 | 0.00
75 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 83.12 | 26.44 | 87.23 | 471.99 | 0.00
76 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 84.76 | 26.38 | 88.77 | 444.07 | 0.00
77 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 83.12 | 26.44 | 87.23 | 471.99 | 0.00
78 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 84.76 | 26.38 | 88.77 | 444.07 | 0.00
79 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 104.43 | 26.44 | 107.72 | 448.13 | 0.00
80 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 106.00 | 26.38 | 109.23 | 471.48 | 0.00
81 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 104.43 | 26.44 | 107.72 | 448.13 | 0.00
82 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 106.00 | 26.38 | 109.23 | 471.48 | 0.00
83 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 129.93 | 0.12 | 129.93 | 16.63 | 0.00
84 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 129.93 | 0.12 | 129.93 | 16.63 | 0.00
85 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.92 | 2.98 | 133.96 | 27.86 | 0.00
86 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.04 | 2.96 | 134.08 | 77.65 | 0.00
87 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.96 | 3.00 | 133.99 | 28.04 | 0.00
88 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.08 | 2.94 | 134.11 | 79.08 | 0.00
89 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.92 | 2.94 | 133.96 | 37.69 | 0.00
90 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.05 | 3.00 | 134.08 | 67.87 | 0.00
91 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 116.23 | 23.75 | 118.63 | 402.07 | 0.00
92 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 117.56 | 23.70 | 119.93 | 428.80 | 0.00
93 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 128.28 | 25.84 | 130.85 | 424.79 | 0.00
94 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 129.54 | 25.05 | 131.94 | 442.12 | 0.00
95 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 128.27 | 25.84 | 130.85 | 424.81 | 0.00
96 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 129.54 | 25.05 | 131.94 | 442.13 | 0.00
97 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 95.73 | 25.84 | 99.15 | 438.66 | 0.00
98 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.08 | 25.06 | 100.27 | 424.87 | 0.00
99 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 95.73 | 25.84 | 99.15 | 438.67 | 0.00
100 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.08 | 25.06 | 100.27 | 424.87 | 0.00
101 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 106.87 | 25.84 | 109.95 | 424.28 | 0.00
102 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 108.13 | 25.05 | 110.99 | 440.59 | 0.00
103 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 106.86 | 25.84 | 109.94 | 424.30 | 0.00
104 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 108.13 | 25.05 | 110.99 | 440.60 | 0.00
105 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 84.41 | 25.84 | 88.28 | 453.05 | 0.00
106 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 85.86 | 25.06 | 89.44 | 409.13 | 0.00
107 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 84.41 | 25.84 | 88.28 | 453.05 | 0.00
108 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 85.86 | 25.06 | 89.44 | 409.13 | 0.00
109 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 128.04 | 23.47 | 130.17 | 384.30 | 0.00
110 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 129.53 | 22.70 | 131.50 | 401.61 | 0.00
111 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 128.03 | 23.47 | 130.17 | 384.32 | 0.00
112 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 129.53 | 22.70 | 131.50 | 401.61 | 0.00
113 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.60 | 23.48 | 98.44 | 398.24 | 0.00
114 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.20 | 22.70 | 99.82 | 384.71 | 0.00
115 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.60 | 23.48 | 98.44 | 398.24 | 0.00
116 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.20 | 22.70 | 99.82 | 384.72 | 0.00
117 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 106.63 | 23.47 | 109.18 | 383.91 | 0.00
118 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 108.12 | 22.70 | 110.48 | 400.19 | 0.00
119 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 106.62 | 23.47 | 109.18 | 383.92 | 0.00
120 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 108.12 | 22.70 | 110.48 | 400.19 | 0.00
121 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 84.40 | 23.48 | 87.61 | 412.59 | 0.00
122 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 86.11 | 22.70 | 89.05 | 369.23 | 0.00
123 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 84.41 | 23.48 | 87.61 | 412.59 | 0.00
124 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 86.11 | 22.70 | 89.05 | 369.23 | 0.00
125 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 103.52 | 23.47 | 106.14 | 387.97 | 0.00
126 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 105.04 | 22.70 | 107.46 | 395.80 | 0.00
127 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 103.51 | 23.47 | 106.14 | 387.98 | 0.00
128 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 105.04 | 22.70 | 107.46 | 395.80 | 0.00
129 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 128.02 | 0.22 | 128.02 | 11.81 | 0.00
130 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 128.02 | 0.22 | 128.02 | 11.81 | 0.00
131 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 131.44 | 2.79 | 131.47 | 26.10 | 0.00
132 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 131.54 | 2.14 | 131.56 | 58.20 | 0.00
133 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 131.46 | 2.81 | 131.50 | 26.64 | 0.00
134 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 131.56 | 2.11 | 131.58 | 58.89 | 0.00
135 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 131.34 | 2.66 | 131.37 | 32.56 | 0.00
136 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 131.45 | 2.26 | 131.47 | 51.75 | 0.00
137 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 115.25 | 20.95 | 117.14 | 345.09 | 0.00
138 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 116.52 | 20.31 | 118.28 | 359.08 | 0.00
139 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 128.20 | 26.48 | 130.91 | 438.47 | 0.00
140 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 129.56 | 30.38 | 133.08 | 550.12 | 0.00
141 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 128.20 | 26.48 | 130.91 | 438.50 | 0.00
142 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 129.56 | 30.37 | 133.08 | 550.02 | 0.00
143 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 95.73 | 26.48 | 99.32 | 451.42 | 0.00
144 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.08 | 30.38 | 101.72 | 533.00 | 0.00
145 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 95.73 | 26.48 | 99.32 | 451.45 | 0.00
146 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.08 | 30.37 | 101.72 | 532.90 | 0.00
147 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 106.79 | 26.48 | 110.02 | 437.95 | 0.00
148 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 108.15 | 30.38 | 112.34 | 548.34 | 0.00
149 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 106.79 | 26.48 | 110.02 | 437.98 | 0.00
150 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 108.15 | 30.37 | 112.34 | 548.23 | 0.00
151 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 84.49 | 26.49 | 88.54 | 464.91 | 0.00
152 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 85.82 | 30.38 | 91.04 | 517.65 | 0.00
153 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 84.49 | 26.49 | 88.54 | 464.94 | 0.00
154 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 85.82 | 30.38 | 91.04 | 517.55 | 0.00
155 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 128.01 | 23.55 | 130.16 | 386.52 | 0.00
156 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 129.63 | 27.32 | 132.48 | 495.56 | 0.00
157 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 128.01 | 23.55 | 130.16 | 386.57 | 0.00
158 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 129.63 | 27.31 | 132.47 | 495.47 | 0.00
159 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.60 | 23.55 | 98.46 | 399.61 | 0.00
160 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.19 | 27.32 | 100.96 | 478.80 | 0.00
161 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.60 | 23.55 | 98.46 | 399.65 | 0.00
162 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.19 | 27.32 | 100.96 | 478.71 | 0.00
163 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 106.60 | 23.55 | 109.17 | 386.12 | 0.00
164 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 108.22 | 27.32 | 111.61 | 493.91 | 0.00
165 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 106.60 | 23.55 | 109.17 | 386.16 | 0.00
166 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 108.22 | 27.31 | 111.61 | 493.83 | 0.00
167 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 84.43 | 23.56 | 87.65 | 413.12 | 0.00
168 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 85.99 | 27.32 | 90.23 | 463.68 | 0.00
169 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 84.43 | 23.56 | 87.65 | 413.17 | 0.00
170 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 85.99 | 27.32 | 90.23 | 463.59 | 0.00
171 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 103.50 | 23.55 | 106.14 | 389.94 | 0.00
172 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 105.11 | 27.32 | 108.60 | 489.63 | 0.00
173 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 103.50 | 23.55 | 106.14 | 389.99 | 0.00
174 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 105.11 | 27.31 | 108.60 | 489.54 | 0.00
175 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 128.81 | 1.04 | 128.81 | 37.22 | 0.00
176 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 128.81 | 1.04 | 128.81 | 37.22 | 0.00
177 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 132.42 | 1.26 | 132.42 | 6.26 | 0.00
178 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 132.56 | 4.39 | 132.63 | 104.86 | 0.00
179 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 132.46 | 1.29 | 132.47 | 6.45 | 0.00
180 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 132.60 | 4.36 | 132.67 | 106.58 | 0.00
181 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 132.37 | 1.18 | 132.38 | 2.73 | 0.00
182 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 132.52 | 4.47 | 132.60 | 96.94 | 0.00
183 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 115.19 | 21.23 | 117.12 | 351.36 | 0.00
184 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 116.57 | 24.35 | 119.09 | 441.12 | 0.00
185 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 128.51 | 30.12 | 132.00 | 513.33 | 0.00
186 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 129.84 | 29.88 | 133.24 | 540.16 | 0.00
187 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 128.51 | 30.12 | 132.00 | 513.33 | 0.00
188 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 129.84 | 29.88 | 133.24 | 540.16 | 0.00
189 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 95.72 | 30.13 | 100.35 | 525.39 | 0.00
190 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.08 | 29.88 | 101.57 | 523.44 | 0.00
191 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 95.72 | 30.13 | 100.35 | 525.39 | 0.00
192 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.08 | 29.88 | 101.57 | 523.44 | 0.00
193 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 107.10 | 30.12 | 111.26 | 512.60 | 0.00
194 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 108.43 | 29.88 | 112.47 | 538.38 | 0.00
195 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 107.10 | 30.12 | 111.26 | 512.60 | 0.00
196 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 108.43 | 29.88 | 112.47 | 538.38 | 0.00
197 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 84.16 | 30.13 | 89.39 | 538.17 | 0.00
198 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 85.54 | 29.89 | 90.61 | 508.49 | 0.00
199 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 84.16 | 30.13 | 89.39 | 538.17 | 0.00
200 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 85.54 | 29.89 | 90.61 | 508.49 | 0.00
201 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 128.36 | 26.74 | 131.11 | 451.87 | 0.00
202 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 129.92 | 26.49 | 132.60 | 478.84 | 0.00
203 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 128.36 | 26.74 | 131.11 | 451.87 | 0.00
204 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 129.92 | 26.49 | 132.60 | 478.84 | 0.00
205 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.60 | 26.74 | 99.27 | 464.18 | 0.00
206 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.20 | 26.50 | 100.75 | 462.46 | 0.00
207 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.60 | 26.74 | 99.27 | 464.18 | 0.00
208 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.20 | 26.50 | 100.75 | 462.46 | 0.00
209 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 106.95 | 26.74 | 110.24 | 451.31 | 0.00
210 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 108.51 | 26.49 | 111.70 | 477.24 | 0.00
211 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 106.95 | 26.74 | 110.24 | 451.31 | 0.00
212 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 108.51 | 26.49 | 111.70 | 477.24 | 0.00
213 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 84.07 | 26.74 | 88.22 | 477.05 | 0.00
214 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 85.70 | 26.50 | 89.71 | 447.69 | 0.00
215 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 84.07 | 26.74 | 88.22 | 477.05 | 0.00
216 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 85.70 | 26.50 | 89.71 | 447.69 | 0.00
217 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 103.74 | 26.74 | 107.13 | 454.96 | 0.00
218 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 105.32 | 26.49 | 108.60 | 473.04 | 0.00
219 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 103.74 | 26.74 | 107.13 | 454.96 | 0.00
220 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 105.32 | 26.49 | 108.60 | 473.04 | 0.00
221 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 129.29 | 0.17 | 129.29 | 14.75 | 0.00
222 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 129.29 | 0.17 | 129.29 | 14.75 | 0.00
223 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.05 | 3.06 | 133.09 | 30.39 | 0.00
224 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 133.17 | 2.88 | 133.20 | 74.62 | 0.00
225 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.10 | 3.08 | 133.14 | 30.50 | 0.00
226 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 133.22 | 2.87 | 133.25 | 76.20 | 0.00
227 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.06 | 3.02 | 133.09 | 39.67 | 0.00
228 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 133.18 | 2.92 | 133.21 | 65.49 | 0.00
229 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 115.45 | 24.04 | 117.93 | 408.84 | 0.00
230 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 116.78 | 23.84 | 119.19 | 430.69 | 0.00
231 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 204.72 | 34.16 | 207.55 | 615.08 | 0.00
232 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 206.02 | 33.85 | 208.79 | 647.35 | 0.00
233 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 204.72 | 34.16 | 207.55 | 615.08 | 0.00
234 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 206.02 | 33.85 | 208.79 | 647.35 | 0.00
235 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 155.57 | 34.16 | 159.28 | 631.04 | 0.00
236 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 156.92 | 33.85 | 160.53 | 627.42 | 0.00
237 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 155.57 | 34.16 | 159.28 | 631.04 | 0.00
238 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 156.92 | 33.85 | 160.53 | 627.42 | 0.00
239 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 170.02 | 34.16 | 173.42 | 614.29 | 0.00
240 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 171.32 | 33.85 | 174.64 | 645.51 | 0.00
241 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 170.02 | 34.16 | 173.42 | 614.29 | 0.00
242 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 171.32 | 33.85 | 174.64 | 645.51 | 0.00
243 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 140.89 | 34.16 | 144.97 | 647.84 | 0.00
244 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 142.29 | 33.85 | 146.26 | 609.31 | 0.00
245 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 140.89 | 34.16 | 144.97 | 647.84 | 0.00
246 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 142.29 | 33.85 | 146.26 | 609.30 | 0.00
247 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 204.48 | 30.99 | 206.81 | 554.00 | 0.00
248 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 206.04 | 30.68 | 208.31 | 586.27 | 0.00
249 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 204.48 | 30.99 | 206.81 | 554.00 | 0.00
250 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 206.04 | 30.68 | 208.31 | 586.27 | 0.00
251 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 155.43 | 30.99 | 158.49 | 570.02 | 0.00
252 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 157.05 | 30.69 | 160.02 | 566.62 | 0.00
253 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 155.43 | 30.99 | 158.49 | 570.02 | 0.00
254 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 157.05 | 30.69 | 160.02 | 566.62 | 0.00
255 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 169.78 | 30.99 | 172.58 | 553.35 | 0.00
256 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 171.34 | 30.68 | 174.06 | 584.56 | 0.00
257 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 169.78 | 30.99 | 172.58 | 553.34 | 0.00
258 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 171.34 | 30.68 | 174.06 | 584.56 | 0.00
259 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 140.86 | 31.00 | 144.23 | 586.76 | 0.00
260 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 142.54 | 30.69 | 145.80 | 548.66 | 0.00
261 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 140.86 | 31.00 | 144.23 | 586.76 | 0.00
262 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 142.54 | 30.69 | 145.80 | 548.66 | 0.00
263 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 165.73 | 30.99 | 168.60 | 558.07 | 0.00
264 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 167.30 | 30.68 | 170.09 | 579.47 | 0.00
265 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 165.73 | 30.99 | 168.60 | 558.07 | 0.00
266 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 167.30 | 30.68 | 170.09 | 579.47 | 0.00
267 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 204.61 | 0.21 | 204.61 | 16.62 | 0.00
268 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 204.61 | 0.21 | 204.61 | 16.62 | 0.00
269 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 209.16 | 3.51 | 209.19 | 38.34 | 0.00
270 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 209.28 | 3.28 | 209.30 | 89.30 | 0.00
271 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 209.16 | 3.52 | 209.19 | 38.42 | 0.00
272 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 209.27 | 3.27 | 209.30 | 90.87 | 0.00
273 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 209.15 | 3.47 | 209.18 | 49.56 | 0.00
274 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 209.26 | 3.32 | 209.29 | 78.18 | 0.00
275 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 184.38 | 27.35 | 186.40 | 492.08 | 0.00
276 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 185.70 | 27.10 | 187.66 | 518.28 | 0.00
277 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 131.80 | 29.48 | 135.05 | 496.52 | 0.00
278 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 133.13 | 29.33 | 136.32 | 533.13 | 0.00
279 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 131.80 | 29.48 | 135.05 | 496.52 | 0.00
280 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 133.13 | 29.33 | 136.32 | 533.14 | 0.00
281 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 96.05 | 29.48 | 100.47 | 512.23 | 0.00
282 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.40 | 29.33 | 101.72 | 512.41 | 0.00
283 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 96.05 | 29.48 | 100.47 | 512.22 | 0.00
284 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.40 | 29.33 | 101.72 | 512.41 | 0.00
285 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 110.32 | 29.48 | 114.19 | 495.90 | 0.00
286 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 111.65 | 29.33 | 115.44 | 531.27 | 0.00
287 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 110.32 | 29.48 | 114.19 | 495.90 | 0.00
288 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 111.65 | 29.33 | 115.44 | 531.28 | 0.00
289 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 81.54 | 29.49 | 86.71 | 528.46 | 0.00
290 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 82.92 | 29.34 | 87.95 | 493.62 | 0.00
291 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 81.54 | 29.49 | 86.71 | 528.45 | 0.00
292 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 82.92 | 29.34 | 87.95 | 493.62 | 0.00
293 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 131.51 | 26.10 | 134.08 | 435.35 | 0.00
294 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 133.08 | 25.95 | 135.58 | 471.76 | 0.00
295 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 131.51 | 26.10 | 134.08 | 435.35 | 0.00
296 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 133.08 | 25.95 | 135.58 | 471.76 | 0.00
297 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.92 | 26.11 | 99.41 | 451.24 | 0.00
298 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.52 | 25.96 | 100.91 | 451.56 | 0.00
299 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.92 | 26.11 | 99.41 | 451.24 | 0.00
300 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.52 | 25.96 | 100.91 | 451.56 | 0.00
301 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 110.03 | 26.10 | 113.09 | 434.91 | 0.00
302 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 111.60 | 25.95 | 114.58 | 470.08 | 0.00
303 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 110.03 | 26.10 | 113.09 | 434.91 | 0.00
304 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 111.60 | 25.95 | 114.58 | 470.08 | 0.00
305 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 81.58 | 26.12 | 85.66 | 467.51 | 0.00
306 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 83.21 | 25.96 | 87.16 | 433.13 | 0.00
307 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 81.58 | 26.12 | 85.66 | 467.50 | 0.00
308 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 83.21 | 25.96 | 87.16 | 433.12 | 0.00
309 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 106.05 | 26.11 | 109.22 | 439.55 | 0.00
310 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 107.63 | 25.95 | 110.71 | 464.81 | 0.00
311 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 106.05 | 26.11 | 109.22 | 439.55 | 0.00
312 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 107.63 | 25.95 | 110.71 | 464.81 | 0.00
313 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 131.48 | 0.16 | 131.48 | 17.87 | 0.00
314 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 131.48 | 0.16 | 131.48 | 17.87 | 0.00
315 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 135.87 | 3.00 | 135.90 | 25.62 | 0.00
316 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 135.99 | 2.87 | 136.02 | 78.36 | 0.00
317 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 135.95 | 3.03 | 135.99 | 25.59 | 0.00
318 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 136.07 | 2.84 | 136.10 | 79.98 | 0.00
319 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 135.88 | 2.93 | 135.92 | 35.63 | 0.00
320 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 136.01 | 2.95 | 136.04 | 68.39 | 0.00
321 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 118.07 | 23.45 | 120.38 | 393.92 | 0.00
322 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 119.41 | 23.33 | 121.67 | 423.57 | 0.00
323 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 129.52 | 29.61 | 132.86 | 501.46 | 0.00
324 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 130.85 | 29.62 | 134.16 | 536.36 | 0.00
325 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 129.52 | 29.61 | 132.86 | 501.52 | 0.00
326 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 130.85 | 29.63 | 134.16 | 536.38 | 0.00
327 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 96.03 | 29.61 | 100.49 | 514.53 | 0.00
328 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.38 | 29.63 | 101.79 | 518.58 | 0.00
329 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 96.03 | 29.62 | 100.49 | 514.58 | 0.00
330 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.38 | 29.63 | 101.79 | 518.61 | 0.00
331 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 108.04 | 29.61 | 112.03 | 500.84 | 0.00
332 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 109.37 | 29.62 | 113.31 | 534.51 | 0.00
333 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 108.04 | 29.61 | 112.03 | 500.89 | 0.00
334 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 109.37 | 29.63 | 113.31 | 534.53 | 0.00
335 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 83.82 | 29.62 | 88.90 | 528.20 | 0.00
336 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 85.19 | 29.63 | 90.20 | 502.66 | 0.00
337 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 83.82 | 29.62 | 88.90 | 528.25 | 0.00
338 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 85.20 | 29.63 | 90.20 | 502.69 | 0.00
339 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 129.33 | 26.25 | 131.97 | 440.60 | 0.00
340 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 130.89 | 26.25 | 133.50 | 475.33 | 0.00
341 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 129.33 | 26.25 | 131.96 | 440.63 | 0.00
342 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 130.89 | 26.25 | 133.50 | 475.34 | 0.00
343 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.90 | 26.25 | 99.43 | 453.89 | 0.00
344 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.50 | 26.26 | 100.97 | 457.96 | 0.00
345 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.90 | 26.25 | 99.43 | 453.92 | 0.00
346 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.50 | 26.26 | 100.97 | 457.98 | 0.00
347 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 107.85 | 26.25 | 111.00 | 440.14 | 0.00
348 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 109.42 | 26.25 | 112.52 | 473.64 | 0.00
349 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 107.85 | 26.25 | 111.00 | 440.17 | 0.00
350 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 109.41 | 26.25 | 112.52 | 473.66 | 0.00
351 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 83.77 | 26.26 | 87.78 | 467.62 | 0.00
352 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 85.39 | 26.26 | 89.34 | 442.30 | 0.00
353 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 83.77 | 26.26 | 87.79 | 467.65 | 0.00
354 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 85.39 | 26.26 | 89.34 | 442.32 | 0.00
355 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 104.48 | 26.25 | 107.73 | 444.04 | 0.00
356 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 106.05 | 26.25 | 109.25 | 469.19 | 0.00
357 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 104.48 | 26.25 | 107.72 | 444.07 | 0.00
358 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 106.05 | 26.25 | 109.25 | 469.21 | 0.00
359 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 130.03 | 0.25 | 130.03 | 17.28 | 0.00
360 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 130.03 | 0.25 | 130.03 | 17.28 | 0.00
361 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.93 | 2.96 | 133.96 | 27.14 | 0.00
362 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.05 | 2.98 | 134.08 | 77.83 | 0.00
363 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.97 | 2.98 | 134.00 | 27.16 | 0.00
364 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.09 | 2.97 | 134.12 | 79.45 | 0.00
365 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.92 | 2.92 | 133.95 | 36.58 | 0.00
366 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.04 | 3.03 | 134.08 | 68.43 | 0.00
367 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 116.28 | 23.60 | 118.65 | 398.78 | 0.00
368 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 117.61 | 23.60 | 119.96 | 427.04 | 0.00
369 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 124.32 | 30.36 | 127.97 | 522.99 | 0.00
370 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 125.67 | 30.41 | 129.30 | 544.91 | 0.00
371 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 124.34 | 30.37 | 128.00 | 523.08 | 0.00
372 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 125.68 | 30.41 | 129.31 | 544.98 | 0.00
373 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 95.98 | 30.37 | 100.67 | 529.79 | 0.00
374 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.34 | 30.41 | 101.98 | 534.33 | 0.00
375 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 95.98 | 30.37 | 100.67 | 529.90 | 0.00
376 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.34 | 30.41 | 101.98 | 534.38 | 0.00
377 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 102.84 | 30.36 | 107.23 | 522.31 | 0.00
378 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 104.19 | 30.41 | 108.54 | 543.07 | 0.00
379 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 102.86 | 30.37 | 107.25 | 522.40 | 0.00
380 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 104.21 | 30.41 | 108.55 | 543.13 | 0.00
381 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 89.02 | 30.37 | 94.06 | 537.30 | 0.00
382 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 90.37 | 30.41 | 95.35 | 525.53 | 0.00
383 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 88.99 | 30.37 | 94.04 | 537.45 | 0.00
384 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 90.36 | 30.41 | 95.34 | 525.57 | 0.00
385 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 124.33 | 26.84 | 127.19 | 458.86 | 0.00
386 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 125.94 | 26.88 | 128.78 | 481.03 | 0.00
387 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 124.36 | 26.84 | 127.22 | 458.87 | 0.00
388 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 125.96 | 26.88 | 128.80 | 481.08 | 0.00
389 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.86 | 26.84 | 99.55 | 465.94 | 0.00
390 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.46 | 26.88 | 101.10 | 470.55 | 0.00
391 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.86 | 26.85 | 99.55 | 466.01 | 0.00
392 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.46 | 26.88 | 101.10 | 470.59 | 0.00
393 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 102.85 | 26.84 | 106.30 | 458.34 | 0.00
394 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 104.47 | 26.88 | 107.87 | 479.34 | 0.00
395 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 102.88 | 26.84 | 106.33 | 458.36 | 0.00
396 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 104.48 | 26.88 | 107.89 | 479.39 | 0.00
397 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 88.76 | 26.85 | 92.73 | 473.60 | 0.00
398 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 90.34 | 26.88 | 94.25 | 461.71 | 0.00
399 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 88.73 | 26.85 | 92.71 | 473.71 | 0.00
400 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 90.32 | 26.88 | 94.24 | 461.73 | 0.00
401 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 100.88 | 26.84 | 104.39 | 460.49 | 0.00
402 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 102.49 | 26.88 | 105.96 | 476.85 | 0.00
403 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 100.90 | 26.85 | 104.41 | 460.53 | 0.00
404 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 102.50 | 26.88 | 105.97 | 476.90 | 0.00
405 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 126.72 | 0.08 | 126.72 | 13.09 | 0.00
406 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 126.72 | 0.08 | 126.72 | 13.09 | 0.00
407 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 129.48 | 2.91 | 129.51 | 33.41 | 0.00
408 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 129.61 | 2.97 | 129.64 | 71.11 | 0.00
409 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 129.49 | 2.92 | 129.52 | 33.49 | 0.00
410 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 129.62 | 2.95 | 129.66 | 72.29 | 0.00
411 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 129.49 | 2.88 | 129.53 | 40.13 | 0.00
412 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 129.63 | 3.01 | 129.67 | 64.43 | 0.00
413 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 112.17 | 24.20 | 114.75 | 416.10 | 0.00
414 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 113.55 | 24.23 | 116.11 | 434.10 | 0.00
415 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 205.03 | 34.28 | 207.87 | 617.54 | 0.00
416 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 206.34 | 34.08 | 209.13 | 652.90 | 0.00
417 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 205.02 | 34.28 | 207.87 | 617.56 | 0.00
418 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 206.33 | 34.09 | 209.13 | 652.92 | 0.00
419 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 155.87 | 34.28 | 159.59 | 633.39 | 0.00
420 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 157.22 | 34.09 | 160.87 | 633.00 | 0.00
421 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 155.87 | 34.28 | 159.59 | 633.41 | 0.00
422 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 157.22 | 34.09 | 160.87 | 633.03 | 0.00
423 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 170.26 | 34.28 | 173.68 | 616.82 | 0.00
424 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 171.57 | 34.08 | 174.92 | 650.97 | 0.00
425 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 170.26 | 34.28 | 173.67 | 616.84 | 0.00
426 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 171.57 | 34.09 | 174.92 | 650.98 | 0.00
427 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 141.24 | 34.29 | 145.34 | 650.00 | 0.00
428 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 142.63 | 34.09 | 146.65 | 615.00 | 0.00
429 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 141.25 | 34.29 | 145.35 | 650.02 | 0.00
430 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 142.64 | 34.09 | 146.66 | 615.05 | 0.00
431 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 204.79 | 30.99 | 207.12 | 553.71 | 0.00
432 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 206.35 | 30.79 | 208.64 | 589.04 | 0.00
433 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 204.78 | 30.99 | 207.11 | 553.71 | 0.00
434 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 206.35 | 30.79 | 208.63 | 589.04 | 0.00
435 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 155.73 | 30.99 | 158.78 | 569.66 | 0.00
436 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 157.35 | 30.79 | 160.33 | 569.45 | 0.00
437 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 155.73 | 30.99 | 158.78 | 569.66 | 0.00
438 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 157.35 | 30.79 | 160.33 | 569.46 | 0.00
439 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 170.02 | 30.99 | 172.82 | 553.13 | 0.00
440 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 171.59 | 30.79 | 174.33 | 587.25 | 0.00
441 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 170.02 | 30.99 | 172.82 | 553.13 | 0.00
442 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 171.58 | 30.79 | 174.32 | 587.24 | 0.00
443 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 141.21 | 30.99 | 144.58 | 586.25 | 0.00
444 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 142.88 | 30.80 | 146.16 | 551.63 | 0.00
445 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 141.22 | 30.99 | 144.58 | 586.25 | 0.00
446 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 142.88 | 30.80 | 146.17 | 551.66 | 0.00
447 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 165.99 | 30.99 | 168.85 | 557.81 | 0.00
448 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 167.57 | 30.79 | 170.37 | 582.20 | 0.00
449 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 165.98 | 30.99 | 168.85 | 557.82 | 0.00
450 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 167.57 | 30.79 | 170.37 | 582.20 | 0.00
451 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 204.98 | 0.19 | 204.98 | 17.60 | 0.00
452 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 204.98 | 0.19 | 204.98 | 17.60 | 0.00
453 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 209.52 | 3.48 | 209.55 | 37.35 | 0.00
454 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 209.64 | 3.34 | 209.66 | 90.95 | 0.00
455 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 209.54 | 3.50 | 209.57 | 37.30 | 0.00
456 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 209.66 | 3.33 | 209.68 | 92.70 | 0.00
457 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 209.52 | 3.45 | 209.55 | 48.57 | 0.00
458 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 209.64 | 3.38 | 209.67 | 79.86 | 0.00
459 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 184.67 | 27.37 | 186.69 | 492.32 | 0.00
460 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 185.99 | 27.21 | 187.97 | 521.10 | 0.00
461 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 129.48 | 30.31 | 132.98 | 515.93 | 0.00
462 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 130.79 | 30.13 | 134.22 | 546.39 | 0.00
463 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 129.48 | 30.31 | 132.98 | 515.95 | 0.00
464 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 130.79 | 30.13 | 134.22 | 546.40 | 0.00
465 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 96.03 | 30.32 | 100.70 | 528.68 | 0.00
466 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 97.38 | 30.14 | 101.94 | 528.82 | 0.00
467 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 96.03 | 30.32 | 100.70 | 528.69 | 0.00
468 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 97.38 | 30.14 | 101.94 | 528.84 | 0.00
469 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 108.00 | 30.31 | 112.17 | 515.29 | 0.00
470 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 109.31 | 30.13 | 113.39 | 544.53 | 0.00
471 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 108.00 | 30.31 | 112.17 | 515.30 | 0.00
472 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 109.31 | 30.14 | 113.39 | 544.55 | 0.00
473 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 83.86 | 30.32 | 89.17 | 542.05 | 0.00
474 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 85.25 | 30.14 | 90.42 | 513.12 | 0.00
475 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 83.86 | 30.32 | 89.17 | 542.06 | 0.00
476 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 85.25 | 30.14 | 90.42 | 513.15 | 0.00
477 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 129.30 | 26.86 | 132.06 | 453.30 | 0.00
478 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 130.84 | 26.68 | 133.53 | 483.81 | 0.00
479 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 129.30 | 26.86 | 132.06 | 453.31 | 0.00
480 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 130.84 | 26.68 | 133.53 | 483.82 | 0.00
481 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 95.90 | 26.86 | 99.59 | 466.30 | 0.00
482 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 97.50 | 26.68 | 101.08 | 466.64 | 0.00
483 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 95.90 | 26.86 | 99.59 | 466.31 | 0.00
484 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 97.50 | 26.68 | 101.08 | 466.66 | 0.00
485 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 107.82 | 26.86 | 111.11 | 452.81 | 0.00
486 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 109.37 | 26.68 | 112.57 | 482.11 | 0.00
487 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 107.82 | 26.86 | 111.11 | 452.82 | 0.00
488 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 109.37 | 26.68 | 112.57 | 482.12 | 0.00
489 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 83.80 | 26.87 | 88.00 | 479.77 | 0.00
490 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 85.44 | 26.69 | 89.51 | 451.18 | 0.00
491 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 83.80 | 26.87 | 88.00 | 479.79 | 0.00
492 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 85.44 | 26.69 | 89.51 | 451.21 | 0.00
493 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 104.46 | 26.86 | 107.85 | 456.64 | 0.00
494 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 106.02 | 26.68 | 109.32 | 477.71 | 0.00
495 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 104.45 | 26.86 | 107.85 | 456.65 | 0.00
496 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 106.02 | 26.68 | 109.32 | 477.73 | 0.00
497 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 130.12 | 0.16 | 130.12 | 16.24 | 0.00
498 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 130.12 | 0.16 | 130.12 | 16.24 | 0.00
499 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 134.05 | 3.07 | 134.09 | 29.16 | 0.00
500 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.17 | 2.96 | 134.20 | 77.64 | 0.00
501 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 134.08 | 3.08 | 134.12 | 29.18 | 0.00
502 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.20 | 2.95 | 134.23 | 79.27 | 0.00
503 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 134.05 | 3.03 | 134.09 | 38.92 | 0.00
504 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 134.17 | 3.00 | 134.20 | 68.00 | 0.00
505 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 116.25 | 24.17 | 118.73 | 410.56 | 0.00
506 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 117.57 | 24.02 | 119.99 | 435.37 | 0.00
507 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 131.85 | 29.39 | 135.09 | 509.73 | 0.00
508 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 133.22 | 29.52 | 136.45 | 550.46 | 0.00
509 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 131.85 | 29.39 | 135.09 | 509.74 | 0.00
510 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 133.22 | 29.52 | 136.45 | 550.46 | 0.00
511 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 97.31 | 29.40 | 101.66 | 523.53 | 0.00
512 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 98.67 | 29.52 | 102.99 | 530.72 | 0.00
513 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 97.31 | 29.40 | 101.66 | 523.54 | 0.00
514 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 98.67 | 29.52 | 102.99 | 530.73 | 0.00
515 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 110.10 | 29.39 | 113.95 | 509.09 | 0.00
516 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 111.47 | 29.52 | 115.31 | 548.45 | 0.00
517 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 110.10 | 29.39 | 113.95 | 509.10 | 0.00
518 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 111.46 | 29.52 | 115.31 | 548.45 | 0.00
519 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 84.32 | 29.40 | 89.30 | 537.92 | 0.00
520 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 85.66 | 29.52 | 90.60 | 513.05 | 0.00
521 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 84.32 | 29.40 | 89.30 | 537.91 | 0.00
522 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 85.66 | 29.52 | 90.61 | 513.06 | 0.00
523 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 131.59 | 27.20 | 134.37 | 472.33 | 0.00
524 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 133.21 | 27.29 | 135.97 | 512.23 | 0.00
525 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 131.59 | 27.20 | 134.37 | 472.36 | 0.00
526 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 133.20 | 27.29 | 135.97 | 512.24 | 0.00
527 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 97.19 | 27.20 | 100.92 | 486.21 | 0.00
528 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 98.79 | 27.30 | 102.49 | 492.87 | 0.00
529 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 97.19 | 27.20 | 100.93 | 486.22 | 0.00
530 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 98.79 | 27.30 | 102.49 | 492.89 | 0.00
531 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 109.84 | 27.20 | 113.15 | 471.78 | 0.00
532 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 111.45 | 27.29 | 114.74 | 510.31 | 0.00
533 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 109.84 | 27.20 | 113.15 | 471.81 | 0.00
534 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 111.45 | 27.29 | 114.74 | 510.33 | 0.00
535 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 84.34 | 27.21 | 88.62 | 500.58 | 0.00
536 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 85.92 | 27.30 | 90.15 | 475.49 | 0.00
537 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 84.34 | 27.21 | 88.62 | 500.59 | 0.00
538 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 85.92 | 27.30 | 90.16 | 475.51 | 0.00
539 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 106.27 | 27.20 | 109.69 | 475.88 | 0.00
540 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 107.88 | 27.29 | 111.28 | 505.36 | 0.00
541 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 106.27 | 27.20 | 109.69 | 475.90 | 0.00
542 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 107.87 | 27.29 | 111.27 | 505.37 | 0.00
543 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 131.45 | 0.06 | 131.45 | 18.01 | 0.00
544 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 131.45 | 0.06 | 131.45 | 18.01 | 0.00
545 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 135.10 | 2.82 | 135.13 | 26.75 | 0.00
546 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 135.23 | 2.89 | 135.26 | 77.56 | 0.00
547 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 135.15 | 2.84 | 135.18 | 26.91 | 0.00
548 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 135.28 | 2.87 | 135.31 | 78.71 | 0.00
549 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 135.10 | 2.77 | 135.12 | 34.25 | 0.00
550 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 135.23 | 2.94 | 135.26 | 69.90 | 0.00
551 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:g | 118.31 | 24.31 | 120.79 | 424.70 | 0.00
552 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:g | 119.69 | 24.38 | 122.15 | 457.14 | 0.00
553 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 128.53 | 28.84 | 131.73 | 501.72 | 0.00
554 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 129.85 | 28.43 | 132.93 | 522.77 | 0.00
555 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 128.53 | 28.84 | 131.73 | 501.71 | 0.00
556 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 129.86 | 28.43 | 132.93 | 522.76 | 0.00
557 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 97.29 | 28.84 | 101.47 | 511.55 | 0.00
558 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 98.64 | 28.43 | 102.66 | 508.15 | 0.00
559 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 97.29 | 28.84 | 101.47 | 511.54 | 0.00
560 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 98.64 | 28.43 | 102.66 | 508.14 | 0.00
561 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 106.78 | 28.84 | 110.60 | 501.09 | 0.00
562 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 108.10 | 28.43 | 111.78 | 520.82 | 0.00
563 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 106.78 | 28.84 | 110.60 | 501.08 | 0.00
564 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 108.10 | 28.43 | 111.78 | 520.82 | 0.00
565 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 87.65 | 28.85 | 92.27 | 522.02 | 0.00
566 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 89.03 | 28.43 | 93.46 | 495.44 | 0.00
567 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 87.65 | 28.85 | 92.27 | 522.01 | 0.00
568 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 89.03 | 28.43 | 93.46 | 495.43 | 0.00
569 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 128.37 | 26.88 | 131.15 | 469.13 | 0.00
570 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 129.93 | 26.46 | 132.59 | 489.94 | 0.00
571 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 128.37 | 26.88 | 131.15 | 469.13 | 0.00
572 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 129.93 | 26.46 | 132.60 | 489.95 | 0.00
573 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 97.16 | 26.88 | 100.81 | 479.06 | 0.00
574 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 98.76 | 26.46 | 102.25 | 475.56 | 0.00
575 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 97.16 | 26.88 | 100.81 | 479.05 | 0.00
576 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 98.76 | 26.46 | 102.25 | 475.57 | 0.00
577 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 106.61 | 26.88 | 109.95 | 468.59 | 0.00
578 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 108.17 | 26.46 | 111.36 | 488.09 | 0.00
579 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 106.61 | 26.88 | 109.95 | 468.59 | 0.00
580 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 108.17 | 26.46 | 111.36 | 488.10 | 0.00
581 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 87.56 | 26.89 | 91.60 | 489.54 | 0.00
582 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 89.20 | 26.46 | 93.04 | 463.00 | 0.00
583 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 87.56 | 26.88 | 91.60 | 489.54 | 0.00
584 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 89.20 | 26.47 | 93.04 | 463.01 | 0.00
585 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 103.95 | 26.88 | 107.37 | 471.56 | 0.00
586 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 105.52 | 26.46 | 108.78 | 484.54 | 0.00
587 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 103.95 | 26.88 | 107.37 | 471.56 | 0.00
588 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 105.52 | 26.46 | 108.78 | 484.55 | 0.00
589 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 129.30 | 0.16 | 129.30 | 12.94 | 0.00
590 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 129.30 | 0.16 | 129.30 | 12.94 | 0.00
591 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 132.28 | 2.89 | 132.31 | 31.44 | 0.00
592 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 132.39 | 2.60 | 132.42 | 67.33 | 0.00
593 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 132.29 | 2.90 | 132.33 | 31.58 | 0.00
594 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 132.41 | 2.59 | 132.43 | 68.34 | 0.00
595 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 132.28 | 2.86 | 132.31 | 38.17 | 0.00
596 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 132.39 | 2.63 | 132.42 | 60.71 | 0.00
597 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:g | 115.65 | 23.98 | 118.11 | 420.63 | 0.00
598 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:g | 116.97 | 23.62 | 119.33 | 437.25 | 0.00
599 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 130.47 | 28.27 | 133.50 | 487.88 | 0.00
600 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 131.82 | 27.96 | 134.75 | 515.62 | 0.00
601 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 130.47 | 28.27 | 133.50 | 487.89 | 0.00
602 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 131.81 | 27.96 | 134.75 | 515.64 | 0.00
603 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 97.30 | 28.27 | 101.33 | 499.85 | 0.00
604 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 98.66 | 27.96 | 102.54 | 498.16 | 0.00
605 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 97.30 | 28.27 | 101.33 | 499.85 | 0.00
606 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 98.66 | 27.96 | 102.54 | 498.17 | 0.00
607 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 108.72 | 28.27 | 112.33 | 487.26 | 0.00
608 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 110.06 | 27.96 | 113.56 | 513.67 | 0.00
609 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 108.72 | 28.27 | 112.33 | 487.27 | 0.00
610 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 110.06 | 27.96 | 113.56 | 513.69 | 0.00
611 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 85.70 | 28.28 | 90.25 | 512.43 | 0.00
612 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 87.07 | 27.97 | 91.45 | 482.67 | 0.00
613 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 85.71 | 28.28 | 90.25 | 512.43 | 0.00
614 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 87.07 | 27.97 | 91.45 | 482.68 | 0.00
615 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 130.28 | 26.48 | 132.94 | 458.63 | 0.00
616 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 131.86 | 26.16 | 134.43 | 486.33 | 0.00
617 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 130.28 | 26.48 | 132.94 | 458.63 | 0.00
618 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 131.86 | 26.16 | 134.43 | 486.34 | 0.00
619 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 97.18 | 26.48 | 100.72 | 470.81 | 0.00
620 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 98.78 | 26.17 | 102.18 | 469.18 | 0.00
621 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 97.18 | 26.48 | 100.72 | 470.81 | 0.00
622 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 98.78 | 26.17 | 102.18 | 469.19 | 0.00
623 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 108.52 | 26.48 | 111.71 | 458.11 | 0.00
624 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 110.11 | 26.16 | 113.17 | 484.48 | 0.00
625 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 108.52 | 26.48 | 111.71 | 458.11 | 0.00
626 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 110.11 | 26.16 | 113.17 | 484.49 | 0.00
627 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 85.65 | 26.49 | 89.65 | 483.50 | 0.00
628 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 87.26 | 26.17 | 91.10 | 453.90 | 0.00
629 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 85.65 | 26.49 | 89.66 | 483.50 | 0.00
630 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 87.27 | 26.17 | 91.11 | 453.90 | 0.00
631 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 105.32 | 26.48 | 108.60 | 461.72 | 0.00
632 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 106.91 | 26.16 | 110.06 | 480.14 | 0.00
633 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 105.32 | 26.48 | 108.60 | 461.72 | 0.00
634 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 106.91 | 26.17 | 110.06 | 480.14 | 0.00
635 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | 130.33 | 0.18 | 130.33 | 14.30 | 0.00
636 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | 130.33 | 0.18 | 130.33 | 14.30 | 0.00
637 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.65 | 2.83 | 133.68 | 27.89 | 0.00
638 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 133.77 | 2.61 | 133.80 | 69.39 | 0.00
639 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.67 | 2.83 | 133.70 | 27.93 | 0.00
640 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 133.80 | 2.60 | 133.82 | 70.49 | 0.00
641 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 133.65 | 2.80 | 133.68 | 35.44 | 0.00
642 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | 133.77 | 2.64 | 133.80 | 61.92 | 0.00
643 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:g | 117.28 | 23.60 | 119.63 | 410.74 | 0.00
644 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:g | 118.62 | 23.34 | 120.90 | 433.40 | 0.00

## Tab_7
rowtext | str_no | structure_name | load_case | joint_label | long_force | tran_force | vert_force | shear_force | tran_moment | long_moment | bending_moment | vert_moment | found_usage
1 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.14 | -30.18 | -129.57 | 30.18 | 513.26 | 0.23 | 513.26 | 3.51 | 0.00
2 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.14 | 29.86 | -130.88 | 29.86 | -540.80 | 0.17 | 540.80 | -3.59 | 0.00
3 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.14 | -30.18 | -129.57 | 30.18 | 513.26 | 0.23 | 513.26 | 3.51 | 0.00
4 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.14 | 29.86 | -130.88 | 29.86 | -540.80 | 0.17 | 540.80 | -3.59 | 0.00
5 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.09 | -30.18 | -95.73 | 30.18 | 526.38 | -1.35 | 526.38 | 3.30 | 0.00
6 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.12 | 29.86 | -97.09 | 29.86 | -522.76 | -1.91 | 522.77 | -3.35 | 0.00
7 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.09 | -30.18 | -95.73 | 30.18 | 526.38 | -1.34 | 526.38 | 3.30 | 0.00
8 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.12 | 29.86 | -97.09 | 29.86 | -522.76 | -1.91 | 522.77 | -3.35 | 0.00
9 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.14 | -30.18 | -108.16 | 30.18 | 512.55 | 0.03 | 512.55 | 3.49 | 0.00
10 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.13 | 29.86 | -109.47 | 29.86 | -539.05 | 0.03 | 539.05 | -3.57 | 0.00
11 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.14 | -30.18 | -108.16 | 30.18 | 512.55 | 0.03 | 512.55 | 3.49 | 0.00
12 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.13 | 29.86 | -109.47 | 29.86 | -539.05 | 0.03 | 539.05 | -3.57 | 0.00
13 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.12 | -30.19 | -83.10 | 30.19 | 540.17 | -4.15 | 540.19 | 3.03 | 0.00
14 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.12 | 29.86 | -84.50 | 29.86 | -506.50 | -3.98 | 506.52 | -3.13 | 0.00
15 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.12 | -30.19 | -83.10 | 30.19 | 540.17 | -4.15 | 540.19 | 3.03 | 0.00
16 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.12 | 29.86 | -84.50 | 29.86 | -506.50 | -3.97 | 506.51 | -3.13 | 0.00
17 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.08 | -26.75 | -129.37 | 26.75 | 451.16 | 2.79 | 451.17 | 3.32 | 0.00
18 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.11 | 26.43 | -130.92 | 26.43 | -478.86 | 2.18 | 478.86 | -3.01 | 0.00
19 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.08 | -26.75 | -129.37 | 26.75 | 451.16 | 2.80 | 451.17 | 3.32 | 0.00
20 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.11 | 26.43 | -130.92 | 26.43 | -478.86 | 2.18 | 478.86 | -3.01 | 0.00
21 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 0.06 | -26.76 | -95.61 | 26.76 | 464.52 | 1.93 | 464.52 | 3.16 | 0.00
22 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 0.03 | 26.44 | -97.21 | 26.44 | -461.24 | 1.39 | 461.25 | -2.87 | 0.00
23 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 0.06 | -26.76 | -95.61 | 26.76 | 464.52 | 1.93 | 464.52 | 3.16 | 0.00
24 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 0.03 | 26.44 | -97.21 | 26.44 | -461.24 | 1.40 | 461.25 | -2.87 | 0.00
25 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.08 | -26.75 | -107.96 | 26.75 | 450.60 | 2.52 | 450.61 | 3.30 | 0.00
26 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.11 | 26.43 | -109.51 | 26.44 | -477.25 | 1.92 | 477.25 | -2.99 | 0.00
27 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.08 | -26.75 | -107.96 | 26.75 | 450.60 | 2.52 | 450.61 | 3.30 | 0.00
28 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.11 | 26.43 | -109.51 | 26.44 | -477.25 | 1.92 | 477.25 | -2.99 | 0.00
29 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.08 | -26.76 | -83.06 | 26.76 | 478.41 | -2.11 | 478.42 | 2.87 | 0.00
30 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.11 | 26.44 | -84.70 | 26.44 | -445.26 | -2.58 | 445.27 | -2.58 | 0.00
31 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.08 | -26.76 | -83.06 | 26.76 | 478.41 | -2.11 | 478.41 | 2.87 | 0.00
32 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.11 | 26.44 | -84.70 | 26.44 | -445.26 | -2.58 | 445.27 | -2.58 | 0.00
33 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.08 | -26.75 | -104.48 | 26.75 | 454.56 | 1.80 | 454.56 | 3.23 | 0.00
34 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.11 | 26.44 | -106.04 | 26.44 | -472.71 | 1.22 | 472.71 | -2.93 | 0.00
35 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.08 | -26.75 | -104.48 | 26.75 | 454.55 | 1.80 | 454.56 | 3.23 | 0.00
36 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.11 | 26.44 | -106.04 | 26.44 | -472.70 | 1.22 | 472.71 | -2.93 | 0.00
37 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.14 | -0.12 | -130.04 | 0.18 | -15.22 | 1.58 | 15.31 | -0.00 | 0.00
38 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.14 | -0.12 | -130.04 | 0.18 | -15.22 | 1.58 | 15.31 | -0.00 | 0.00
39 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.15 | -3.12 | -134.06 | 3.12 | 30.21 | 2.11 | 30.29 | 0.39 | 0.00
40 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.16 | 2.89 | -134.18 | 2.89 | -76.20 | 1.89 | 76.22 | -0.41 | 0.00
41 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.15 | -3.14 | -134.10 | 3.14 | 30.38 | 2.23 | 30.46 | 0.41 | 0.00
42 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.16 | 2.87 | -134.21 | 2.87 | -77.69 | 2.01 | 77.71 | -0.39 | 0.00
43 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.15 | -3.08 | -134.07 | 3.08 | 40.21 | 2.12 | 40.26 | 0.41 | 0.00
44 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.16 | 2.92 | -134.18 | 2.93 | -66.33 | 2.01 | 66.36 | -0.40 | 0.00
45 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.04 | -24.03 | -116.28 | 24.03 | 407.88 | 3.00 | 407.89 | 3.10 | 0.00
46 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.07 | 23.77 | -117.60 | 23.77 | -430.34 | 2.43 | 430.34 | -2.85 | 0.00
47 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 0.18 | -29.78 | -129.51 | 29.78 | 505.01 | 7.72 | 505.07 | 4.20 | 0.00
48 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 0.18 | 29.72 | -130.84 | 29.72 | -538.01 | 7.89 | 538.07 | -3.60 | 0.00
49 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 0.18 | -29.77 | -129.51 | 29.78 | 505.01 | 7.72 | 505.07 | 4.20 | 0.00
50 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 0.18 | 29.72 | -130.84 | 29.72 | -538.01 | 7.89 | 538.07 | -3.60 | 0.00
51 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 0.18 | -29.78 | -95.73 | 29.78 | 518.16 | 4.66 | 518.18 | 3.89 | 0.00
52 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 0.18 | 29.73 | -97.09 | 29.73 | -520.01 | 4.86 | 520.03 | -3.30 | 0.00
53 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 0.18 | -29.78 | -95.73 | 29.78 | 518.16 | 4.66 | 518.18 | 3.89 | 0.00
54 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 0.18 | 29.73 | -97.09 | 29.73 | -520.00 | 4.86 | 520.03 | -3.30 | 0.00
55 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 0.18 | -29.78 | -108.10 | 29.78 | 504.32 | 7.30 | 504.38 | 4.16 | 0.00
56 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 0.18 | 29.72 | -109.43 | 29.72 | -536.26 | 7.47 | 536.32 | -3.56 | 0.00
57 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 0.18 | -29.78 | -108.10 | 29.78 | 504.32 | 7.30 | 504.38 | 4.16 | 0.00
58 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 0.18 | 29.72 | -109.43 | 29.72 | -536.26 | 7.47 | 536.31 | -3.56 | 0.00
59 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 0.18 | -29.78 | -83.17 | 29.78 | 531.97 | 2.29 | 531.98 | 3.64 | 0.00
60 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 0.18 | 29.73 | -84.55 | 29.73 | -503.76 | 2.51 | 503.77 | -3.06 | 0.00
61 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 0.18 | -29.78 | -83.17 | 29.78 | 531.97 | 2.29 | 531.98 | 3.64 | 0.00
62 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 0.18 | 29.73 | -84.55 | 29.73 | -503.76 | 2.51 | 503.77 | -3.06 | 0.00
63 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.07 | -26.43 | -129.31 | 26.43 | 444.71 | 2.98 | 444.72 | 3.19 | 0.00
64 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.07 | 26.38 | -130.87 | 26.38 | -477.62 | 3.18 | 477.63 | -2.90 | 0.00
65 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.07 | -26.43 | -129.31 | 26.43 | 444.71 | 2.98 | 444.72 | 3.19 | 0.00
66 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.07 | 26.38 | -130.87 | 26.38 | -477.62 | 3.18 | 477.63 | -2.90 | 0.00
67 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 0.07 | -26.44 | -95.61 | 26.44 | 458.09 | 2.12 | 458.09 | 3.04 | 0.00
68 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 0.07 | 26.38 | -97.21 | 26.38 | -460.03 | 2.33 | 460.03 | -2.75 | 0.00
69 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 0.07 | -26.44 | -95.61 | 26.44 | 458.09 | 2.12 | 458.09 | 3.04 | 0.00
70 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 0.07 | 26.38 | -97.21 | 26.38 | -460.03 | 2.33 | 460.03 | -2.75 | 0.00
71 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.07 | -26.43 | -107.90 | 26.44 | 444.17 | 2.70 | 444.18 | 3.17 | 0.00
72 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.07 | 26.38 | -109.46 | 26.38 | -476.01 | 2.89 | 476.02 | -2.88 | 0.00
73 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.07 | -26.43 | -107.90 | 26.43 | 444.17 | 2.70 | 444.18 | 3.17 | 0.00
74 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.07 | 26.38 | -109.46 | 26.38 | -476.01 | 2.89 | 476.02 | -2.88 | 0.00
75 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.07 | -26.44 | -83.12 | 26.44 | 471.98 | -1.91 | 471.99 | 2.74 | 0.00
76 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.07 | 26.38 | -84.76 | 26.38 | -444.06 | -1.67 | 444.07 | -2.46 | 0.00
77 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.07 | -26.44 | -83.12 | 26.44 | 471.98 | -1.91 | 471.99 | 2.74 | 0.00
78 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.07 | 26.38 | -84.76 | 26.38 | -444.06 | -1.67 | 444.07 | -2.46 | 0.00
79 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.07 | -26.44 | -104.43 | 26.44 | 448.12 | 1.98 | 448.13 | 3.10 | 0.00
80 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.07 | 26.38 | -106.00 | 26.38 | -471.47 | 2.18 | 471.48 | -2.81 | 0.00
81 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.07 | -26.44 | -104.43 | 26.44 | 448.12 | 1.98 | 448.13 | 3.10 | 0.00
82 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.07 | 26.38 | -106.00 | 26.38 | -471.47 | 2.18 | 471.48 | -2.81 | 0.00
83 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.11 | -0.05 | -129.93 | 0.12 | -16.48 | 2.26 | 16.63 | 0.03 | 0.00
84 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.11 | -0.05 | -129.93 | 0.12 | -16.48 | 2.26 | 16.63 | 0.03 | 0.00
85 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.07 | -2.98 | -133.92 | 2.98 | 27.57 | 3.98 | 27.86 | 0.47 | 0.00
86 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.08 | 2.96 | -134.04 | 2.96 | -77.55 | 3.91 | 77.65 | -0.32 | 0.00
87 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.08 | -3.00 | -133.96 | 3.00 | 27.76 | 3.93 | 28.04 | 0.47 | 0.00
88 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.08 | 2.94 | -134.08 | 2.94 | -78.99 | 3.85 | 79.08 | -0.32 | 0.00
89 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.08 | -2.94 | -133.92 | 2.94 | 37.48 | 3.93 | 37.69 | 0.42 | 0.00
90 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.08 | 3.00 | -134.05 | 3.00 | -67.76 | 3.93 | 67.87 | -0.37 | 0.00
91 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.12 | -23.75 | -116.23 | 23.75 | 402.07 | 0.81 | 402.07 | 2.72 | 0.00
92 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.12 | 23.70 | -117.56 | 23.70 | -428.80 | 1.11 | 428.80 | -2.71 | 0.00
93 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.84 | -25.82 | -128.28 | 25.84 | 424.43 | -17.45 | 424.79 | 0.73 | 0.00
94 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.98 | 25.03 | -129.54 | 25.05 | -441.65 | -20.52 | 442.12 | -2.50 | 0.00
95 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.86 | -25.82 | -128.27 | 25.84 | 424.44 | -17.77 | 424.81 | 0.70 | 0.00
96 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.98 | 25.03 | -129.54 | 25.05 | -441.65 | -20.58 | 442.13 | -2.50 | 0.00
97 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.84 | -25.83 | -95.73 | 25.84 | 438.27 | -18.49 | 438.66 | 0.62 | 0.00
98 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.98 | 25.04 | -97.08 | 25.06 | -424.33 | -21.33 | 424.87 | -2.40 | 0.00
99 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.86 | -25.83 | -95.73 | 25.84 | 438.27 | -18.79 | 438.67 | 0.59 | 0.00
100 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.98 | 25.04 | -97.08 | 25.06 | -424.33 | -21.39 | 424.87 | -2.40 | 0.00
101 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.84 | -25.82 | -106.87 | 25.84 | 423.94 | -17.10 | 424.28 | 0.75 | 0.00
102 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.98 | 25.03 | -108.13 | 25.05 | -440.13 | -20.08 | 440.59 | -2.52 | 0.00
103 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.86 | -25.82 | -106.86 | 25.84 | 423.95 | -17.41 | 424.30 | 0.72 | 0.00
104 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.98 | 25.03 | -108.13 | 25.05 | -440.13 | -20.14 | 440.60 | -2.52 | 0.00
105 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.85 | -25.83 | -84.41 | 25.84 | 452.62 | -19.74 | 453.05 | 0.51 | 0.00
106 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.98 | 25.04 | -85.86 | 25.06 | -408.51 | -22.45 | 409.13 | -2.28 | 0.00
107 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.86 | -25.83 | -84.41 | 25.84 | 452.61 | -20.02 | 453.05 | 0.48 | 0.00
108 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.98 | 25.04 | -85.86 | 25.06 | -408.51 | -22.50 | 409.13 | -2.28 | 0.00
109 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.25 | -23.47 | -128.04 | 23.47 | 384.29 | -3.01 | 384.30 | 1.89 | 0.00
110 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.38 | 22.69 | -129.53 | 22.70 | -401.56 | -6.08 | 401.61 | -2.43 | 0.00
111 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.26 | -23.47 | -128.03 | 23.47 | 384.30 | -3.29 | 384.32 | 1.87 | 0.00
112 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.38 | 22.69 | -129.53 | 22.70 | -401.56 | -6.13 | 401.61 | -2.43 | 0.00
113 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.25 | -23.48 | -95.60 | 23.48 | 398.21 | -5.03 | 398.24 | 1.73 | 0.00
114 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.38 | 22.70 | -97.20 | 22.70 | -384.63 | -7.86 | 384.71 | -2.28 | 0.00
115 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.26 | -23.48 | -95.60 | 23.48 | 398.21 | -5.29 | 398.24 | 1.71 | 0.00
116 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.38 | 22.70 | -97.20 | 22.70 | -384.63 | -7.90 | 384.72 | -2.28 | 0.00
117 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.25 | -23.47 | -106.63 | 23.47 | 383.90 | -3.10 | 383.91 | 1.89 | 0.00
118 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.38 | 22.69 | -108.12 | 22.70 | -400.14 | -6.08 | 400.19 | -2.42 | 0.00
119 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.26 | -23.47 | -106.62 | 23.47 | 383.91 | -3.37 | 383.92 | 1.86 | 0.00
120 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.38 | 22.69 | -108.12 | 22.70 | -400.14 | -6.13 | 400.19 | -2.42 | 0.00
121 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.25 | -23.48 | -84.40 | 23.48 | 412.54 | -6.78 | 412.59 | 1.59 | 0.00
122 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.38 | 22.70 | -86.11 | 22.70 | -369.11 | -9.46 | 369.23 | -2.15 | 0.00
123 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.26 | -23.48 | -84.41 | 23.48 | 412.53 | -7.03 | 412.59 | 1.57 | 0.00
124 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.38 | 22.70 | -86.11 | 22.70 | -369.11 | -9.51 | 369.23 | -2.15 | 0.00
125 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.25 | -23.47 | -103.52 | 23.47 | 387.96 | -3.66 | 387.97 | 1.84 | 0.00
126 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.38 | 22.69 | -105.04 | 22.70 | -395.74 | -6.60 | 395.80 | -2.38 | 0.00
127 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.26 | -23.47 | -103.51 | 23.47 | 387.96 | -3.94 | 387.98 | 1.81 | 0.00
128 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.38 | 22.69 | -105.04 | 22.70 | -395.74 | -6.65 | 395.80 | -2.38 | 0.00
129 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.12 | -0.19 | -128.02 | 0.22 | -11.72 | 1.42 | 11.81 | 0.01 | 0.00
130 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.12 | -0.19 | -128.02 | 0.22 | -11.72 | 1.42 | 11.81 | 0.01 | 0.00
131 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.13 | -2.78 | -131.44 | 2.79 | 26.01 | 2.11 | 26.10 | 0.33 | 0.00
132 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.15 | 2.13 | -131.54 | 2.14 | -58.18 | 1.50 | 58.20 | -0.29 | 0.00
133 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.13 | -2.81 | -131.46 | 2.81 | 26.55 | 2.14 | 26.64 | 0.34 | 0.00
134 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.15 | 2.10 | -131.56 | 2.11 | -58.87 | 1.49 | 58.89 | -0.28 | 0.00
135 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.13 | -2.66 | -131.34 | 2.66 | 32.49 | 2.12 | 32.56 | 0.30 | 0.00
136 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.15 | 2.25 | -131.45 | 2.26 | -51.72 | 1.56 | 51.75 | -0.30 | 0.00
137 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.07 | -20.95 | -115.25 | 20.95 | 345.08 | 2.02 | 345.09 | 2.38 | 0.00
138 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.10 | 20.31 | -116.52 | 20.31 | -359.08 | 0.29 | 359.08 | -2.30 | 0.00
139 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.24 | -26.48 | -128.20 | 26.48 | 438.46 | -2.82 | 438.47 | 2.41 | 0.00
140 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.37 | -129.56 | 30.38 | -549.93 | -14.57 | 550.12 | -2.95 | 0.00
141 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.29 | -26.48 | -128.20 | 26.48 | 438.49 | -3.99 | 438.50 | 2.29 | 0.00
142 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.75 | 30.36 | -129.56 | 30.37 | -549.82 | -14.83 | 550.02 | -2.94 | 0.00
143 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.24 | -26.48 | -95.73 | 26.48 | 451.40 | -4.86 | 451.42 | 2.22 | 0.00
144 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.37 | -97.08 | 30.38 | -532.76 | -15.79 | 533.00 | -2.79 | 0.00
145 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.29 | -26.48 | -95.73 | 26.48 | 451.41 | -5.95 | 451.45 | 2.11 | 0.00
146 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.75 | 30.36 | -97.08 | 30.37 | -532.66 | -16.03 | 532.90 | -2.78 | 0.00
147 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.24 | -26.48 | -106.79 | 26.48 | 437.94 | -2.91 | 437.95 | 2.40 | 0.00
148 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.37 | -108.15 | 30.38 | -548.15 | -14.31 | 548.34 | -2.96 | 0.00
149 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.29 | -26.48 | -106.79 | 26.48 | 437.96 | -4.05 | 437.98 | 2.28 | 0.00
150 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.75 | 30.36 | -108.15 | 30.37 | -548.04 | -14.56 | 548.23 | -2.95 | 0.00
151 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.24 | -26.48 | -84.49 | 26.49 | 464.86 | -6.63 | 464.91 | 2.06 | 0.00
152 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.37 | -85.82 | 30.38 | -517.36 | -17.12 | 517.65 | -2.62 | 0.00
153 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.29 | -26.49 | -84.49 | 26.49 | 464.88 | -7.68 | 464.94 | 1.95 | 0.00
154 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.75 | 30.37 | -85.82 | 30.38 | -517.26 | -17.36 | 517.55 | -2.62 | 0.00
155 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.09 | -23.55 | -128.01 | 23.55 | 386.52 | 2.14 | 386.52 | 2.62 | 0.00
156 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.43 | 27.31 | -129.63 | 27.32 | -495.51 | -7.23 | 495.56 | -2.75 | 0.00
157 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.13 | -23.55 | -128.01 | 23.55 | 386.56 | 1.37 | 386.57 | 2.52 | 0.00
158 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.44 | 27.31 | -129.63 | 27.31 | -495.42 | -7.48 | 495.47 | -2.75 | 0.00
159 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 0.05 | -23.55 | -95.60 | 23.55 | 399.61 | 1.60 | 399.61 | 2.51 | 0.00
160 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.43 | 27.32 | -97.19 | 27.32 | -478.72 | -8.95 | 478.80 | -2.58 | 0.00
161 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.01 | -23.55 | -95.60 | 23.55 | 399.65 | 0.29 | 399.65 | 2.39 | 0.00
162 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.44 | 27.31 | -97.19 | 27.32 | -478.62 | -9.18 | 478.71 | -2.57 | 0.00
163 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.09 | -23.55 | -106.60 | 23.55 | 386.11 | 1.88 | 386.12 | 2.60 | 0.00
164 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.43 | 27.31 | -108.22 | 27.32 | -493.86 | -7.20 | 493.91 | -2.75 | 0.00
165 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.13 | -23.55 | -106.60 | 23.55 | 386.16 | 1.14 | 386.16 | 2.51 | 0.00
166 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.44 | 27.31 | -108.22 | 27.31 | -493.77 | -7.43 | 493.83 | -2.75 | 0.00
167 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.09 | -23.56 | -84.43 | 23.56 | 413.11 | -2.20 | 413.12 | 2.28 | 0.00
168 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.43 | 27.32 | -85.99 | 27.32 | -463.56 | -10.53 | 463.68 | -2.41 | 0.00
169 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.11 | -23.56 | -84.43 | 23.56 | 413.16 | -2.85 | 413.17 | 2.19 | 0.00
170 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.44 | 27.32 | -85.99 | 27.32 | -463.47 | -10.75 | 463.59 | -2.41 | 0.00
171 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.09 | -23.55 | -103.50 | 23.55 | 389.94 | 1.25 | 389.94 | 2.55 | 0.00
172 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.43 | 27.31 | -105.11 | 27.32 | -489.56 | -7.71 | 489.63 | -2.70 | 0.00
173 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.10 | -23.55 | -103.50 | 23.55 | 389.99 | 0.60 | 389.99 | 2.46 | 0.00
174 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.44 | 27.31 | -105.11 | 27.31 | -489.47 | -7.95 | 489.54 | -2.69 | 0.00
175 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.13 | 1.03 | -128.81 | 1.04 | -37.21 | 0.99 | 37.22 | -0.16 | 0.00
176 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.13 | 1.03 | -128.81 | 1.04 | -37.21 | 0.99 | 37.22 | -0.16 | 0.00
177 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.14 | -1.25 | -132.42 | 1.26 | -5.94 | 1.97 | 6.26 | 0.13 | 0.00
178 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.17 | 4.39 | -132.56 | 4.39 | -104.86 | 0.60 | 104.86 | -0.63 | 0.00
179 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.14 | -1.28 | -132.46 | 1.29 | -6.15 | 1.93 | 6.45 | 0.13 | 0.00
180 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.17 | 4.36 | -132.60 | 4.36 | -106.58 | 0.53 | 106.58 | -0.63 | 0.00
181 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.15 | -1.17 | -132.37 | 1.18 | 2.02 | 1.84 | 2.73 | 0.12 | 0.00
182 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.16 | 4.46 | -132.52 | 4.47 | -96.94 | 0.55 | 96.94 | -0.58 | 0.00
183 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 0.14 | -21.23 | -115.19 | 21.23 | 351.32 | 5.66 | 351.36 | 2.78 | 0.00
184 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.33 | 24.35 | -116.57 | 24.35 | -441.09 | -5.08 | 441.12 | -2.63 | 0.00
185 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -1.11 | -30.10 | -128.51 | 30.12 | 512.77 | -24.03 | 513.33 | 0.34 | 0.00
186 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -1.14 | 29.86 | -129.84 | 29.88 | -539.60 | -24.63 | 540.16 | -2.84 | 0.00
187 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -1.11 | -30.10 | -128.51 | 30.12 | 512.77 | -24.04 | 513.33 | 0.34 | 0.00
188 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -1.14 | 29.86 | -129.84 | 29.88 | -539.60 | -24.62 | 540.16 | -2.84 | 0.00
189 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -1.11 | -30.10 | -95.72 | 30.13 | 524.81 | -24.63 | 525.39 | 0.25 | 0.00
190 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -1.14 | 29.86 | -97.08 | 29.88 | -522.83 | -25.18 | 523.44 | -2.73 | 0.00
191 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -1.11 | -30.10 | -95.72 | 30.13 | 524.81 | -24.64 | 525.39 | 0.25 | 0.00
192 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -1.14 | 29.86 | -97.08 | 29.88 | -522.83 | -25.18 | 523.44 | -2.73 | 0.00
193 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -1.11 | -30.10 | -107.10 | 30.12 | 512.06 | -23.48 | 512.60 | 0.38 | 0.00
194 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -1.14 | 29.86 | -108.43 | 29.88 | -537.85 | -24.06 | 538.38 | -2.88 | 0.00
195 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -1.11 | -30.10 | -107.10 | 30.12 | 512.06 | -23.49 | 512.60 | 0.38 | 0.00
196 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -1.14 | 29.86 | -108.43 | 29.88 | -537.84 | -24.05 | 538.38 | -2.88 | 0.00
197 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -1.11 | -30.11 | -84.16 | 30.13 | 537.56 | -25.66 | 538.17 | 0.13 | 0.00
198 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -1.14 | 29.86 | -85.54 | 29.89 | -507.82 | -26.17 | 508.49 | -2.60 | 0.00
199 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -1.11 | -30.11 | -84.16 | 30.13 | 537.56 | -25.67 | 538.17 | 0.13 | 0.00
200 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -1.14 | 29.86 | -85.54 | 29.89 | -507.82 | -26.17 | 508.49 | -2.60 | 0.00
201 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.18 | -26.74 | -128.36 | 26.74 | 451.87 | -1.36 | 451.87 | 2.48 | 0.00
202 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.49 | -129.92 | 26.49 | -478.84 | -2.06 | 478.84 | -2.97 | 0.00
203 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.18 | -26.74 | -128.36 | 26.74 | 451.87 | -1.37 | 451.87 | 2.48 | 0.00
204 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.22 | 26.49 | -129.92 | 26.49 | -478.84 | -2.05 | 478.84 | -2.97 | 0.00
205 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.18 | -26.74 | -95.60 | 26.74 | 464.17 | -3.55 | 464.18 | 2.28 | 0.00
206 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.50 | -97.20 | 26.50 | -462.44 | -4.18 | 462.46 | -2.77 | 0.00
207 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.18 | -26.74 | -95.60 | 26.74 | 464.16 | -3.56 | 464.18 | 2.28 | 0.00
208 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.22 | 26.50 | -97.20 | 26.50 | -462.44 | -4.17 | 462.46 | -2.77 | 0.00
209 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.18 | -26.74 | -106.95 | 26.74 | 451.31 | -1.50 | 451.31 | 2.47 | 0.00
210 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.49 | -108.51 | 26.49 | -477.23 | -2.18 | 477.24 | -2.95 | 0.00
211 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.18 | -26.74 | -106.95 | 26.74 | 451.31 | -1.51 | 451.31 | 2.47 | 0.00
212 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.22 | 26.49 | -108.51 | 26.49 | -477.23 | -2.17 | 477.24 | -2.95 | 0.00
213 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.18 | -26.74 | -84.07 | 26.74 | 477.02 | -5.41 | 477.05 | 2.10 | 0.00
214 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.50 | -85.70 | 26.50 | -447.65 | -5.99 | 447.69 | -2.59 | 0.00
215 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.18 | -26.74 | -84.07 | 26.74 | 477.02 | -5.42 | 477.05 | 2.10 | 0.00
216 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.22 | 26.50 | -85.70 | 26.50 | -447.65 | -5.98 | 447.69 | -2.59 | 0.00
217 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.18 | -26.74 | -103.74 | 26.74 | 454.96 | -2.10 | 454.96 | 2.41 | 0.00
218 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.49 | -105.32 | 26.49 | -473.04 | -2.77 | 473.04 | -2.90 | 0.00
219 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.18 | -26.74 | -103.74 | 26.74 | 454.96 | -2.11 | 454.96 | 2.41 | 0.00
220 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.22 | 26.49 | -105.32 | 26.49 | -473.03 | -2.76 | 473.04 | -2.90 | 0.00
221 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.14 | -0.10 | -129.29 | 0.17 | -14.72 | 0.89 | 14.75 | -0.04 | 0.00
222 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.14 | -0.10 | -129.29 | 0.17 | -14.72 | 0.89 | 14.75 | -0.04 | 0.00
223 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.17 | -3.06 | -133.05 | 3.06 | 30.36 | 1.37 | 30.39 | 0.30 | 0.00
224 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.17 | 2.87 | -133.17 | 2.88 | -74.61 | 1.16 | 74.62 | -0.43 | 0.00
225 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.17 | -3.07 | -133.10 | 3.08 | 30.47 | 1.46 | 30.50 | 0.31 | 0.00
226 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.17 | 2.86 | -133.22 | 2.87 | -76.19 | 1.24 | 76.20 | -0.42 | 0.00
227 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.17 | -3.02 | -133.06 | 3.02 | 39.65 | 1.42 | 39.67 | 0.33 | 0.00
228 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.17 | 2.91 | -133.18 | 2.92 | -65.48 | 1.22 | 65.49 | -0.40 | 0.00
229 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 0.12 | -24.03 | -115.45 | 24.04 | 408.80 | 5.16 | 408.84 | 3.08 | 0.00
230 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.04 | 23.84 | -116.78 | 23.84 | -430.68 | 3.05 | 430.69 | -2.78 | 0.00
231 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.75 | -34.15 | -204.72 | 34.16 | 614.90 | -15.17 | 615.08 | 2.61 | 0.00
232 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.80 | 33.84 | -206.02 | 33.85 | -647.15 | -16.30 | 647.35 | -4.02 | 0.00
233 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.75 | -34.15 | -204.72 | 34.16 | 614.90 | -15.20 | 615.08 | 2.61 | 0.00
234 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.80 | 33.84 | -206.02 | 33.85 | -647.15 | -16.28 | 647.35 | -4.02 | 0.00
235 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.75 | -34.15 | -155.57 | 34.16 | 630.80 | -17.61 | 631.04 | 2.47 | 0.00
236 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.80 | 33.84 | -156.92 | 33.85 | -627.14 | -18.67 | 627.42 | -3.87 | 0.00
237 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.75 | -34.15 | -155.57 | 34.16 | 630.80 | -17.64 | 631.04 | 2.46 | 0.00
238 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.80 | 33.84 | -156.92 | 33.85 | -627.14 | -18.65 | 627.42 | -3.87 | 0.00
239 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.75 | -34.15 | -170.02 | 34.16 | 614.11 | -15.01 | 614.29 | 2.62 | 0.00
240 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.80 | 33.84 | -171.32 | 33.85 | -645.31 | -16.12 | 645.51 | -4.03 | 0.00
241 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.75 | -34.15 | -170.02 | 34.16 | 614.10 | -15.04 | 614.29 | 2.61 | 0.00
242 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.80 | 33.84 | -171.32 | 33.85 | -645.31 | -16.10 | 645.51 | -4.03 | 0.00
243 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.75 | -34.16 | -140.89 | 34.16 | 647.53 | -20.06 | 647.84 | 2.32 | 0.00
244 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.80 | 33.84 | -142.29 | 33.85 | -608.94 | -21.07 | 609.31 | -3.72 | 0.00
245 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.75 | -34.16 | -140.89 | 34.16 | 647.53 | -20.09 | 647.84 | 2.32 | 0.00
246 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.80 | 33.84 | -142.29 | 33.85 | -608.94 | -21.05 | 609.30 | -3.72 | 0.00
247 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.16 | -30.99 | -204.48 | 30.99 | 554.00 | -0.17 | 554.00 | 3.27 | 0.00
248 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.20 | 30.68 | -206.04 | 30.68 | -586.26 | -0.83 | 586.27 | -3.46 | 0.00
249 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.16 | -30.99 | -204.48 | 30.99 | 554.00 | -0.16 | 554.00 | 3.27 | 0.00
250 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.20 | 30.68 | -206.04 | 30.68 | -586.26 | -0.81 | 586.27 | -3.46 | 0.00
251 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.13 | -30.99 | -155.43 | 30.99 | 570.02 | -2.71 | 570.02 | 3.13 | 0.00
252 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.20 | 30.69 | -157.05 | 30.69 | -566.61 | -3.93 | 566.62 | -3.30 | 0.00
253 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.13 | -30.99 | -155.43 | 30.99 | 570.01 | -2.74 | 570.02 | 3.13 | 0.00
254 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.20 | 30.68 | -157.05 | 30.69 | -566.60 | -3.91 | 566.62 | -3.30 | 0.00
255 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.16 | -30.99 | -169.78 | 30.99 | 553.35 | -0.33 | 553.35 | 3.26 | 0.00
256 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.20 | 30.68 | -171.34 | 30.68 | -584.56 | -1.01 | 584.56 | -3.45 | 0.00
257 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.16 | -30.99 | -169.78 | 30.99 | 553.34 | -0.32 | 553.34 | 3.26 | 0.00
258 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.20 | 30.68 | -171.34 | 30.68 | -584.56 | -0.99 | 584.56 | -3.45 | 0.00
259 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.14 | -31.00 | -140.86 | 31.00 | 586.73 | -5.62 | 586.76 | 2.98 | 0.00
260 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.20 | 30.69 | -142.54 | 30.69 | -548.62 | -6.69 | 548.66 | -3.15 | 0.00
261 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.14 | -31.00 | -140.86 | 31.00 | 586.73 | -5.65 | 586.76 | 2.98 | 0.00
262 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.19 | 30.69 | -142.54 | 30.69 | -548.62 | -6.67 | 548.66 | -3.15 | 0.00
263 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.13 | -30.99 | -165.73 | 30.99 | 558.07 | -0.59 | 558.07 | 3.24 | 0.00
264 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.20 | 30.68 | -167.30 | 30.68 | -579.47 | -1.85 | 579.47 | -3.41 | 0.00
265 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.13 | -30.99 | -165.73 | 30.99 | 558.07 | -0.62 | 558.07 | 3.24 | 0.00
266 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.20 | 30.68 | -167.30 | 30.68 | -579.46 | -1.84 | 579.47 | -3.41 | 0.00
267 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.16 | -0.13 | -204.61 | 0.21 | -16.57 | 1.20 | 16.62 | -0.02 | 0.00
268 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.16 | -0.13 | -204.61 | 0.21 | -16.57 | 1.20 | 16.62 | -0.02 | 0.00
269 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.20 | -3.51 | -209.16 | 3.51 | 38.28 | 2.10 | 38.34 | 0.42 | 0.00
270 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.20 | 3.28 | -209.28 | 3.28 | -89.28 | 1.66 | 89.30 | -0.47 | 0.00
271 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.20 | -3.52 | -209.16 | 3.52 | 38.37 | 2.02 | 38.42 | 0.41 | 0.00
272 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.21 | 3.26 | -209.27 | 3.27 | -90.86 | 1.57 | 90.87 | -0.48 | 0.00
273 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.20 | -3.47 | -209.15 | 3.47 | 49.51 | 2.04 | 49.56 | 0.43 | 0.00
274 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.21 | 3.31 | -209.26 | 3.32 | -78.16 | 1.64 | 78.18 | -0.45 | 0.00
275 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.11 | -27.35 | -184.38 | 27.35 | 492.08 | 1.90 | 492.08 | 3.30 | 0.00
276 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.13 | 27.10 | -185.70 | 27.10 | -518.28 | 1.28 | 518.28 | -3.20 | 0.00
277 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -1.24 | -29.45 | -131.80 | 29.48 | 495.80 | -26.80 | 496.52 | -0.14 | 0.00
278 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -1.28 | 29.30 | -133.13 | 29.33 | -532.43 | -27.42 | 533.13 | -2.79 | 0.00
279 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -1.24 | -29.45 | -131.80 | 29.48 | 495.80 | -26.78 | 496.52 | -0.13 | 0.00
280 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -1.28 | 29.30 | -133.13 | 29.33 | -532.43 | -27.46 | 533.14 | -2.79 | 0.00
281 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -1.24 | -29.46 | -96.05 | 29.48 | 511.49 | -27.50 | 512.23 | -0.24 | 0.00
282 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -1.28 | 29.30 | -97.40 | 29.33 | -511.64 | -28.07 | 512.41 | -2.67 | 0.00
283 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -1.24 | -29.46 | -96.05 | 29.48 | 511.49 | -27.48 | 512.22 | -0.24 | 0.00
284 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -1.28 | 29.30 | -97.40 | 29.33 | -511.64 | -28.11 | 512.41 | -2.67 | 0.00
285 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -1.24 | -29.45 | -110.32 | 29.48 | 495.21 | -26.17 | 495.90 | -0.09 | 0.00
286 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -1.28 | 29.30 | -111.65 | 29.33 | -530.60 | -26.78 | 531.27 | -2.84 | 0.00
287 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -1.24 | -29.45 | -110.32 | 29.48 | 495.21 | -26.15 | 495.90 | -0.09 | 0.00
288 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -1.28 | 29.30 | -111.65 | 29.33 | -530.60 | -26.82 | 531.28 | -2.84 | 0.00
289 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -1.24 | -29.46 | -81.54 | 29.49 | 527.68 | -28.63 | 528.46 | -0.37 | 0.00
290 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -1.28 | 29.31 | -82.92 | 29.34 | -492.76 | -29.16 | 493.62 | -2.51 | 0.00
291 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -1.24 | -29.46 | -81.54 | 29.49 | 527.68 | -28.60 | 528.45 | -0.37 | 0.00
292 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -1.28 | 29.31 | -82.92 | 29.34 | -492.76 | -29.20 | 493.62 | -2.51 | 0.00
293 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.31 | -26.10 | -131.51 | 26.10 | 435.33 | -4.25 | 435.35 | 1.98 | 0.00
294 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.36 | 25.95 | -133.08 | 25.95 | -471.73 | -4.81 | 471.76 | -2.94 | 0.00
295 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.31 | -26.10 | -131.51 | 26.10 | 435.33 | -4.22 | 435.35 | 1.99 | 0.00
296 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.36 | 25.95 | -133.08 | 25.95 | -471.73 | -4.85 | 471.76 | -2.94 | 0.00
297 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.32 | -26.11 | -95.92 | 26.11 | 451.19 | -6.74 | 451.24 | 1.76 | 0.00
298 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.36 | 25.95 | -97.52 | 25.96 | -451.50 | -7.24 | 451.56 | -2.71 | 0.00
299 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.31 | -26.11 | -95.92 | 26.11 | 451.19 | -6.72 | 451.24 | 1.76 | 0.00
300 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.36 | 25.95 | -97.52 | 25.96 | -451.50 | -7.28 | 451.56 | -2.71 | 0.00
301 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.31 | -26.10 | -110.03 | 26.10 | 434.88 | -4.32 | 434.91 | 1.98 | 0.00
302 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.36 | 25.95 | -111.60 | 25.95 | -470.05 | -4.87 | 470.08 | -2.93 | 0.00
303 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.31 | -26.10 | -110.03 | 26.10 | 434.88 | -4.29 | 434.91 | 1.98 | 0.00
304 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.36 | 25.95 | -111.60 | 25.95 | -470.05 | -4.91 | 470.08 | -2.93 | 0.00
305 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.32 | -26.11 | -81.58 | 26.12 | 467.42 | -8.87 | 467.51 | 1.56 | 0.00
306 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.36 | 25.96 | -83.21 | 25.96 | -433.03 | -9.32 | 433.13 | -2.52 | 0.00
307 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.32 | -26.11 | -81.58 | 26.12 | 467.42 | -8.84 | 467.50 | 1.56 | 0.00
308 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.36 | 25.96 | -83.21 | 25.96 | -433.02 | -9.36 | 433.12 | -2.52 | 0.00
309 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.31 | -26.10 | -106.05 | 26.11 | 439.52 | -5.04 | 439.55 | 1.91 | 0.00
310 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.36 | 25.95 | -107.63 | 25.95 | -464.78 | -5.58 | 464.81 | -2.87 | 0.00
311 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.31 | -26.10 | -106.05 | 26.11 | 439.52 | -5.02 | 439.55 | 1.91 | 0.00
312 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.36 | 25.95 | -107.63 | 25.95 | -464.78 | -5.62 | 464.81 | -2.87 | 0.00
313 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.14 | -0.08 | -131.48 | 0.16 | -17.77 | 1.96 | 17.87 | 0.05 | 0.00
314 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.14 | -0.08 | -131.48 | 0.16 | -17.77 | 1.96 | 17.87 | 0.05 | 0.00
315 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.11 | -3.00 | -135.87 | 3.00 | 25.38 | 3.46 | 25.62 | 0.46 | 0.00
316 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.12 | 2.86 | -135.99 | 2.87 | -78.29 | 3.26 | 78.36 | -0.30 | 0.00
317 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.11 | -3.02 | -135.95 | 3.03 | 25.36 | 3.48 | 25.59 | 0.47 | 0.00
318 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.12 | 2.84 | -136.07 | 2.84 | -79.91 | 3.36 | 79.98 | -0.29 | 0.00
319 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.12 | -2.92 | -135.88 | 2.93 | 35.47 | 3.38 | 35.63 | 0.44 | 0.00
320 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.12 | 2.94 | -136.01 | 2.95 | -68.31 | 3.25 | 68.39 | -0.32 | 0.00
321 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.08 | -23.45 | -118.07 | 23.45 | 393.92 | 2.17 | 393.92 | 2.68 | 0.00
322 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.11 | 23.33 | -119.41 | 23.33 | -423.56 | 1.72 | 423.57 | -2.76 | 0.00
323 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.90 | -29.60 | -129.52 | 29.61 | 501.11 | -18.56 | 501.46 | 1.07 | 0.00
324 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.97 | 29.61 | -130.85 | 29.62 | -535.98 | -20.08 | 536.36 | -2.76 | 0.00
325 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.95 | -29.60 | -129.52 | 29.61 | 501.13 | -19.72 | 501.52 | 0.94 | 0.00
326 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -1.00 | 29.61 | -130.85 | 29.63 | -535.98 | -20.67 | 536.38 | -2.75 | 0.00
327 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.90 | -29.60 | -96.03 | 29.61 | 514.15 | -19.65 | 514.53 | 0.93 | 0.00
328 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.97 | 29.61 | -97.38 | 29.63 | -518.16 | -21.05 | 518.58 | -2.62 | 0.00
329 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.95 | -29.60 | -96.03 | 29.62 | 514.17 | -20.72 | 514.58 | 0.81 | 0.00
330 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -1.00 | 29.61 | -97.38 | 29.63 | -518.16 | -21.60 | 518.61 | -2.61 | 0.00
331 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.90 | -29.60 | -108.04 | 29.61 | 500.51 | -18.18 | 500.84 | 1.09 | 0.00
332 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.97 | 29.61 | -109.37 | 29.62 | -534.15 | -19.67 | 534.51 | -2.79 | 0.00
333 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.95 | -29.60 | -108.04 | 29.61 | 500.52 | -19.31 | 500.89 | 0.97 | 0.00
334 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -1.00 | 29.61 | -109.37 | 29.63 | -534.15 | -20.24 | 534.53 | -2.77 | 0.00
335 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.90 | -29.60 | -83.82 | 29.62 | 527.78 | -20.94 | 528.20 | 0.79 | 0.00
336 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.97 | 29.61 | -85.19 | 29.63 | -502.17 | -22.27 | 502.66 | -2.47 | 0.00
337 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.95 | -29.60 | -83.82 | 29.62 | 527.79 | -21.98 | 528.25 | 0.67 | 0.00
338 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -1.00 | 29.62 | -85.20 | 29.63 | -502.18 | -22.80 | 502.69 | -2.46 | 0.00
339 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.36 | -26.24 | -129.33 | 26.25 | 440.57 | -5.39 | 440.60 | 2.07 | 0.00
340 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.46 | 26.25 | -130.89 | 26.25 | -475.27 | -7.58 | 475.33 | -2.69 | 0.00
341 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.40 | -26.24 | -129.33 | 26.25 | 440.58 | -6.55 | 440.63 | 1.95 | 0.00
342 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.48 | 26.25 | -130.89 | 26.25 | -475.27 | -8.15 | 475.34 | -2.68 | 0.00
343 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.36 | -26.25 | -95.90 | 26.25 | 453.83 | -7.43 | 453.89 | 1.88 | 0.00
344 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.46 | 26.25 | -97.50 | 26.26 | -457.87 | -9.43 | 457.96 | -2.51 | 0.00
345 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.40 | -26.25 | -95.90 | 26.25 | 453.84 | -8.51 | 453.92 | 1.76 | 0.00
346 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.48 | 26.25 | -97.50 | 26.26 | -457.87 | -9.96 | 457.98 | -2.50 | 0.00
347 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.36 | -26.24 | -107.85 | 26.25 | 440.11 | -5.42 | 440.14 | 2.06 | 0.00
348 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.46 | 26.25 | -109.42 | 26.25 | -473.58 | -7.54 | 473.64 | -2.69 | 0.00
349 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.40 | -26.24 | -107.85 | 26.25 | 440.12 | -6.55 | 440.17 | 1.94 | 0.00
350 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.48 | 26.25 | -109.41 | 26.25 | -473.59 | -8.10 | 473.66 | -2.68 | 0.00
351 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.36 | -26.25 | -83.77 | 26.26 | 467.53 | -9.22 | 467.62 | 1.71 | 0.00
352 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.46 | 26.26 | -85.39 | 26.26 | -442.16 | -11.12 | 442.30 | -2.34 | 0.00
353 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.41 | -26.25 | -83.77 | 26.26 | 467.54 | -10.26 | 467.65 | 1.60 | 0.00
354 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.48 | 26.26 | -85.39 | 26.26 | -442.17 | -11.63 | 442.32 | -2.33 | 0.00
355 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.36 | -26.25 | -104.48 | 26.25 | 444.00 | -6.02 | 444.04 | 2.01 | 0.00
356 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.46 | 26.25 | -106.05 | 26.25 | -469.12 | -8.10 | 469.19 | -2.63 | 0.00
357 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.40 | -26.25 | -104.48 | 26.25 | 444.02 | -7.13 | 444.07 | 1.89 | 0.00
358 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.48 | 26.25 | -106.05 | 26.25 | -469.13 | -8.65 | 469.21 | -2.62 | 0.00
359 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.25 | -0.04 | -130.03 | 0.25 | -17.07 | -2.65 | 17.28 | -0.25 | 0.00
360 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.25 | -0.04 | -130.03 | 0.25 | -17.07 | -2.65 | 17.28 | -0.25 | 0.00
361 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.36 | -2.94 | -133.93 | 2.96 | 26.73 | -4.68 | 27.14 | -0.14 | 0.00
362 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.38 | 2.96 | -134.05 | 2.98 | -77.66 | -5.10 | 77.83 | -0.78 | 0.00
363 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.36 | -2.96 | -133.97 | 2.98 | 26.74 | -4.77 | 27.16 | -0.15 | 0.00
364 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.38 | 2.95 | -134.09 | 2.97 | -79.28 | -5.17 | 79.45 | -0.78 | 0.00
365 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.36 | -2.90 | -133.92 | 2.92 | 36.27 | -4.72 | 36.58 | 0.09 | 0.00
366 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.38 | 3.00 | -134.04 | 3.03 | -68.24 | -5.13 | 68.43 | -0.53 | 0.00
367 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.11 | -23.60 | -116.28 | 23.60 | 398.78 | 0.06 | 398.78 | 2.56 | 0.00
368 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.18 | 23.60 | -117.61 | 23.60 | -427.04 | -1.45 | 427.04 | -2.65 | 0.00
369 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.65 | -30.36 | -124.32 | 30.36 | 522.82 | -13.32 | 522.99 | 1.54 | 0.00
370 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.40 | -125.67 | 30.41 | -544.70 | -15.17 | 544.91 | -2.88 | 0.00
371 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.75 | -30.36 | -124.34 | 30.37 | 522.84 | -15.74 | 523.08 | 1.27 | 0.00
372 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.79 | 30.40 | -125.68 | 30.41 | -544.74 | -16.41 | 544.98 | -2.84 | 0.00
373 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.65 | -30.36 | -95.98 | 30.37 | 529.60 | -14.05 | 529.79 | 1.45 | 0.00
374 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.40 | -97.34 | 30.41 | -534.09 | -15.80 | 534.33 | -2.79 | 0.00
375 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.75 | -30.36 | -95.98 | 30.37 | 529.65 | -16.35 | 529.90 | 1.18 | 0.00
376 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.79 | 30.40 | -97.34 | 30.41 | -534.11 | -16.97 | 534.38 | -2.76 | 0.00
377 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.65 | -30.36 | -102.84 | 30.36 | 522.15 | -13.10 | 522.31 | 1.55 | 0.00
378 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.40 | -104.19 | 30.41 | -542.86 | -14.90 | 543.07 | -2.90 | 0.00
379 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.75 | -30.36 | -102.86 | 30.37 | 522.17 | -15.45 | 522.40 | 1.28 | 0.00
380 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.79 | 30.40 | -104.21 | 30.41 | -542.90 | -16.10 | 543.13 | -2.86 | 0.00
381 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.65 | -30.36 | -89.02 | 30.37 | 537.10 | -14.95 | 537.30 | 1.35 | 0.00
382 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.74 | 30.40 | -90.37 | 30.41 | -525.26 | -16.64 | 525.53 | -2.69 | 0.00
383 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.75 | -30.36 | -88.99 | 30.37 | 537.17 | -17.19 | 537.45 | 1.09 | 0.00
384 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.79 | 30.40 | -90.36 | 30.41 | -525.27 | -17.79 | 525.57 | -2.66 | 0.00
385 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 0.11 | -26.84 | -124.33 | 26.84 | 458.83 | 4.61 | 458.86 | 3.00 | 0.00
386 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.09 | 26.88 | -125.94 | 26.88 | -481.03 | 0.48 | 481.03 | -2.89 | 0.00
387 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.09 | -26.84 | -124.36 | 26.84 | 458.87 | 0.63 | 458.87 | 2.65 | 0.00
388 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.12 | 26.88 | -125.96 | 26.88 | -481.08 | -0.41 | 481.08 | -2.89 | 0.00
389 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 0.11 | -26.84 | -95.86 | 26.84 | 465.93 | 2.89 | 465.94 | 2.84 | 0.00
390 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.07 | 26.88 | -97.46 | 26.88 | -470.55 | -0.68 | 470.55 | -2.77 | 0.00
391 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.02 | -26.85 | -95.86 | 26.85 | 466.01 | 0.11 | 466.01 | 2.56 | 0.00
392 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.12 | 26.88 | -97.46 | 26.88 | -470.59 | -1.86 | 470.59 | -2.75 | 0.00
393 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 0.11 | -26.84 | -102.85 | 26.84 | 458.32 | 4.29 | 458.34 | 2.97 | 0.00
394 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.08 | 26.88 | -104.47 | 26.88 | -479.34 | 0.34 | 479.34 | -2.88 | 0.00
395 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.09 | -26.84 | -102.88 | 26.84 | 458.36 | 0.42 | 458.36 | 2.64 | 0.00
396 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.12 | 26.88 | -104.48 | 26.88 | -479.39 | -0.59 | 479.39 | -2.87 | 0.00
397 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 0.11 | -26.85 | -88.76 | 26.85 | 473.60 | 1.56 | 473.60 | 2.72 | 0.00
398 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.07 | 26.88 | -90.34 | 26.88 | -461.71 | -1.92 | 461.71 | -2.66 | 0.00
399 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.07 | -26.85 | -88.73 | 26.85 | 473.71 | -1.93 | 473.71 | 2.40 | 0.00
400 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.12 | 26.88 | -90.32 | 26.88 | -461.72 | -3.07 | 461.73 | -2.64 | 0.00
401 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 0.11 | -26.84 | -100.88 | 26.84 | 460.48 | 3.89 | 460.49 | 2.93 | 0.00
402 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.07 | 26.88 | -102.49 | 26.88 | -476.85 | 0.24 | 476.85 | -2.86 | 0.00
403 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.07 | -26.85 | -100.90 | 26.85 | 460.53 | 0.26 | 460.53 | 2.61 | 0.00
404 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.12 | 26.88 | -102.50 | 26.88 | -476.90 | -0.96 | 476.90 | -2.84 | 0.00
405 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.07 | -0.03 | -126.72 | 0.08 | -12.86 | 2.45 | 13.09 | 0.05 | 0.00
406 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.07 | -0.03 | -126.72 | 0.08 | -12.86 | 2.45 | 13.09 | 0.05 | 0.00
407 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 0.14 | -2.91 | -129.48 | 2.91 | 32.78 | 6.47 | 33.41 | 0.51 | 0.00
408 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.03 | 2.97 | -129.61 | 2.97 | -71.00 | 4.02 | 71.11 | -0.26 | 0.00
409 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.01 | -2.92 | -129.49 | 2.92 | 33.18 | 4.56 | 33.49 | 0.49 | 0.00
410 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.04 | 2.95 | -129.62 | 2.95 | -72.18 | 3.96 | 72.29 | -0.27 | 0.00
411 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 0.14 | -2.87 | -129.49 | 2.88 | 39.61 | 6.49 | 40.13 | 0.40 | 0.00
412 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.03 | 3.01 | -129.63 | 3.01 | -64.30 | 4.04 | 64.43 | -0.34 | 0.00
413 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | 0.28 | -24.20 | -112.17 | 24.20 | 416.02 | 8.22 | 416.10 | 3.27 | 0.00
414 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | 0.10 | 24.23 | -113.55 | 24.23 | -434.08 | 4.48 | 434.10 | -2.78 | 0.00
415 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.55 | -34.28 | -205.03 | 34.28 | 617.46 | -10.01 | 617.54 | 2.71 | 0.00
416 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.47 | 34.08 | -206.34 | 34.08 | -652.86 | -7.76 | 652.90 | -4.26 | 0.00
417 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.59 | -34.28 | -205.02 | 34.28 | 617.46 | -11.10 | 617.56 | 2.62 | 0.00
418 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.54 | 34.08 | -206.33 | 34.09 | -652.85 | -9.42 | 652.92 | -4.27 | 0.00
419 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.55 | -34.28 | -155.87 | 34.28 | 633.26 | -12.71 | 633.39 | 2.55 | 0.00
420 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.47 | 34.08 | -157.22 | 34.09 | -632.91 | -10.56 | 633.00 | -4.09 | 0.00
421 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.59 | -34.28 | -155.87 | 34.28 | 633.26 | -13.75 | 633.41 | 2.46 | 0.00
422 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.54 | 34.08 | -157.22 | 34.09 | -632.91 | -12.13 | 633.03 | -4.10 | 0.00
423 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.55 | -34.28 | -170.26 | 34.28 | 616.74 | -9.98 | 616.82 | 2.71 | 0.00
424 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.47 | 34.08 | -171.57 | 34.08 | -650.92 | -7.79 | 650.97 | -4.26 | 0.00
425 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.59 | -34.28 | -170.26 | 34.28 | 616.74 | -11.05 | 616.84 | 2.62 | 0.00
426 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.54 | 34.08 | -171.57 | 34.09 | -650.92 | -9.41 | 650.98 | -4.27 | 0.00
427 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.55 | -34.28 | -141.24 | 34.29 | 649.82 | -15.28 | 650.00 | 2.39 | 0.00
428 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.47 | 34.09 | -142.63 | 34.09 | -614.86 | -13.16 | 615.00 | -3.93 | 0.00
429 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.59 | -34.28 | -141.25 | 34.29 | 649.82 | -16.29 | 650.02 | 2.31 | 0.00
430 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.54 | 34.09 | -142.64 | 34.09 | -614.87 | -14.70 | 615.05 | -3.94 | 0.00
431 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.21 | -30.99 | -204.79 | 30.99 | 553.71 | -1.47 | 553.71 | 2.87 | 0.00
432 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.16 | 30.79 | -206.35 | 30.79 | -589.04 | 0.30 | 589.04 | -3.55 | 0.00
433 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.25 | -30.99 | -204.78 | 30.99 | 553.70 | -2.53 | 553.71 | 2.79 | 0.00
434 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.21 | 30.79 | -206.35 | 30.79 | -589.04 | -0.95 | 589.04 | -3.58 | 0.00
435 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.21 | -30.99 | -155.73 | 30.99 | 569.64 | -4.58 | 569.66 | 2.71 | 0.00
436 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.14 | 30.79 | -157.35 | 30.79 | -569.44 | -2.50 | 569.45 | -3.40 | 0.00
437 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.26 | -30.99 | -155.73 | 30.99 | 569.64 | -5.58 | 569.66 | 2.63 | 0.00
438 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.21 | 30.79 | -157.35 | 30.79 | -569.44 | -4.05 | 569.46 | -3.42 | 0.00
439 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.21 | -30.99 | -170.02 | 30.99 | 553.12 | -1.65 | 553.13 | 2.86 | 0.00
440 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.16 | 30.79 | -171.59 | 30.79 | -587.25 | 0.16 | 587.25 | -3.55 | 0.00
441 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.25 | -30.99 | -170.02 | 30.99 | 553.12 | -2.68 | 553.13 | 2.78 | 0.00
442 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.21 | 30.79 | -171.58 | 30.79 | -587.24 | -1.14 | 587.24 | -3.57 | 0.00
443 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.21 | -30.99 | -141.21 | 30.99 | 586.20 | -7.34 | 586.25 | 2.56 | 0.00
444 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.14 | 30.80 | -142.88 | 30.80 | -551.61 | -5.29 | 551.63 | -3.25 | 0.00
445 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.26 | -30.99 | -141.22 | 30.99 | 586.19 | -8.32 | 586.25 | 2.48 | 0.00
446 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.21 | 30.80 | -142.88 | 30.80 | -551.61 | -6.80 | 551.66 | -3.27 | 0.00
447 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.21 | -30.99 | -165.99 | 30.99 | 557.81 | -2.50 | 557.81 | 2.82 | 0.00
448 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.14 | 30.79 | -167.57 | 30.79 | -582.20 | -0.40 | 582.20 | -3.51 | 0.00
449 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.25 | -30.99 | -165.98 | 30.99 | 557.80 | -3.52 | 557.82 | 2.73 | 0.00
450 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.21 | 30.79 | -167.57 | 30.79 | -582.19 | -1.98 | 582.20 | -3.53 | 0.00
451 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.16 | -0.11 | -204.98 | 0.19 | -17.60 | 0.29 | 17.60 | -0.21 | 0.00
452 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.16 | -0.11 | -204.98 | 0.19 | -17.60 | 0.29 | 17.60 | -0.21 | 0.00
453 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.21 | -3.48 | -209.52 | 3.48 | 37.35 | -0.09 | 37.35 | 0.04 | 0.00
454 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.21 | 3.33 | -209.64 | 3.34 | -90.95 | 0.19 | 90.95 | -0.73 | 0.00
455 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.21 | -3.49 | -209.54 | 3.50 | 37.30 | -0.25 | 37.30 | 0.02 | 0.00
456 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.21 | 3.32 | -209.66 | 3.33 | -92.70 | 0.05 | 92.70 | -0.74 | 0.00
457 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.21 | -3.44 | -209.52 | 3.45 | 48.57 | 0.02 | 48.57 | 0.12 | 0.00
458 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.21 | 3.37 | -209.64 | 3.38 | -79.86 | 0.27 | 79.86 | -0.66 | 0.00
459 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.14 | -27.37 | -184.67 | 27.37 | 492.31 | 0.52 | 492.32 | 3.03 | 0.00
460 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.13 | 27.21 | -185.99 | 27.21 | -521.09 | 1.96 | 521.10 | -3.25 | 0.00
461 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.44 | -30.31 | -129.48 | 30.31 | 515.88 | -7.33 | 515.93 | 2.43 | 0.00
462 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.37 | 30.13 | -130.79 | 30.13 | -546.36 | -5.18 | 546.39 | -2.99 | 0.00
463 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.49 | -30.31 | -129.48 | 30.31 | 515.88 | -8.57 | 515.95 | 2.29 | 0.00
464 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.44 | 30.13 | -130.79 | 30.13 | -546.36 | -7.05 | 546.40 | -2.94 | 0.00
465 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.44 | -30.31 | -96.03 | 30.32 | 528.60 | -9.23 | 528.68 | 2.22 | 0.00
466 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.37 | 30.13 | -97.38 | 30.14 | -528.77 | -7.22 | 528.82 | -2.77 | 0.00
467 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.49 | -30.31 | -96.03 | 30.32 | 528.59 | -10.39 | 528.69 | 2.09 | 0.00
468 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.44 | 30.13 | -97.38 | 30.14 | -528.77 | -8.95 | 528.84 | -2.73 | 0.00
469 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.44 | -30.31 | -108.00 | 30.31 | 515.23 | -7.30 | 515.29 | 2.43 | 0.00
470 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.37 | 30.13 | -109.31 | 30.13 | -544.50 | -5.23 | 544.53 | -2.98 | 0.00
471 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.49 | -30.31 | -108.00 | 30.31 | 515.23 | -8.51 | 515.30 | 2.29 | 0.00
472 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.44 | 30.13 | -109.31 | 30.14 | -544.50 | -7.03 | 544.55 | -2.94 | 0.00
473 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.44 | -30.32 | -83.86 | 30.32 | 541.94 | -10.96 | 542.05 | 2.03 | 0.00
474 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.37 | 30.14 | -85.25 | 30.14 | -513.04 | -9.01 | 513.12 | -2.57 | 0.00
475 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.49 | -30.32 | -83.86 | 30.32 | 541.93 | -12.06 | 542.06 | 1.90 | 0.00
476 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.44 | 30.14 | -85.25 | 30.14 | -513.04 | -10.67 | 513.15 | -2.53 | 0.00
477 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.28 | -26.86 | -129.30 | 26.86 | 453.29 | -3.61 | 453.30 | 2.34 | 0.00
478 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.21 | 26.68 | -130.84 | 26.68 | -483.81 | -1.51 | 483.81 | -2.67 | 0.00
479 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.33 | -26.86 | -129.30 | 26.86 | 453.29 | -4.85 | 453.31 | 2.21 | 0.00
480 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.29 | 26.68 | -130.84 | 26.68 | -483.81 | -3.40 | 483.82 | -2.63 | 0.00
481 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.28 | -26.86 | -95.90 | 26.86 | 466.26 | -5.77 | 466.30 | 2.13 | 0.00
482 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.21 | 26.68 | -97.50 | 26.68 | -466.62 | -3.80 | 466.64 | -2.45 | 0.00
483 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.34 | -26.86 | -95.90 | 26.86 | 466.26 | -6.92 | 466.31 | 2.01 | 0.00
484 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.29 | 26.68 | -97.50 | 26.68 | -466.63 | -5.56 | 466.66 | -2.43 | 0.00
485 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.28 | -26.86 | -107.82 | 26.86 | 452.79 | -3.69 | 452.81 | 2.33 | 0.00
486 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.21 | 26.68 | -109.37 | 26.68 | -482.10 | -1.67 | 482.11 | -2.65 | 0.00
487 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.33 | -26.86 | -107.82 | 26.86 | 452.79 | -4.90 | 452.82 | 2.20 | 0.00
488 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.29 | 26.68 | -109.37 | 26.68 | -482.11 | -3.50 | 482.12 | -2.62 | 0.00
489 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.28 | -26.87 | -83.80 | 26.87 | 479.71 | -7.63 | 479.77 | 1.95 | 0.00
490 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.21 | 26.69 | -85.44 | 26.69 | -451.15 | -5.71 | 451.18 | -2.27 | 0.00
491 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.34 | -26.87 | -83.80 | 26.87 | 479.71 | -8.73 | 479.79 | 1.83 | 0.00
492 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.29 | 26.69 | -85.44 | 26.69 | -451.15 | -7.40 | 451.21 | -2.25 | 0.00
493 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.28 | -26.86 | -104.46 | 26.86 | 456.62 | -4.31 | 456.64 | 2.27 | 0.00
494 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.21 | 26.68 | -106.02 | 26.68 | -477.71 | -2.29 | 477.71 | -2.59 | 0.00
495 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.33 | -26.86 | -104.45 | 26.86 | 456.62 | -5.50 | 456.65 | 2.14 | 0.00
496 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.29 | 26.68 | -106.02 | 26.68 | -477.71 | -4.11 | 477.73 | -2.56 | 0.00
497 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.14 | -0.08 | -130.12 | 0.16 | -16.24 | 0.45 | 16.24 | -0.08 | 0.00
498 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.14 | -0.08 | -130.12 | 0.16 | -16.24 | 0.45 | 16.24 | -0.08 | 0.00
499 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.18 | -3.07 | -134.05 | 3.07 | 29.15 | 0.21 | 29.16 | 0.18 | 0.00
500 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.18 | 2.96 | -134.17 | 2.96 | -77.64 | 0.56 | 77.64 | -0.46 | 0.00
501 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.18 | -3.08 | -134.08 | 3.08 | 29.18 | 0.07 | 29.18 | 0.16 | 0.00
502 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.19 | 2.94 | -134.20 | 2.95 | -79.27 | 0.45 | 79.27 | -0.47 | 0.00
503 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.18 | -3.03 | -134.05 | 3.03 | 38.92 | 0.21 | 38.92 | 0.24 | 0.00
504 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.19 | 2.99 | -134.17 | 3.00 | -68.00 | 0.50 | 68.00 | -0.40 | 0.00
505 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.17 | -24.17 | -116.25 | 24.17 | 410.56 | -1.53 | 410.56 | 2.42 | 0.00
506 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.12 | 24.02 | -117.57 | 24.02 | -435.37 | 0.10 | 435.37 | -2.57 | 0.00
507 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.07 | -29.39 | -131.85 | 29.39 | 509.73 | 1.06 | 509.73 | 2.17 | 0.00
508 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.25 | 29.52 | -133.22 | 29.52 | -550.44 | -4.36 | 550.46 | -1.78 | 0.00
509 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.04 | -29.39 | -131.85 | 29.39 | 509.74 | 1.62 | 509.74 | 2.23 | 0.00
510 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.20 | 29.52 | -133.22 | 29.52 | -550.45 | -3.11 | 550.46 | -1.81 | 0.00
511 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 0.08 | -29.40 | -97.31 | 29.40 | 523.53 | 1.16 | 523.53 | 2.08 | 0.00
512 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.25 | 29.52 | -98.67 | 29.52 | -530.69 | -5.72 | 530.72 | -1.62 | 0.00
513 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 0.11 | -29.40 | -97.31 | 29.40 | 523.54 | 1.67 | 523.54 | 2.15 | 0.00
514 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.20 | 29.52 | -98.67 | 29.52 | -530.71 | -4.57 | 530.73 | -1.65 | 0.00
515 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.07 | -29.39 | -110.10 | 29.39 | 509.09 | 0.90 | 509.09 | 2.15 | 0.00
516 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.25 | 29.52 | -111.47 | 29.52 | -548.43 | -4.34 | 548.45 | -1.78 | 0.00
517 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.04 | -29.39 | -110.10 | 29.39 | 509.10 | 1.44 | 509.10 | 2.22 | 0.00
518 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.20 | 29.52 | -111.46 | 29.52 | -548.44 | -3.13 | 548.45 | -1.81 | 0.00
519 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.07 | -29.40 | -84.32 | 29.40 | 537.91 | -2.22 | 537.92 | 1.81 | 0.00
520 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.25 | 29.52 | -85.66 | 29.52 | -513.01 | -6.93 | 513.05 | -1.48 | 0.00
521 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.04 | -29.40 | -84.32 | 29.40 | 537.91 | -1.73 | 537.91 | 1.88 | 0.00
522 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.20 | 29.52 | -85.66 | 29.52 | -513.03 | -5.83 | 513.06 | -1.50 | 0.00
523 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 0.29 | -27.20 | -131.59 | 27.20 | 472.26 | 8.11 | 472.33 | 2.48 | 0.00
524 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.14 | 27.29 | -133.21 | 27.29 | -512.23 | -1.53 | 512.23 | -1.58 | 0.00
525 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -27.20 | -131.59 | 27.20 | 472.28 | 8.69 | 472.36 | 2.55 | 0.00
526 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.15 | 27.29 | -133.20 | 27.29 | -512.24 | -0.89 | 512.24 | -1.57 | 0.00
527 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 0.29 | -27.20 | -97.19 | 27.20 | 486.17 | 5.77 | 486.21 | 2.26 | 0.00
528 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.10 | 27.30 | -98.79 | 27.30 | -492.87 | -2.30 | 492.87 | -1.46 | 0.00
529 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -27.20 | -97.19 | 27.20 | 486.18 | 6.31 | 486.22 | 2.33 | 0.00
530 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.05 | 27.30 | -98.79 | 27.30 | -492.89 | -1.10 | 492.89 | -1.48 | 0.00
531 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 0.29 | -27.20 | -109.84 | 27.20 | 471.72 | 7.73 | 471.78 | 2.45 | 0.00
532 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.14 | 27.29 | -111.45 | 27.29 | -510.31 | -1.61 | 510.31 | -1.57 | 0.00
533 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -27.20 | -109.84 | 27.20 | 471.73 | 8.30 | 471.81 | 2.52 | 0.00
534 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.15 | 27.29 | -111.45 | 27.29 | -510.33 | -0.99 | 510.33 | -1.56 | 0.00
535 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 0.29 | -27.20 | -84.34 | 27.21 | 500.56 | 4.02 | 500.58 | 2.09 | 0.00
536 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.11 | 27.30 | -85.92 | 27.30 | -475.47 | -3.88 | 475.49 | -1.30 | 0.00
537 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -27.21 | -84.34 | 27.21 | 500.57 | 4.54 | 500.59 | 2.15 | 0.00
538 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.11 | 27.30 | -85.92 | 27.30 | -475.50 | -3.66 | 475.51 | -1.27 | 0.00
539 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 0.29 | -27.20 | -106.27 | 27.20 | 475.83 | 7.15 | 475.88 | 2.40 | 0.00
540 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.11 | 27.29 | -107.88 | 27.29 | -505.35 | -1.26 | 505.36 | -1.57 | 0.00
541 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -27.20 | -106.27 | 27.20 | 475.84 | 7.71 | 475.90 | 2.46 | 0.00
542 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.11 | 27.29 | -107.87 | 27.29 | -505.37 | -1.19 | 505.37 | -1.52 | 0.00
543 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.06 | -0.02 | -131.45 | 0.06 | -17.85 | 2.37 | 18.01 | 0.11 | 0.00
544 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.06 | -0.02 | -131.45 | 0.06 | -17.85 | 2.37 | 18.01 | 0.11 | 0.00
545 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 0.20 | -2.81 | -135.10 | 2.82 | 25.63 | 7.65 | 26.75 | 0.54 | 0.00
546 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.04 | 2.89 | -135.23 | 2.89 | -77.48 | 3.52 | 77.56 | -0.09 | 0.00
547 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 0.20 | -2.84 | -135.15 | 2.84 | 25.76 | 7.80 | 26.91 | 0.56 | 0.00
548 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.04 | 2.87 | -135.28 | 2.87 | -78.63 | 3.55 | 78.71 | -0.09 | 0.00
549 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | 0.20 | -2.76 | -135.10 | 2.77 | 33.38 | 7.65 | 34.25 | 0.39 | 0.00
550 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.04 | 2.94 | -135.23 | 2.94 | -69.81 | 3.53 | 69.90 | -0.19 | 0.00
551 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:g | 0.39 | -24.31 | -118.31 | 24.31 | 424.59 | 10.00 | 424.70 | 2.60 | 0.00
552 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.08 | 24.38 | -119.69 | 24.38 | -457.14 | 0.66 | 457.14 | -1.54 | 0.00
553 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | -0.51 | -28.84 | -128.53 | 28.84 | 501.59 | -11.71 | 501.72 | 0.36 | 0.00
554 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | -0.67 | 28.42 | -129.85 | 28.43 | -522.55 | -15.05 | 522.77 | -1.67 | 0.00
555 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | -0.50 | -28.84 | -128.53 | 28.84 | 501.58 | -11.49 | 501.71 | 0.38 | 0.00
556 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | -0.64 | 28.42 | -129.86 | 28.43 | -522.56 | -14.50 | 522.76 | -1.67 | 0.00
557 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | -0.51 | -28.84 | -97.29 | 28.84 | 511.41 | -12.27 | 511.55 | 0.28 | 0.00
558 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | -0.67 | 28.42 | -98.64 | 28.43 | -507.91 | -15.39 | 508.15 | -1.60 | 0.00
559 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | -0.50 | -28.84 | -97.29 | 28.84 | 511.40 | -12.07 | 511.54 | 0.31 | 0.00
560 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | -0.64 | 28.42 | -98.64 | 28.43 | -507.92 | -14.88 | 508.14 | -1.61 | 0.00
561 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | -0.51 | -28.84 | -106.78 | 28.84 | 500.96 | -11.44 | 501.09 | 0.37 | 0.00
562 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | -0.67 | 28.42 | -108.10 | 28.43 | -520.62 | -14.69 | 520.82 | -1.69 | 0.00
563 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | -0.50 | -28.84 | -106.78 | 28.84 | 500.96 | -11.23 | 501.08 | 0.40 | 0.00
564 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | -0.64 | 28.42 | -108.10 | 28.43 | -520.62 | -14.15 | 520.82 | -1.70 | 0.00
565 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | -0.51 | -28.84 | -87.65 | 28.85 | 521.86 | -13.03 | 522.02 | 0.20 | 0.00
566 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | -0.67 | 28.43 | -89.03 | 28.43 | -495.18 | -16.03 | 495.44 | -1.52 | 0.00
567 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | -0.50 | -28.84 | -87.65 | 28.85 | 521.85 | -12.83 | 522.01 | 0.23 | 0.00
568 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | -0.64 | 28.43 | -89.03 | 28.43 | -495.19 | -15.53 | 495.43 | -1.52 | 0.00
569 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | -0.12 | -26.88 | -128.37 | 26.88 | 469.13 | -0.77 | 469.13 | 1.28 | 0.00
570 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.46 | -129.93 | 26.46 | -489.93 | -3.03 | 489.94 | -1.74 | 0.00
571 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | -0.12 | -26.88 | -128.37 | 26.88 | 469.13 | -0.64 | 469.13 | 1.31 | 0.00
572 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | -0.20 | 26.46 | -129.93 | 26.46 | -489.95 | -2.46 | 489.95 | -1.74 | 0.00
573 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | -0.05 | -26.88 | -97.16 | 26.88 | 479.06 | -0.91 | 479.06 | 1.22 | 0.00
574 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.46 | -98.76 | 26.46 | -475.54 | -4.18 | 475.56 | -1.62 | 0.00
575 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | -0.04 | -26.88 | -97.16 | 26.88 | 479.05 | -0.69 | 479.05 | 1.25 | 0.00
576 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | -0.19 | 26.46 | -98.76 | 26.46 | -475.55 | -3.65 | 475.57 | -1.62 | 0.00
577 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.12 | -26.88 | -106.61 | 26.88 | 468.59 | -0.87 | 468.59 | 1.27 | 0.00
578 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.46 | -108.17 | 26.46 | -488.08 | -3.06 | 488.09 | -1.73 | 0.00
579 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.12 | -26.88 | -106.61 | 26.88 | 468.59 | -0.74 | 468.59 | 1.30 | 0.00
580 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | -0.20 | 26.46 | -108.17 | 26.46 | -488.10 | -2.51 | 488.10 | -1.74 | 0.00
581 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | -0.09 | -26.88 | -87.56 | 26.89 | 489.53 | -2.85 | 489.54 | 1.06 | 0.00
582 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.46 | -89.20 | 26.46 | -462.97 | -5.21 | 463.00 | -1.52 | 0.00
583 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | -0.09 | -26.88 | -87.56 | 26.88 | 489.53 | -2.78 | 489.54 | 1.08 | 0.00
584 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | -0.19 | 26.46 | -89.20 | 26.47 | -462.98 | -4.70 | 463.01 | -1.52 | 0.00
585 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | -0.09 | -26.88 | -103.95 | 26.88 | 471.56 | -0.85 | 471.56 | 1.26 | 0.00
586 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | -0.22 | 26.46 | -105.52 | 26.46 | -484.52 | -3.39 | 484.54 | -1.70 | 0.00
587 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | -0.09 | -26.88 | -103.95 | 26.88 | 471.56 | -0.78 | 471.56 | 1.28 | 0.00
588 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | -0.20 | 26.46 | -105.52 | 26.46 | -484.54 | -2.85 | 484.55 | -1.71 | 0.00
589 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.10 | -0.12 | -129.30 | 0.16 | -12.85 | 1.49 | 12.94 | -0.03 | 0.00
590 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.10 | -0.12 | -129.30 | 0.16 | -12.85 | 1.49 | 12.94 | -0.03 | 0.00
591 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.06 | -2.89 | -132.28 | 2.89 | 31.26 | 3.42 | 31.44 | 0.19 | 0.00
592 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.09 | 2.60 | -132.39 | 2.60 | -67.28 | 2.62 | 67.33 | -0.29 | 0.00
593 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.06 | -2.90 | -132.29 | 2.90 | 31.41 | 3.32 | 31.58 | 0.18 | 0.00
594 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.09 | 2.59 | -132.41 | 2.59 | -68.30 | 2.48 | 68.34 | -0.31 | 0.00
595 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.04 | -2.86 | -132.28 | 2.86 | 37.99 | 3.68 | 38.17 | 0.19 | 0.00
596 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.08 | 2.63 | -132.39 | 2.63 | -60.64 | 2.88 | 60.71 | -0.26 | 0.00
597 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:g | 0.25 | -23.98 | -115.65 | 23.98 | 420.56 | 7.78 | 420.63 | 2.08 | 0.00
598 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:g | 0.09 | 23.62 | -116.97 | 23.62 | -437.22 | 4.69 | 437.25 | -1.81 | 0.00
599 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1:g | 0.78 | -28.26 | -130.47 | 28.27 | 487.33 | 23.09 | 487.88 | 4.25 | 0.00
600 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1:g | 0.63 | 27.95 | -131.82 | 27.96 | -515.23 | 20.02 | 515.62 | -2.48 | 0.00
601 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1:g | 0.78 | -28.26 | -130.47 | 28.27 | 487.34 | 23.26 | 487.89 | 4.27 | 0.00
602 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1:g | 0.65 | 27.95 | -131.81 | 27.96 | -515.23 | 20.46 | 515.64 | -2.49 | 0.00
603 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1:g | 0.78 | -28.26 | -97.30 | 28.27 | 499.46 | 19.73 | 499.85 | 3.93 | 0.00
604 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1:g | 0.63 | 27.96 | -98.66 | 27.96 | -497.87 | 16.91 | 498.16 | -2.21 | 0.00
605 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1:g | 0.78 | -28.26 | -97.30 | 28.27 | 499.45 | 19.89 | 499.85 | 3.95 | 0.00
606 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1:g | 0.65 | 27.96 | -98.66 | 27.96 | -497.87 | 17.32 | 498.17 | -2.21 | 0.00
607 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1:g | 0.78 | -28.26 | -108.72 | 28.27 | 486.75 | 22.20 | 487.26 | 4.18 | 0.00
608 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1:g | 0.63 | 27.95 | -110.06 | 27.96 | -513.31 | 19.23 | 513.67 | -2.42 | 0.00
609 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1:g | 0.78 | -28.26 | -108.72 | 28.27 | 486.75 | 22.36 | 487.27 | 4.20 | 0.00
610 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1:g | 0.65 | 27.95 | -110.06 | 27.96 | -513.31 | 19.66 | 513.69 | -2.42 | 0.00
611 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1:g | 0.78 | -28.27 | -85.70 | 28.28 | 512.13 | 17.49 | 512.43 | 3.70 | 0.00
612 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1:g | 0.63 | 27.96 | -87.07 | 27.97 | -482.44 | 14.81 | 482.67 | -2.02 | 0.00
613 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1:g | 0.78 | -28.27 | -85.71 | 28.28 | 512.13 | 17.64 | 512.43 | 3.72 | 0.00
614 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1:g | 0.65 | 27.96 | -87.07 | 27.97 | -482.44 | 15.20 | 482.68 | -2.02 | 0.00
615 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1:g | 0.30 | -26.48 | -130.28 | 26.48 | 458.51 | 10.34 | 458.63 | 2.55 | 0.00
616 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1:g | 0.16 | 26.16 | -131.86 | 26.16 | -486.28 | 7.42 | 486.33 | -1.76 | 0.00
617 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -26.48 | -130.28 | 26.48 | 458.51 | 10.51 | 458.63 | 2.57 | 0.00
618 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1:g | 0.18 | 26.16 | -131.86 | 26.16 | -486.28 | 7.84 | 486.34 | -1.76 | 0.00
619 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1:g | 0.30 | -26.48 | -97.18 | 26.48 | 470.75 | 7.95 | 470.81 | 2.33 | 0.00
620 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1:g | 0.16 | 26.17 | -98.78 | 26.17 | -469.15 | 5.27 | 469.18 | -1.57 | 0.00
621 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -26.48 | -97.18 | 26.48 | 470.74 | 8.11 | 470.81 | 2.35 | 0.00
622 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1:g | 0.18 | 26.17 | -98.78 | 26.17 | -469.15 | 5.66 | 469.19 | -1.57 | 0.00
623 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1:g | 0.30 | -26.48 | -108.52 | 26.48 | 458.00 | 9.87 | 458.11 | 2.51 | 0.00
624 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1:g | 0.16 | 26.16 | -110.11 | 26.16 | -484.43 | 7.04 | 484.48 | -1.73 | 0.00
625 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -26.48 | -108.52 | 26.48 | 458.00 | 10.03 | 458.11 | 2.53 | 0.00
626 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1:g | 0.18 | 26.16 | -110.11 | 26.16 | -484.43 | 7.45 | 484.49 | -1.73 | 0.00
627 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1:g | 0.30 | -26.49 | -85.65 | 26.49 | 483.46 | 6.23 | 483.50 | 2.16 | 0.00
628 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1:g | 0.16 | 26.17 | -87.26 | 26.17 | -453.88 | 3.67 | 453.90 | -1.42 | 0.00
629 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -26.48 | -85.65 | 26.49 | 483.46 | 6.38 | 483.50 | 2.18 | 0.00
630 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1:g | 0.18 | 26.17 | -87.27 | 26.17 | -453.89 | 4.05 | 453.90 | -1.42 | 0.00
631 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1:g | 0.30 | -26.48 | -105.32 | 26.48 | 461.62 | 9.30 | 461.72 | 2.46 | 0.00
632 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1:g | 0.16 | 26.16 | -106.91 | 26.16 | -480.09 | 6.52 | 480.14 | -1.68 | 0.00
633 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1:g | 0.31 | -26.48 | -105.32 | 26.48 | 461.62 | 9.47 | 461.72 | 2.48 | 0.00
634 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1:g | 0.18 | 26.16 | -106.91 | 26.17 | -480.09 | 6.92 | 480.14 | -1.68 | 0.00
635 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1:g | -0.13 | -0.12 | -130.33 | 0.18 | -14.30 | 0.01 | 14.30 | -0.03 | 0.00
636 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1:g | -0.13 | -0.12 | -130.33 | 0.18 | -14.30 | 0.01 | 14.30 | -0.03 | 0.00
637 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.18 | -2.82 | -133.65 | 2.83 | 27.89 | -0.04 | 27.89 | 0.16 | 0.00
638 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.16 | 2.61 | -133.77 | 2.61 | -69.39 | -0.13 | 69.39 | -0.27 | 0.00
639 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.16 | -2.83 | -133.67 | 2.83 | 27.93 | 0.41 | 27.93 | 0.15 | 0.00
640 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.16 | 2.60 | -133.80 | 2.60 | -70.49 | -0.27 | 70.49 | -0.29 | 0.00
641 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1:g | -0.18 | -2.79 | -133.65 | 2.80 | 35.44 | -0.07 | 35.44 | 0.18 | 0.00
642 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1:g | -0.16 | 2.63 | -133.77 | 2.64 | -61.92 | -0.15 | 61.92 | -0.24 | 0.00
643 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1:g | -0.03 | -23.60 | -117.28 | 23.60 | 410.74 | 2.10 | 410.74 | 1.68 | 0.00
644 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1:g | -0.11 | 23.34 | -118.62 | 23.34 | -433.40 | 0.49 | 433.40 | -1.48 | 0.00

## Tab_8
rowtext | str_no | structure_name | load_case | insulator_label | insulator_type | structure_attach_label | structure_attach_load_x | structure_attach_load_y | structure_attach_load_z | structure_attach_load_res
1 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | 4.537 | 8.164
2 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | 4.555 | 8.050
3 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | 4.672 | 8.304
4 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | 4.535 | 8.048
5 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.019 | -6.804 | 4.556 | 8.189
6 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | 4.668 | 8.056
7 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | 4.537 | 8.164
8 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | 4.555 | 8.050
9 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | 4.672 | 8.304
10 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | 4.535 | 8.049
11 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.018 | -6.804 | 4.556 | 8.189
12 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | 4.668 | 8.056
13 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | 0.375 | 6.798
14 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | 0.375 | 6.648
15 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | 0.376 | 6.875
16 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | 0.375 | 6.660
17 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.019 | -6.804 | 0.375 | 6.814
18 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | 0.376 | 6.577
19 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | 0.375 | 6.798
20 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | 0.375 | 6.648
21 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | 0.376 | 6.875
22 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | 0.375 | 6.660
23 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.018 | -6.804 | 0.375 | 6.814
24 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | 0.376 | 6.577
25 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | 4.461 | 8.122
26 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | 4.479 | 8.007
27 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | 4.596 | 8.261
28 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | 4.459 | 8.006
29 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.019 | -6.804 | 4.480 | 8.147
30 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | 4.592 | 8.012
31 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | 4.461 | 8.122
32 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | 4.479 | 8.007
33 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | 4.596 | 8.261
34 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | 4.459 | 8.006
35 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.018 | -6.804 | 4.480 | 8.147
36 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | 4.592 | 8.012
37 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | -3.777 | 7.768
38 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | -3.795 | 7.646
39 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | -3.912 | 7.901
40 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | -3.775 | 7.646
41 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.019 | -6.804 | -3.796 | 7.791
42 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | -3.908 | 7.641
43 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.013 | 6.787 | -3.777 | 7.768
44 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.062 | 6.637 | -3.795 | 7.646
45 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.011 | 6.865 | -3.912 | 7.901
46 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.056 | -6.649 | -3.775 | 7.646
47 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.018 | -6.804 | -3.796 | 7.791
48 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.046 | -6.566 | -3.908 | 7.641
49 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 4.512 | 7.134
50 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 4.528 | 7.042
51 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 4.646 | 7.449
52 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 4.509 | 7.030
53 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 4.530 | 7.165
54 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 4.640 | 7.220
55 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 4.511 | 7.133
56 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 4.528 | 7.042
57 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 4.646 | 7.449
58 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 4.509 | 7.030
59 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 4.530 | 7.165
60 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 4.640 | 7.220
61 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 0.375 | 5.538
62 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 0.375 | 5.406
63 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 0.376 | 5.834
64 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 0.375 | 5.406
65 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 0.375 | 5.564
66 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 0.376 | 5.544
67 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 0.375 | 5.538
68 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 0.375 | 5.406
69 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 0.376 | 5.834
70 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 0.375 | 5.406
71 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 0.375 | 5.564
72 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 0.376 | 5.544
73 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 4.436 | 7.086
74 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 4.452 | 6.993
75 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 4.570 | 7.401
76 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 4.433 | 6.981
77 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 4.454 | 7.118
78 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 4.564 | 7.172
79 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 4.435 | 7.086
80 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 4.452 | 6.993
81 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 4.570 | 7.401
82 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 4.433 | 6.981
83 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 4.454 | 7.118
84 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 4.564 | 7.172
85 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | -3.752 | 6.679
86 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | -3.768 | 6.579
87 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | -3.886 | 7.000
88 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | -3.749 | 6.568
89 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | -3.770 | 6.711
90 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | -3.880 | 6.757
91 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | -3.751 | 6.679
92 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | -3.768 | 6.579
93 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | -3.886 | 7.000
94 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | -3.749 | 6.568
95 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | -3.770 | 6.711
96 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | -3.880 | 6.757
97 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 3.289 | 6.431
98 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 3.301 | 6.323
99 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 3.386 | 6.735
100 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 3.287 | 6.316
101 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 3.303 | 6.460
102 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 3.382 | 6.484
103 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.035 | 5.526 | 3.289 | 6.431
104 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.015 | 5.393 | 3.301 | 6.323
105 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.038 | 5.822 | 3.386 | 6.735
106 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.007 | -5.393 | 3.287 | 6.316
107 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.028 | -5.552 | 3.303 | 6.460
108 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.004 | -5.532 | 3.382 | 6.484
109 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.010 | 0.037 | 4.478 | 4.478
110 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.004 | -0.045 | 4.491 | 4.491
111 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | -0.001 | 0.079 | 4.566 | 4.567
112 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.010 | 0.037 | 4.478 | 4.478
113 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.004 | -0.045 | 4.491 | 4.491
114 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | -0.001 | 0.079 | 4.566 | 4.567
115 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.011 | 0.906 | 6.915 | 6.974
116 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.008 | 0.570 | 5.306 | 5.336
117 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.005 | 0.742 | 5.398 | 5.449
118 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.021 | -0.770 | 6.913 | 6.956
119 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.001 | -0.695 | 5.307 | 5.352
120 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.001 | -0.524 | 5.396 | 5.421
121 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.009 | 0.683 | 5.291 | 5.335
122 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.008 | 0.570 | 5.306 | 5.336
123 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.007 | 0.985 | 7.058 | 7.126
124 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.016 | -0.581 | 5.290 | 5.321
125 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.001 | -0.695 | 5.307 | 5.352
126 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.001 | -0.694 | 7.055 | 7.089
127 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.009 | 0.683 | 5.291 | 5.335
128 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.010 | 0.756 | 6.935 | 6.976
129 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.005 | 0.742 | 5.398 | 5.449
130 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.016 | -0.581 | 5.290 | 5.321
131 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.002 | -0.921 | 6.936 | 6.997
132 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.001 | -0.524 | 5.396 | 5.421
133 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.036 | 5.266 | 3.647 | 6.405
134 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.001 | 5.159 | 3.659 | 6.325
135 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.040 | 5.538 | 3.757 | 6.693
136 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.000 | -5.158 | 3.644 | 6.315
137 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.038 | -5.289 | 3.662 | 6.433
138 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | -0.008 | -5.301 | 3.752 | 6.494
139 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | 4.523 | 8.041
140 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | 4.526 | 7.918
141 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | 4.654 | 8.191
142 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | 4.526 | 8.012
143 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | 4.533 | 8.137
144 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | 4.652 | 8.006
145 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | 4.523 | 8.041
146 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | 4.526 | 7.918
147 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | 4.654 | 8.191
148 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | 4.526 | 8.012
149 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | 4.533 | 8.137
150 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | 4.652 | 8.006
151 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | 0.375 | 6.659
152 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | 0.375 | 6.508
153 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | 0.376 | 6.750
154 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | 0.375 | 6.622
155 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | 0.375 | 6.768
156 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | 0.376 | 6.527
157 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | 0.375 | 6.659
158 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | 0.375 | 6.508
159 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | 0.376 | 6.750
160 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | 0.375 | 6.622
161 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | 0.375 | 6.768
162 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | 0.376 | 6.527
163 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | 4.447 | 7.999
164 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | 4.450 | 7.875
165 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | 4.578 | 8.148
166 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | 4.450 | 7.969
167 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | 4.457 | 8.095
168 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | 4.576 | 7.962
169 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | 4.447 | 7.999
170 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | 4.450 | 7.875
171 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | 4.578 | 8.148
172 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | 4.450 | 7.969
173 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | 4.457 | 8.095
174 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | 4.576 | 7.962
175 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | -3.763 | 7.639
176 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | -3.766 | 7.510
177 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | -3.894 | 7.784
178 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | -3.766 | 7.608
179 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | -3.773 | 7.739
180 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | -3.892 | 7.590
181 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.086 | 6.648 | -3.763 | 7.639
182 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.038 | 6.497 | -3.766 | 7.510
183 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.058 | 6.740 | -3.894 | 7.784
184 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.075 | -6.611 | -3.766 | 7.608
185 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.057 | -6.757 | -3.773 | 7.739
186 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.049 | -6.516 | -3.892 | 7.590
187 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 4.495 | 7.038
188 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 4.497 | 6.939
189 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 4.627 | 7.360
190 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 4.497 | 7.012
191 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 4.505 | 7.134
192 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 4.624 | 7.190
193 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 4.495 | 7.038
194 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 4.497 | 6.939
195 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 4.627 | 7.360
196 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 4.497 | 7.012
197 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 4.505 | 7.134
198 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 4.624 | 7.190
199 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 0.375 | 5.429
200 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 0.375 | 5.298
201 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 0.376 | 5.736
202 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 0.375 | 5.393
203 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 0.375 | 5.545
204 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 0.376 | 5.518
205 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 0.375 | 5.429
206 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 0.375 | 5.298
207 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 0.376 | 5.736
208 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 0.375 | 5.393
209 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 0.375 | 5.545
210 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 0.376 | 5.518
211 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 4.419 | 6.990
212 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 4.421 | 6.890
213 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 4.551 | 7.312
214 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 4.421 | 6.964
215 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 4.429 | 7.087
216 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 4.548 | 7.141
217 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 4.419 | 6.990
218 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 4.421 | 6.890
219 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 4.551 | 7.312
220 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 4.421 | 6.964
221 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 4.429 | 7.087
222 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 4.548 | 7.141
223 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | -3.735 | 6.579
224 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | -3.737 | 6.472
225 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | -3.867 | 6.907
226 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | -3.737 | 6.551
227 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | -3.745 | 6.681
228 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | -3.864 | 6.726
229 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | -3.735 | 6.579
230 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | -3.737 | 6.472
231 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | -3.867 | 6.907
232 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | -3.737 | 6.551
233 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | -3.745 | 6.681
234 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | -3.864 | 6.726
235 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 3.277 | 6.330
236 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 3.279 | 6.219
237 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 3.372 | 6.643
238 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 3.279 | 6.301
239 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 3.284 | 6.434
240 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 3.370 | 6.455
241 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.050 | 5.416 | 3.277 | 6.330
242 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.003 | 5.284 | 3.279 | 6.219
243 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.018 | 5.724 | 3.372 | 6.643
244 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.038 | -5.380 | 3.279 | 6.301
245 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.024 | -5.532 | 3.284 | 6.434
246 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.007 | -5.506 | 3.370 | 6.455
247 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | -0.017 | 0.011 | 4.447 | 4.447
248 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | -0.015 | -0.068 | 4.450 | 4.451
249 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | -0.009 | 0.060 | 4.532 | 4.532
250 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | -0.017 | 0.011 | 4.447 | 4.447
251 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | -0.015 | -0.068 | 4.450 | 4.451
252 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | -0.009 | 0.060 | 4.532 | 4.532
253 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.034 | 0.846 | 6.866 | 6.918
254 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.018 | 0.528 | 5.256 | 5.282
255 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.014 | 0.706 | 5.357 | 5.404
256 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.030 | -0.805 | 6.867 | 6.914
257 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.023 | -0.717 | 5.259 | 5.308
258 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.010 | -0.541 | 5.356 | 5.383
259 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.025 | 0.638 | 5.254 | 5.292
260 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.018 | 0.528 | 5.256 | 5.282
261 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.019 | 0.937 | 7.004 | 7.066
262 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.022 | -0.607 | 5.255 | 5.290
263 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.023 | -0.717 | 5.259 | 5.308
264 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.014 | -0.716 | 7.002 | 7.039
265 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.025 | 0.638 | 5.254 | 5.292
266 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.024 | 0.699 | 6.868 | 6.904
267 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.014 | 0.706 | 5.357 | 5.404
268 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.022 | -0.607 | 5.255 | 5.290
269 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.031 | -0.952 | 6.873 | 6.938
270 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.010 | -0.541 | 5.356 | 5.383
271 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.019 | 5.167 | 3.635 | 6.318
272 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.014 | 5.061 | 3.636 | 6.232
273 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.014 | 5.449 | 3.743 | 6.611
274 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | -0.010 | -5.138 | 3.636 | 6.295
275 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.002 | -5.264 | 3.642 | 6.402
276 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.019 | -5.270 | 3.740 | 6.463
277 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.299 | 5.456 | 4.256 | 6.926
278 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.293 | 4.905 | 3.868 | 6.253
279 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.249 | 5.576 | 4.341 | 7.071
280 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.349 | -4.931 | 4.224 | 6.502
281 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.328 | -5.450 | 3.882 | 6.699
282 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | 4.300 | 6.458
283 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.303 | 5.456 | 4.255 | 6.925
284 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.298 | 4.906 | 3.868 | 6.254
285 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.253 | 5.576 | 4.339 | 7.070
286 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.350 | -4.931 | 4.224 | 6.502
287 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.329 | -5.449 | 3.882 | 6.699
288 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | 4.300 | 6.459
289 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.299 | 5.456 | 0.373 | 5.477
290 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.293 | 4.905 | 0.370 | 4.927
291 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.249 | 5.576 | 0.373 | 5.594
292 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.349 | -4.931 | 0.372 | 4.957
293 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.328 | -5.450 | 0.370 | 5.472
294 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | 0.373 | 4.833
295 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.303 | 5.456 | 0.373 | 5.477
296 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.298 | 4.906 | 0.370 | 4.928
297 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.253 | 5.576 | 0.373 | 5.594
298 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.350 | -4.931 | 0.372 | 4.957
299 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.329 | -5.449 | 0.370 | 5.472
300 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | 0.373 | 4.833
301 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.299 | 5.456 | 4.180 | 6.879
302 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.293 | 4.905 | 3.792 | 6.207
303 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.249 | 5.576 | 4.265 | 7.025
304 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.349 | -4.931 | 4.148 | 6.453
305 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.328 | -5.450 | 3.806 | 6.655
306 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | 4.224 | 6.408
307 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.303 | 5.456 | 4.179 | 6.879
308 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.298 | 4.906 | 3.792 | 6.207
309 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.253 | 5.576 | 4.263 | 7.023
310 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.350 | -4.931 | 4.148 | 6.453
311 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.329 | -5.449 | 3.806 | 6.655
312 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | 4.224 | 6.408
313 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.299 | 5.456 | -3.496 | 6.487
314 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.293 | 4.905 | -3.108 | 5.814
315 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.249 | 5.576 | -3.581 | 6.632
316 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.349 | -4.931 | -3.464 | 6.036
317 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.328 | -5.450 | -3.122 | 6.289
318 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | -3.540 | 5.979
319 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.303 | 5.456 | -3.495 | 6.486
320 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.298 | 4.906 | -3.108 | 5.815
321 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.253 | 5.576 | -3.579 | 6.631
322 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.350 | -4.931 | -3.464 | 6.036
323 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.329 | -5.449 | -3.122 | 6.289
324 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.306 | -4.809 | -3.540 | 5.980
325 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 4.548 | 4.207 | 6.196
326 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.089 | 4.055 | 3.828 | 5.577
327 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.073 | 4.860 | 4.310 | 6.496
328 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.137 | -4.044 | 4.171 | 5.811
329 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 3.845 | 5.983
330 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.137 | -4.105 | 4.264 | 5.920
331 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.086 | 4.548 | 4.205 | 6.195
332 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.093 | 4.056 | 3.828 | 5.578
333 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.076 | 4.859 | 4.309 | 6.495
334 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.138 | -4.044 | 4.171 | 5.811
335 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 3.845 | 5.982
336 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.138 | -4.105 | 4.264 | 5.920
337 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 4.548 | 0.372 | 4.564
338 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.089 | 4.055 | 0.369 | 4.073
339 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.073 | 4.860 | 0.373 | 4.875
340 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.137 | -4.044 | 0.372 | 4.063
341 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 0.369 | 4.598
342 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.137 | -4.105 | 0.373 | 4.124
343 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.086 | 4.548 | 0.372 | 4.564
344 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.093 | 4.056 | 0.369 | 4.074
345 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.076 | 4.859 | 0.373 | 4.874
346 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.138 | -4.044 | 0.372 | 4.063
347 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 0.369 | 4.598
348 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.138 | -4.105 | 0.373 | 4.124
349 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 4.548 | 4.131 | 6.145
350 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.089 | 4.055 | 3.752 | 5.526
351 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.073 | 4.860 | 4.234 | 6.446
352 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.137 | -4.044 | 4.095 | 5.756
353 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 3.769 | 5.934
354 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.137 | -4.105 | 4.188 | 5.866
355 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.086 | 4.548 | 4.129 | 6.144
356 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.093 | 4.056 | 3.752 | 5.526
357 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.076 | 4.859 | 4.233 | 6.445
358 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.138 | -4.044 | 4.095 | 5.757
359 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 3.769 | 5.934
360 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.138 | -4.105 | 4.188 | 5.866
361 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 4.548 | -3.447 | 5.707
362 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.089 | 4.055 | -3.068 | 5.086
363 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.073 | 4.860 | -3.550 | 6.019
364 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.137 | -4.044 | -3.411 | 5.292
365 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | -3.085 | 5.525
366 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.137 | -4.105 | -3.504 | 5.399
367 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.086 | 4.548 | -3.445 | 5.706
368 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.093 | 4.056 | -3.068 | 5.086
369 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.076 | 4.859 | -3.549 | 6.018
370 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.138 | -4.044 | -3.411 | 5.292
371 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | -3.085 | 5.525
372 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.138 | -4.105 | -3.504 | 5.399
373 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 4.548 | 3.070 | 5.488
374 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.089 | 4.055 | 2.797 | 4.927
375 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.073 | 4.860 | 3.145 | 5.789
376 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.137 | -4.044 | 3.044 | 5.063
377 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 2.810 | 5.376
378 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.137 | -4.105 | 3.111 | 5.152
379 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.086 | 4.548 | 3.069 | 5.487
380 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.093 | 4.056 | 2.797 | 4.928
381 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.076 | 4.859 | 3.143 | 5.788
382 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.138 | -4.044 | 3.044 | 5.063
383 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.109 | -4.582 | 2.809 | 5.376
384 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.138 | -4.105 | 3.111 | 5.152
385 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.002 | 0.132 | 3.903 | 3.905
386 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | -0.003 | -0.133 | 3.659 | 3.662
387 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.002 | 0.192 | 3.956 | 3.961
388 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.002 | 0.132 | 3.903 | 3.905
389 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | -0.003 | -0.133 | 3.659 | 3.662
390 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.002 | 0.192 | 3.956 | 3.961
391 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.002 | 0.866 | 6.011 | 6.073
392 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.006 | 0.280 | 4.309 | 4.318
393 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.003 | 0.739 | 4.679 | 4.737
394 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.010 | -0.378 | 5.997 | 6.009
395 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.003 | -0.650 | 4.315 | 4.364
396 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.007 | -0.205 | 4.666 | 4.670
397 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.002 | 0.653 | 4.613 | 4.659
398 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.006 | 0.280 | 4.309 | 4.318
399 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.005 | 0.980 | 6.099 | 6.177
400 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.007 | -0.287 | 4.602 | 4.611
401 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.003 | -0.650 | 4.315 | 4.364
402 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.010 | -0.269 | 6.081 | 6.087
403 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.002 | 0.653 | 4.613 | 4.659
404 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.008 | 0.368 | 5.606 | 5.618
405 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.003 | 0.739 | 4.679 | 4.737
406 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.007 | -0.287 | 4.602 | 4.611
407 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.005 | -0.862 | 5.614 | 5.680
408 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.007 | -0.205 | 4.666 | 4.670
409 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.017 | 4.335 | 3.419 | 5.521
410 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.009 | 3.933 | 3.105 | 5.010
411 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.022 | 4.618 | 3.506 | 5.798
412 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.031 | -3.919 | 3.388 | 5.180
413 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | 0.000 | -4.368 | 3.120 | 5.368
414 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.035 | -3.994 | 3.465 | 5.287
415 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 5.613 | 4.135 | 6.972
416 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.094 | 5.237 | 3.957 | 6.564
417 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.063 | 5.740 | 4.297 | 7.170
418 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.261 | -6.770 | 4.144 | 7.942
419 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.281 | -7.118 | 4.000 | 8.170
420 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.200 | -6.639 | 4.295 | 7.910
421 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.100 | 5.614 | 4.134 | 6.972
422 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.111 | 5.238 | 3.957 | 6.565
423 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.077 | 5.740 | 4.296 | 7.170
424 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.265 | -6.769 | 4.145 | 7.941
425 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.285 | -7.116 | 4.000 | 8.168
426 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.638 | 4.295 | 7.909
427 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 5.613 | 0.372 | 5.626
428 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.094 | 5.237 | 0.370 | 5.251
429 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.063 | 5.740 | 0.373 | 5.753
430 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.261 | -6.770 | 0.372 | 6.786
431 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.281 | -7.118 | 0.371 | 7.134
432 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.200 | -6.639 | 0.373 | 6.653
433 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.100 | 5.614 | 0.372 | 5.627
434 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.111 | 5.238 | 0.370 | 5.252
435 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.077 | 5.740 | 0.373 | 5.753
436 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.265 | -6.769 | 0.372 | 6.784
437 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.285 | -7.116 | 0.371 | 7.131
438 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.638 | 0.373 | 6.652
439 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 5.613 | 4.059 | 6.927
440 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.094 | 5.237 | 3.881 | 6.519
441 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.063 | 5.740 | 4.221 | 7.125
442 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.261 | -6.770 | 4.068 | 7.903
443 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.281 | -7.118 | 3.924 | 8.133
444 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.200 | -6.639 | 4.219 | 7.869
445 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.100 | 5.614 | 4.058 | 6.928
446 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.111 | 5.238 | 3.881 | 6.520
447 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.077 | 5.740 | 4.220 | 7.125
448 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.265 | -6.769 | 4.069 | 7.902
449 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.285 | -7.116 | 3.924 | 8.131
450 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.638 | 4.219 | 7.868
451 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.082 | 5.613 | -3.375 | 6.550
452 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.094 | 5.237 | -3.197 | 6.136
453 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.063 | 5.740 | -3.537 | 6.743
454 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.261 | -6.770 | -3.384 | 7.574
455 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.281 | -7.118 | -3.240 | 7.826
456 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.200 | -6.639 | -3.535 | 7.524
457 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.100 | 5.614 | -3.374 | 6.550
458 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.111 | 5.238 | -3.197 | 6.137
459 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.077 | 5.740 | -3.536 | 6.743
460 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.265 | -6.769 | -3.385 | 7.572
461 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.285 | -7.116 | -3.240 | 7.824
462 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.638 | -3.535 | 7.523
463 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.023 | 4.516 | 4.111 | 6.107
464 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.004 | 4.185 | 3.937 | 5.746
465 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.026 | 4.839 | 4.273 | 6.456
466 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.146 | -5.633 | 4.125 | 6.983
467 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.172 | -5.998 | 3.988 | 7.205
468 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.119 | -5.726 | 4.274 | 7.146
469 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.006 | 4.517 | 4.110 | 6.107
470 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.020 | 4.186 | 3.937 | 5.747
471 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.012 | 4.840 | 4.273 | 6.456
472 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.150 | -5.631 | 4.125 | 6.982
473 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.176 | -5.996 | 3.988 | 7.203
474 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.122 | -5.724 | 4.274 | 7.145
475 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.023 | 4.516 | 0.372 | 4.532
476 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.004 | 4.185 | 0.370 | 4.201
477 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.026 | 4.839 | 0.373 | 4.854
478 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.146 | -5.633 | 0.372 | 5.647
479 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.172 | -5.998 | 0.371 | 6.012
480 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.119 | -5.726 | 0.373 | 5.739
481 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.006 | 4.517 | 0.372 | 4.532
482 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.020 | 4.186 | 0.370 | 4.202
483 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.012 | 4.840 | 0.373 | 4.854
484 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.150 | -5.631 | 0.372 | 5.646
485 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.176 | -5.996 | 0.371 | 6.010
486 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.122 | -5.724 | 0.373 | 5.738
487 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.023 | 4.516 | 4.035 | 6.056
488 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.004 | 4.185 | 3.861 | 5.694
489 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.026 | 4.839 | 4.197 | 6.406
490 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.146 | -5.633 | 4.049 | 6.939
491 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.172 | -5.998 | 3.912 | 7.163
492 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.119 | -5.726 | 4.198 | 7.101
493 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.006 | 4.517 | 4.034 | 6.056
494 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.020 | 4.186 | 3.861 | 5.695
495 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.012 | 4.840 | 4.197 | 6.406
496 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.150 | -5.631 | 4.049 | 6.938
497 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.176 | -5.996 | 3.912 | 7.161
498 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.122 | -5.724 | 4.198 | 7.100
499 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.023 | 4.516 | -3.351 | 5.623
500 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.004 | 4.185 | -3.177 | 5.254
501 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.026 | 4.839 | -3.513 | 5.980
502 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.146 | -5.633 | -3.365 | 6.563
503 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.172 | -5.998 | -3.228 | 6.813
504 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.119 | -5.726 | -3.514 | 6.719
505 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.006 | 4.517 | -3.350 | 5.624
506 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.020 | 4.186 | -3.177 | 5.255
507 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.012 | 4.840 | -3.513 | 5.980
508 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.150 | -5.631 | -3.365 | 6.562
509 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.176 | -5.996 | -3.228 | 6.812
510 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.122 | -5.724 | -3.514 | 6.718
511 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.023 | 4.516 | 3.001 | 5.422
512 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.004 | 4.185 | 2.876 | 5.078
513 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.026 | 4.839 | 3.118 | 5.757
514 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.146 | -5.633 | 3.011 | 6.389
515 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.172 | -5.998 | 2.913 | 6.670
516 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.119 | -5.726 | 3.118 | 6.521
517 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.006 | 4.517 | 3.001 | 5.423
518 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.020 | 4.186 | 2.876 | 5.079
519 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.012 | 4.840 | 3.118 | 5.757
520 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.150 | -5.631 | 3.011 | 6.388
521 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.176 | -5.996 | 2.913 | 6.668
522 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.122 | -5.724 | 3.118 | 6.520
523 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.004 | -0.309 | 4.102 | 4.113
524 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.015 | -0.479 | 3.997 | 4.025
525 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.008 | -0.243 | 4.204 | 4.211
526 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.004 | -0.309 | 4.102 | 4.113
527 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.015 | -0.479 | 3.997 | 4.025
528 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.008 | -0.243 | 4.204 | 4.211
529 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.008 | 0.196 | 6.308 | 6.311
530 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.010 | -0.090 | 4.702 | 4.703
531 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.001 | 0.244 | 4.963 | 4.969
532 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.024 | -1.335 | 6.315 | 6.455
533 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.033 | -1.239 | 4.720 | 4.880
534 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.022 | -0.915 | 4.963 | 5.047
535 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.006 | 0.151 | 4.836 | 4.838
536 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.010 | -0.090 | 4.702 | 4.703
537 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.001 | 0.320 | 6.478 | 6.486
538 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.018 | -1.005 | 4.841 | 4.944
539 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.033 | -1.239 | 4.720 | 4.880
540 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.030 | -1.216 | 6.478 | 6.591
541 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.006 | 0.151 | 4.836 | 4.838
542 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.014 | -0.124 | 6.130 | 6.131
543 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.001 | 0.244 | 4.963 | 4.969
544 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.018 | -1.005 | 4.841 | 4.944
545 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.043 | -1.648 | 6.154 | 6.371
546 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.022 | -0.915 | 4.963 | 5.047
547 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.058 | 4.380 | 3.324 | 5.498
548 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.025 | 4.108 | 3.179 | 5.195
549 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.054 | 4.673 | 3.459 | 5.814
550 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.105 | -5.305 | 3.338 | 6.268
551 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | 0.132 | -5.611 | 3.226 | 6.474
552 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.092 | -5.408 | 3.461 | 6.422
553 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.354 | 6.754 | 4.177 | 7.949
554 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.613 | 4.192 | 7.838
555 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | 4.339 | 8.112
556 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | 4.181 | 7.849
557 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.389 | -6.807 | 4.198 | 8.007
558 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.385 | -6.579 | 4.337 | 7.890
559 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.355 | 6.754 | 4.177 | 7.949
560 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.612 | 4.192 | 7.838
561 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | 4.338 | 8.111
562 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | 4.181 | 7.849
563 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.388 | -6.807 | 4.198 | 8.007
564 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.384 | -6.579 | 4.337 | 7.890
565 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.354 | 6.754 | 0.372 | 6.774
566 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.613 | 0.372 | 6.634
567 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | 0.373 | 6.864
568 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | 0.372 | 6.654
569 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.389 | -6.807 | 0.372 | 6.829
570 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.385 | -6.579 | 0.373 | 6.601
571 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.355 | 6.754 | 0.372 | 6.774
572 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.612 | 0.372 | 6.634
573 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | 0.373 | 6.864
574 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | 0.372 | 6.654
575 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.388 | -6.807 | 0.372 | 6.828
576 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.384 | -6.579 | 0.373 | 6.601
577 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.354 | 6.754 | 4.101 | 7.910
578 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.613 | 4.116 | 7.798
579 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | 4.263 | 8.071
580 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | 4.105 | 7.809
581 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.389 | -6.807 | 4.122 | 7.967
582 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.385 | -6.579 | 4.261 | 7.848
583 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.355 | 6.754 | 4.101 | 7.910
584 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.612 | 4.116 | 7.798
585 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | 4.262 | 8.071
586 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | 4.105 | 7.809
587 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.388 | -6.807 | 4.122 | 7.967
588 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.384 | -6.579 | 4.261 | 7.848
589 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.354 | 6.754 | -3.417 | 7.578
590 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.613 | -3.432 | 7.460
591 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | -3.579 | 7.732
592 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | -3.421 | 7.472
593 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.389 | -6.807 | -3.438 | 7.636
594 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.385 | -6.579 | -3.577 | 7.499
595 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.355 | 6.754 | -3.417 | 7.578
596 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.375 | 6.612 | -3.432 | 7.460
597 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.373 | 6.844 | -3.578 | 7.732
598 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.375 | -6.633 | -3.421 | 7.472
599 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.388 | -6.807 | -3.438 | 7.636
600 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.384 | -6.579 | -3.577 | 7.499
601 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.055 | 5.517 | 4.166 | 6.913
602 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 4.182 | 6.824
603 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 4.323 | 7.245
604 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 4.169 | 6.823
605 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 4.188 | 6.976
606 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 4.322 | 7.040
607 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.056 | 5.517 | 4.166 | 6.913
608 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 4.182 | 6.824
609 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 4.323 | 7.245
610 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 4.169 | 6.823
611 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 4.188 | 6.976
612 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 4.322 | 7.040
613 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.055 | 5.517 | 0.372 | 5.530
614 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 0.372 | 5.406
615 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 0.373 | 5.825
616 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 0.372 | 5.413
617 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 0.372 | 5.591
618 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 0.373 | 5.570
619 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.056 | 5.517 | 0.372 | 5.530
620 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 0.372 | 5.406
621 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 0.373 | 5.825
622 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 0.372 | 5.413
623 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 0.372 | 5.591
624 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 0.373 | 5.570
625 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.055 | 5.517 | 4.090 | 6.868
626 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 4.106 | 6.778
627 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 4.247 | 7.200
628 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 4.093 | 6.776
629 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 4.112 | 6.930
630 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 4.246 | 6.994
631 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.056 | 5.517 | 4.090 | 6.868
632 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 4.106 | 6.778
633 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 4.247 | 7.200
634 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 4.093 | 6.776
635 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 4.112 | 6.930
636 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 4.246 | 6.994
637 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.055 | 5.517 | -3.406 | 6.484
638 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | -3.422 | 6.387
639 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | -3.563 | 6.819
640 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | -3.409 | 6.387
641 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | -3.428 | 6.548
642 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | -3.562 | 6.601
643 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.056 | 5.517 | -3.406 | 6.484
644 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | -3.422 | 6.387
645 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | -3.563 | 6.819
646 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | -3.409 | 6.387
647 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | -3.428 | 6.548
648 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | -3.562 | 6.601
649 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.055 | 5.517 | 3.040 | 6.300
650 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 3.052 | 6.197
651 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 3.154 | 6.614
652 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 3.043 | 6.199
653 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 3.057 | 6.361
654 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 3.153 | 6.390
655 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.056 | 5.517 | 3.040 | 6.300
656 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.055 | 5.393 | 3.052 | 6.197
657 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.066 | 5.813 | 3.154 | 6.614
658 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.077 | -5.400 | 3.043 | 6.199
659 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.062 | -5.578 | 3.057 | 6.361
660 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.082 | -5.557 | 3.153 | 6.390
661 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.017 | 0.036 | 4.212 | 4.213
662 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.011 | -0.050 | 4.237 | 4.237
663 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.008 | 0.069 | 4.337 | 4.338
664 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.017 | 0.036 | 4.212 | 4.213
665 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.011 | -0.050 | 4.237 | 4.237
666 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.008 | 0.069 | 4.337 | 4.338
667 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.027 | 0.886 | 6.487 | 6.547
668 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.014 | 0.553 | 4.998 | 5.028
669 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.008 | 0.720 | 5.121 | 5.171
670 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.033 | -0.755 | 6.488 | 6.532
671 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.015 | -0.692 | 5.000 | 5.048
672 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.011 | -0.530 | 5.120 | 5.147
673 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.020 | 0.668 | 4.970 | 5.015
674 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.014 | 0.553 | 4.998 | 5.028
675 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.011 | 0.955 | 6.689 | 6.757
676 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.024 | -0.569 | 4.970 | 5.003
677 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.015 | -0.692 | 5.000 | 5.048
678 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.015 | -0.701 | 6.687 | 6.724
679 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.020 | 0.668 | 4.970 | 5.015
680 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.018 | 0.733 | 6.524 | 6.565
681 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.008 | 0.720 | 5.121 | 5.171
682 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.024 | -0.569 | 4.970 | 5.003
683 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.020 | -0.918 | 6.528 | 6.592
684 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.011 | -0.530 | 5.120 | 5.147
685 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.037 | 5.265 | 3.363 | 6.248
686 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.039 | 5.166 | 3.376 | 6.171
687 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.039 | 5.535 | 3.493 | 6.545
688 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | -0.018 | -5.169 | 3.366 | 6.169
689 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.038 | -5.317 | 3.382 | 6.301
690 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | -0.023 | -5.326 | 3.491 | 6.368
691 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.224 | 6.995 | 5.268 | 8.759
692 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.271 | 6.851 | 5.227 | 8.621
693 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | 5.306 | 8.835
694 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.248 | -6.847 | 5.264 | 8.640
695 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | 5.226 | 8.734
696 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | 5.301 | 8.617
697 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.225 | 6.995 | 5.268 | 8.759
698 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.272 | 6.851 | 5.227 | 8.621
699 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | 5.306 | 8.834
700 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.247 | -6.847 | 5.264 | 8.640
701 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | 5.226 | 8.734
702 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | 5.301 | 8.617
703 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.224 | 6.995 | 0.381 | 7.008
704 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.271 | 6.851 | 0.380 | 6.866
705 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | 0.381 | 7.074
706 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.248 | -6.847 | 0.381 | 6.862
707 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | 0.380 | 7.009
708 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | 0.381 | 6.804
709 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.225 | 6.995 | 0.381 | 7.008
710 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.272 | 6.851 | 0.380 | 6.866
711 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | 0.381 | 7.074
712 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.247 | -6.847 | 0.381 | 6.862
713 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | 0.380 | 7.009
714 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | 0.381 | 6.804
715 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.224 | 6.995 | 5.192 | 8.714
716 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.271 | 6.851 | 5.151 | 8.575
717 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | 5.230 | 8.789
718 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.248 | -6.847 | 5.188 | 8.594
719 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | 5.150 | 8.689
720 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | 5.225 | 8.570
721 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.225 | 6.995 | 5.192 | 8.714
722 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.272 | 6.851 | 5.151 | 8.575
723 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | 5.230 | 8.789
724 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.247 | -6.847 | 5.188 | 8.594
725 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | 5.150 | 8.689
726 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | 5.225 | 8.570
727 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.224 | 6.995 | -4.508 | 8.324
728 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.271 | 6.851 | -4.467 | 8.183
729 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | -4.546 | 8.400
730 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.248 | -6.847 | -4.504 | 8.200
731 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | -4.466 | 8.302
732 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | -4.541 | 8.171
733 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.225 | 6.995 | -4.508 | 8.324
734 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.272 | 6.851 | -4.467 | 8.183
735 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.250 | 7.059 | -4.546 | 8.400
736 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.247 | -6.847 | -4.504 | 8.200
737 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.294 | -6.992 | -4.466 | 8.302
738 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.265 | -6.788 | -4.541 | 8.171
739 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 5.227 | 7.777
740 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.632 | 5.186 | 7.656
741 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 5.274 | 8.005
742 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 5.222 | 7.669
743 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.073 | -5.769 | 5.186 | 7.758
744 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 5.268 | 7.803
745 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 5.227 | 7.777
746 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.058 | 5.632 | 5.186 | 7.656
747 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 5.274 | 8.005
748 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 5.222 | 7.669
749 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.072 | -5.769 | 5.186 | 7.758
750 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 5.268 | 7.804
751 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 0.380 | 5.771
752 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.632 | 0.380 | 5.645
753 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 0.381 | 6.035
754 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 0.380 | 5.629
755 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.073 | -5.769 | 0.380 | 5.782
756 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 0.381 | 5.770
757 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 0.380 | 5.771
758 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.058 | 5.632 | 0.380 | 5.645
759 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 0.381 | 6.035
760 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 0.380 | 5.629
761 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.072 | -5.769 | 0.380 | 5.782
762 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 0.381 | 5.770
763 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 5.151 | 7.726
764 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.632 | 5.110 | 7.605
765 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 5.198 | 7.955
766 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 5.146 | 7.618
767 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.073 | -5.769 | 5.110 | 7.707
768 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 5.192 | 7.752
769 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 5.151 | 7.726
770 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.058 | 5.632 | 5.110 | 7.605
771 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 5.198 | 7.955
772 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 5.146 | 7.618
773 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.072 | -5.769 | 5.110 | 7.707
774 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 5.192 | 7.752
775 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | -4.467 | 7.288
776 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.632 | -4.426 | 7.163
777 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | -4.514 | 7.526
778 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | -4.462 | 7.173
779 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.073 | -5.769 | -4.426 | 7.272
780 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | -4.508 | 7.312
781 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | -4.467 | 7.288
782 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.058 | 5.632 | -4.426 | 7.163
783 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | -4.514 | 7.526
784 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | -4.462 | 7.173
785 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.072 | -5.769 | -4.426 | 7.272
786 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | -4.508 | 7.312
787 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 3.805 | 6.902
788 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.632 | 3.775 | 6.780
789 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 3.838 | 7.142
790 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 3.801 | 6.782
791 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.073 | -5.769 | 3.775 | 6.895
792 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 3.834 | 6.917
793 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.018 | 5.758 | 3.805 | 6.901
794 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.058 | 5.632 | 3.775 | 6.780
795 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.056 | 6.022 | 3.838 | 7.141
796 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.046 | -5.616 | 3.801 | 6.782
797 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.072 | -5.769 | 3.775 | 6.895
798 | 304A | WB8025 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.080 | -5.757 | 3.834 | 6.917
799 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.008 | 0.039 | 5.019 | 5.019
800 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.011 | -0.039 | 4.982 | 4.982
801 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.012 | 0.070 | 5.010 | 5.011
802 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.008 | 0.039 | 5.019 | 5.019
803 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.011 | -0.039 | 4.982 | 4.982
804 | 304A | WB8025 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.012 | 0.070 | 5.010 | 5.011
805 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.007 | 0.946 | 7.788 | 7.845
806 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.013 | 0.603 | 5.900 | 5.931
807 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.012 | 0.753 | 5.937 | 5.984
808 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.017 | -0.801 | 7.785 | 7.826
809 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.015 | -0.712 | 5.900 | 5.943
810 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.019 | -0.560 | 5.934 | 5.961
811 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.006 | 0.713 | 5.945 | 5.988
812 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.013 | 0.603 | 5.900 | 5.931
813 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.016 | 1.000 | 7.776 | 7.840
814 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.012 | -0.604 | 5.943 | 5.974
815 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.015 | -0.712 | 5.900 | 5.943
816 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.026 | -0.742 | 7.773 | 7.808
817 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.006 | 0.713 | 5.945 | 5.988
818 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.017 | 0.799 | 7.727 | 7.768
819 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.012 | 0.753 | 5.937 | 5.984
820 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.012 | -0.604 | 5.943 | 5.974
821 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.020 | -0.944 | 7.727 | 7.785
822 | 304A | WB8025 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.019 | -0.560 | 5.934 | 5.961
823 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.034 | 5.484 | 4.231 | 6.927
824 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.004 | 5.383 | 4.198 | 6.826
825 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.007 | 5.728 | 4.271 | 7.145
826 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | -0.011 | -5.368 | 4.227 | 6.833
827 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | 0.008 | -5.495 | 4.198 | 6.915
828 | 304A | WB8025 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.025 | -5.510 | 4.266 | 6.968
829 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | 5.208 | 8.412
830 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.403 | 6.276 | 5.250 | 8.192
831 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | 5.526 | 8.689
832 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | 5.228 | 8.298
833 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.430 | -6.733 | 5.274 | 8.564
834 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.374 | -6.304 | 5.505 | 8.378
835 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | 5.208 | 8.412
836 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.402 | 6.276 | 5.250 | 8.192
837 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | 5.526 | 8.689
838 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | 5.228 | 8.298
839 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.431 | -6.733 | 5.274 | 8.564
840 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.375 | -6.304 | 5.505 | 8.378
841 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | 0.478 | 6.623
842 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.403 | 6.276 | 0.479 | 6.307
843 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | 0.481 | 6.723
844 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | 0.479 | 6.461
845 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.430 | -6.733 | 0.479 | 6.764
846 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.374 | -6.304 | 0.481 | 6.333
847 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | 0.478 | 6.623
848 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.402 | 6.276 | 0.479 | 6.307
849 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | 0.481 | 6.723
850 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | 0.479 | 6.461
851 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.431 | -6.733 | 0.479 | 6.764
852 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.375 | -6.304 | 0.481 | 6.333
853 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | 5.110 | 8.351
854 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.403 | 6.276 | 5.152 | 8.130
855 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | 5.428 | 8.627
856 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | 5.130 | 8.236
857 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.430 | -6.733 | 5.176 | 8.504
858 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.374 | -6.304 | 5.407 | 8.314
859 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | 5.110 | 8.351
860 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.402 | 6.276 | 5.152 | 8.130
861 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | 5.428 | 8.627
862 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | 5.130 | 8.236
863 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.431 | -6.733 | 5.176 | 8.504
864 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.375 | -6.304 | 5.407 | 8.314
865 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | -4.228 | 7.843
866 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.403 | 6.276 | -4.270 | 7.601
867 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | -4.546 | 8.101
868 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | -4.248 | 7.718
869 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.430 | -6.733 | -4.294 | 7.998
870 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.374 | -6.304 | -4.525 | 7.769
871 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.426 | 6.592 | -4.228 | 7.843
872 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.402 | 6.276 | -4.270 | 7.601
873 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.403 | 6.694 | -4.546 | 8.101
874 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.484 | -6.425 | -4.248 | 7.718
875 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.431 | -6.733 | -4.294 | 7.997
876 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.375 | -6.304 | -4.525 | 7.769
877 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 5.150 | 7.431
878 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.092 | 5.069 | 5.192 | 7.256
879 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 5.474 | 7.880
880 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 5.169 | 7.331
881 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.101 | -5.503 | 5.218 | 7.585
882 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.290 | 5.453 | 7.598
883 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 5.150 | 7.431
884 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.091 | 5.069 | 5.192 | 7.256
885 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 5.474 | 7.880
886 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 5.169 | 7.331
887 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.102 | -5.503 | 5.218 | 7.585
888 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.119 | -5.290 | 5.453 | 7.598
889 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 0.478 | 5.379
890 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.092 | 5.069 | 0.478 | 5.092
891 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 0.480 | 5.689
892 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 0.478 | 5.220
893 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.101 | -5.503 | 0.478 | 5.525
894 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.290 | 0.480 | 5.314
895 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 0.478 | 5.379
896 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.091 | 5.069 | 0.478 | 5.092
897 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 0.480 | 5.689
898 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 0.478 | 5.220
899 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.102 | -5.503 | 0.478 | 5.525
900 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.119 | -5.290 | 0.480 | 5.314
901 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 5.052 | 7.364
902 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.092 | 5.069 | 5.094 | 7.187
903 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 5.376 | 7.813
904 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 5.071 | 7.262
905 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.101 | -5.503 | 5.120 | 7.518
906 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.290 | 5.355 | 7.528
907 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 5.052 | 7.364
908 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.091 | 5.069 | 5.094 | 7.187
909 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 5.376 | 7.813
910 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 5.071 | 7.262
911 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.102 | -5.503 | 5.120 | 7.518
912 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.119 | -5.290 | 5.355 | 7.528
913 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | -4.170 | 6.789
914 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.092 | 5.069 | -4.212 | 6.591
915 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | -4.494 | 7.234
916 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | -4.189 | 6.676
917 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.101 | -5.503 | -4.238 | 6.947
918 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.290 | -4.473 | 6.929
919 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | -4.170 | 6.789
920 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.091 | 5.069 | -4.212 | 6.591
921 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | -4.494 | 7.234
922 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | -4.189 | 6.676
923 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.102 | -5.503 | -4.238 | 6.947
924 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.119 | -5.290 | -4.473 | 6.929
925 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 3.761 | 6.546
926 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.092 | 5.069 | 3.791 | 6.330
927 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 3.995 | 6.934
928 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 3.775 | 6.424
929 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.101 | -5.503 | 3.810 | 6.694
930 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.290 | 3.979 | 6.621
931 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.085 | 5.357 | 3.761 | 6.546
932 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.091 | 5.069 | 3.791 | 6.330
933 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.136 | 5.667 | 3.994 | 6.934
934 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.141 | -5.197 | 3.775 | 6.424
935 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.102 | -5.503 | 3.810 | 6.694
936 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.119 | -5.290 | 3.979 | 6.621
937 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | -0.006 | 0.051 | 4.911 | 4.912
938 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | -0.000 | -0.118 | 4.954 | 4.955
939 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | -0.008 | 0.100 | 5.116 | 5.117
940 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | -0.006 | 0.051 | 4.911 | 4.912
941 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | -0.000 | -0.118 | 4.954 | 4.955
942 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | -0.008 | 0.100 | 5.116 | 5.117
943 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.017 | 0.903 | 7.541 | 7.595
944 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.000 | 0.448 | 5.839 | 5.856
945 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.009 | 0.752 | 6.044 | 6.091
946 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.005 | -0.718 | 7.546 | 7.580
947 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.000 | -0.776 | 5.847 | 5.899
948 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.011 | -0.474 | 6.038 | 6.056
949 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.012 | 0.681 | 5.790 | 5.830
950 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.000 | 0.448 | 5.839 | 5.856
951 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.012 | 0.998 | 7.879 | 7.942
952 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.004 | -0.542 | 5.795 | 5.820
953 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.000 | -0.776 | 5.847 | 5.899
954 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.014 | -0.627 | 7.870 | 7.895
955 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.012 | 0.681 | 5.790 | 5.830
956 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.000 | 0.593 | 7.605 | 7.628
957 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.009 | 0.752 | 6.044 | 6.091
958 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.004 | -0.542 | 5.795 | 5.820
959 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.001 | -1.030 | 7.617 | 7.686
960 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.011 | -0.474 | 6.038 | 6.056
961 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.034 | 5.111 | 4.182 | 6.604
962 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.020 | 4.879 | 4.215 | 6.448
963 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.018 | 5.394 | 4.447 | 6.991
964 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.012 | -4.981 | 4.198 | 6.514
965 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.017 | -5.234 | 4.238 | 6.735
966 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.005 | -5.087 | 4.429 | 6.745
967 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.319 | 6.604 | 4.529 | 8.014
968 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.321 | 6.437 | 4.504 | 7.863
969 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.256 | 6.665 | 4.681 | 8.148
970 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.352 | -6.548 | 4.532 | 7.971
971 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.357 | -6.727 | 4.511 | 8.108
972 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.269 | -6.494 | 4.682 | 8.010
973 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.336 | 6.604 | 4.528 | 8.014
974 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.338 | 6.438 | 4.503 | 7.864
975 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.269 | 6.665 | 4.680 | 8.148
976 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.361 | -6.548 | 4.531 | 7.971
977 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.366 | -6.727 | 4.511 | 8.108
978 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.276 | -6.494 | 4.681 | 8.011
979 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.319 | 6.604 | 0.473 | 6.628
980 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.321 | 6.437 | 0.473 | 6.463
981 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.256 | 6.665 | 0.474 | 6.687
982 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.352 | -6.548 | 0.473 | 6.575
983 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.357 | -6.727 | 0.473 | 6.753
984 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.269 | -6.494 | 0.474 | 6.517
985 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.336 | 6.604 | 0.473 | 6.629
986 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.338 | 6.438 | 0.473 | 6.464
987 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.269 | 6.665 | 0.474 | 6.687
988 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.361 | -6.548 | 0.473 | 6.575
989 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.366 | -6.727 | 0.473 | 6.754
990 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.276 | -6.494 | 0.474 | 6.518
991 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.319 | 6.604 | 4.431 | 7.959
992 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.321 | 6.437 | 4.406 | 7.807
993 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.256 | 6.665 | 4.583 | 8.093
994 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.352 | -6.548 | 4.434 | 7.916
995 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.357 | -6.727 | 4.413 | 8.053
996 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.269 | -6.494 | 4.584 | 7.954
997 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.336 | 6.604 | 4.430 | 7.959
998 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.338 | 6.438 | 4.405 | 7.808
999 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.269 | 6.665 | 4.582 | 8.092
1000 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.361 | -6.548 | 4.433 | 7.916
1001 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.366 | -6.727 | 4.413 | 8.054
1002 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.276 | -6.494 | 4.583 | 7.954
1003 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.319 | 6.604 | -3.549 | 7.503
1004 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.321 | 6.437 | -3.524 | 7.346
1005 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.256 | 6.665 | -3.701 | 7.628
1006 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.352 | -6.548 | -3.552 | 7.458
1007 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.357 | -6.727 | -3.531 | 7.606
1008 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.269 | -6.494 | -3.702 | 7.480
1009 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.336 | 6.604 | -3.548 | 7.504
1010 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.338 | 6.438 | -3.523 | 7.347
1011 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.269 | 6.665 | -3.700 | 7.628
1012 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.361 | -6.548 | -3.551 | 7.458
1013 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.366 | -6.727 | -3.531 | 7.606
1014 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.276 | -6.494 | -3.701 | 7.480
1015 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.133 | 5.366 | 4.504 | 7.007
1016 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.129 | 5.222 | 4.480 | 6.881
1017 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.093 | 5.646 | 4.655 | 7.318
1018 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.175 | -5.313 | 4.507 | 6.969
1019 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.170 | -5.497 | 4.488 | 7.099
1020 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.480 | 4.655 | 7.191
1021 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.150 | 5.366 | 4.504 | 7.007
1022 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.146 | 5.222 | 4.480 | 6.882
1023 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.107 | 5.646 | 4.654 | 7.317
1024 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.183 | -5.313 | 4.506 | 6.969
1025 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.178 | -5.497 | 4.488 | 7.099
1026 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.126 | -5.480 | 4.654 | 7.191
1027 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.133 | 5.366 | 0.473 | 5.388
1028 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.129 | 5.222 | 0.473 | 5.244
1029 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.093 | 5.646 | 0.474 | 5.667
1030 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.175 | -5.313 | 0.473 | 5.337
1031 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.170 | -5.497 | 0.473 | 5.520
1032 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.480 | 0.474 | 5.502
1033 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.150 | 5.366 | 0.473 | 5.389
1034 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.146 | 5.222 | 0.473 | 5.246
1035 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.107 | 5.646 | 0.474 | 5.667
1036 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.183 | -5.313 | 0.473 | 5.337
1037 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.178 | -5.497 | 0.473 | 5.520
1038 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.126 | -5.480 | 0.474 | 5.502
1039 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.133 | 5.366 | 4.406 | 6.944
1040 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.129 | 5.222 | 4.382 | 6.818
1041 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.093 | 5.646 | 4.557 | 7.256
1042 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.175 | -5.313 | 4.409 | 6.906
1043 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.170 | -5.497 | 4.390 | 7.037
1044 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.480 | 4.557 | 7.128
1045 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.150 | 5.366 | 4.406 | 6.944
1046 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.146 | 5.222 | 4.382 | 6.819
1047 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.107 | 5.646 | 4.556 | 7.255
1048 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.183 | -5.313 | 4.408 | 6.906
1049 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.178 | -5.497 | 4.390 | 7.037
1050 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.126 | -5.480 | 4.556 | 7.128
1051 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.133 | 5.366 | -3.524 | 6.421
1052 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.129 | 5.222 | -3.500 | 6.288
1053 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.093 | 5.646 | -3.675 | 6.737
1054 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.175 | -5.313 | -3.527 | 6.379
1055 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.170 | -5.497 | -3.508 | 6.523
1056 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.480 | -3.675 | 6.599
1057 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.150 | 5.366 | -3.524 | 6.421
1058 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.146 | 5.222 | -3.500 | 6.288
1059 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.107 | 5.646 | -3.674 | 6.737
1060 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.183 | -5.313 | -3.526 | 6.379
1061 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.178 | -5.497 | -3.508 | 6.523
1062 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.126 | -5.480 | -3.674 | 6.599
1063 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.133 | 5.366 | 3.296 | 6.298
1064 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.129 | 5.222 | 3.279 | 6.167
1065 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.093 | 5.646 | 3.404 | 6.594
1066 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.175 | -5.313 | 3.298 | 6.255
1067 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.170 | -5.497 | 3.285 | 6.406
1068 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.118 | -5.480 | 3.404 | 6.452
1069 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.150 | 5.366 | 3.296 | 6.299
1070 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.146 | 5.222 | 3.278 | 6.168
1071 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.107 | 5.646 | 3.404 | 6.593
1072 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.183 | -5.313 | 3.298 | 6.256
1073 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.178 | -5.497 | 3.285 | 6.406
1074 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.126 | -5.480 | 3.404 | 6.452
1075 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.084 | 0.016 | 4.478 | 4.479
1076 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.087 | -0.076 | 4.467 | 4.469
1077 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.075 | 0.048 | 4.582 | 4.582
1078 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.084 | 0.016 | 4.478 | 4.479
1079 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.087 | -0.076 | 4.467 | 4.469
1080 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.075 | 0.048 | 4.582 | 4.582
1081 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.148 | 0.848 | 6.840 | 6.894
1082 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.115 | 0.512 | 5.252 | 5.278
1083 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.099 | 0.685 | 5.391 | 5.435
1084 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.157 | -0.787 | 6.841 | 6.888
1085 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.121 | -0.722 | 5.253 | 5.304
1086 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.103 | -0.553 | 5.391 | 5.420
1087 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.111 | 0.639 | 5.265 | 5.305
1088 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.115 | 0.512 | 5.252 | 5.278
1089 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.132 | 0.908 | 7.008 | 7.068
1090 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.118 | -0.594 | 5.266 | 5.300
1091 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.121 | -0.722 | 5.253 | 5.304
1092 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.137 | -0.732 | 7.008 | 7.048
1093 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.111 | 0.639 | 5.265 | 5.305
1094 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.154 | 0.678 | 6.822 | 6.858
1095 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.099 | 0.685 | 5.391 | 5.435
1096 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.118 | -0.594 | 5.266 | 5.300
1097 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.162 | -0.958 | 6.824 | 6.893
1098 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.103 | -0.553 | 5.391 | 5.420
1099 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.040 | 5.128 | 3.651 | 6.295
1100 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.039 | 5.012 | 3.631 | 6.189
1101 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.010 | 5.388 | 3.774 | 6.578
1102 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.078 | -5.085 | 3.653 | 6.262
1103 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | 0.070 | -5.237 | 3.639 | 6.378
1104 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.037 | -5.252 | 3.774 | 6.467
1105 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.240 | 6.857 | 2.815 | 7.416
1106 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.200 | 6.703 | 2.841 | 7.283
1107 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.203 | 6.904 | 2.863 | 7.477
1108 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.277 | -6.828 | 2.820 | 7.392
1109 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.282 | -6.987 | 2.861 | 7.556
1110 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.188 | -6.746 | 2.856 | 7.328
1111 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.277 | 6.858 | 2.823 | 7.421
1112 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.237 | 6.704 | 2.848 | 7.288
1113 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.232 | 6.904 | 2.870 | 7.481
1114 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.295 | -6.828 | 2.824 | 7.395
1115 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.301 | -6.987 | 2.865 | 7.558
1116 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.746 | 2.860 | 7.330
1117 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.240 | 6.857 | 0.459 | 6.877
1118 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.200 | 6.703 | 0.459 | 6.722
1119 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.203 | 6.904 | 0.460 | 6.922
1120 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.277 | -6.828 | 0.459 | 6.849
1121 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.282 | -6.987 | 0.460 | 7.008
1122 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.188 | -6.746 | 0.460 | 6.764
1123 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.277 | 6.858 | 0.459 | 6.879
1124 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.237 | 6.704 | 0.459 | 6.724
1125 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.232 | 6.904 | 0.460 | 6.923
1126 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.295 | -6.828 | 0.459 | 6.850
1127 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.301 | -6.987 | 0.460 | 7.009
1128 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.746 | 0.460 | 6.765
1129 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.240 | 6.857 | 2.717 | 7.380
1130 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.200 | 6.703 | 2.743 | 7.245
1131 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.203 | 6.904 | 2.765 | 7.440
1132 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.277 | -6.828 | 2.722 | 7.355
1133 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.282 | -6.987 | 2.763 | 7.519
1134 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.188 | -6.746 | 2.758 | 7.290
1135 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.277 | 6.858 | 2.725 | 7.385
1136 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.237 | 6.704 | 2.750 | 7.251
1137 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.232 | 6.904 | 2.772 | 7.444
1138 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.295 | -6.828 | 2.726 | 7.358
1139 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.301 | -6.987 | 2.767 | 7.521
1140 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.746 | 2.762 | 7.293
1141 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.240 | 6.857 | -1.835 | 7.102
1142 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.200 | 6.703 | -1.861 | 6.959
1143 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.203 | 6.904 | -1.883 | 7.159
1144 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.277 | -6.828 | -1.840 | 7.077
1145 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.282 | -6.987 | -1.881 | 7.242
1146 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.188 | -6.746 | -1.876 | 7.004
1147 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.277 | 6.858 | -1.843 | 7.107
1148 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.237 | 6.704 | -1.868 | 6.964
1149 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.232 | 6.904 | -1.890 | 7.162
1150 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.295 | -6.828 | -1.844 | 7.079
1151 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.301 | -6.987 | -1.885 | 7.244
1152 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.203 | -6.746 | -1.880 | 7.006
1153 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.028 | 5.563 | 2.869 | 6.260
1154 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.067 | 5.431 | 2.895 | 6.155
1155 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.011 | 5.833 | 2.887 | 6.508
1156 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.037 | -5.536 | 2.883 | 6.242
1157 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.027 | -5.704 | 2.925 | 6.411
1158 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.009 | -5.680 | 2.887 | 6.371
1159 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.008 | 5.564 | 2.879 | 6.265
1160 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.031 | 5.433 | 2.905 | 6.161
1161 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.021 | 5.833 | 2.896 | 6.513
1162 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.055 | -5.537 | 2.888 | 6.245
1163 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.045 | -5.704 | 2.930 | 6.413
1164 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.025 | -5.680 | 2.892 | 6.374
1165 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.028 | 5.563 | 0.460 | 5.582
1166 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.067 | 5.431 | 0.460 | 5.451
1167 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.011 | 5.833 | 0.460 | 5.851
1168 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.037 | -5.536 | 0.460 | 5.555
1169 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.027 | -5.704 | 0.460 | 5.723
1170 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.009 | -5.680 | 0.460 | 5.698
1171 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.008 | 5.564 | 0.460 | 5.583
1172 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.031 | 5.433 | 0.460 | 5.452
1173 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.021 | 5.833 | 0.460 | 5.852
1174 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.055 | -5.537 | 0.460 | 5.556
1175 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.045 | -5.704 | 0.460 | 5.723
1176 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.025 | -5.680 | 0.460 | 5.699
1177 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.028 | 5.563 | 2.771 | 6.215
1178 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.067 | 5.431 | 2.797 | 6.109
1179 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.011 | 5.833 | 2.789 | 6.465
1180 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.037 | -5.536 | 2.785 | 6.197
1181 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.027 | -5.704 | 2.827 | 6.367
1182 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.009 | -5.680 | 2.789 | 6.328
1183 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.008 | 5.564 | 2.781 | 6.221
1184 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.031 | 5.433 | 2.807 | 6.115
1185 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.021 | 5.833 | 2.798 | 6.470
1186 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.055 | -5.537 | 2.790 | 6.200
1187 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.045 | -5.704 | 2.832 | 6.369
1188 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.025 | -5.680 | 2.794 | 6.330
1189 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.028 | 5.563 | -1.889 | 5.875
1190 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.067 | 5.431 | -1.915 | 5.759
1191 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.011 | 5.833 | -1.907 | 6.137
1192 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.037 | -5.536 | -1.903 | 5.854
1193 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.027 | -5.704 | -1.945 | 6.027
1194 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.009 | -5.680 | -1.907 | 5.991
1195 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.008 | 5.564 | -1.899 | 5.880
1196 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.031 | 5.433 | -1.925 | 5.764
1197 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.021 | 5.833 | -1.916 | 6.140
1198 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.055 | -5.537 | -1.908 | 5.857
1199 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.045 | -5.704 | -1.950 | 6.029
1200 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.025 | -5.680 | -1.912 | 5.993
1201 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.028 | 5.563 | 2.119 | 5.953
1202 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.067 | 5.431 | 2.137 | 5.837
1203 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.011 | 5.833 | 2.131 | 6.210
1204 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.037 | -5.536 | 2.129 | 5.931
1205 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.027 | -5.704 | 2.159 | 6.099
1206 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.009 | -5.680 | 2.132 | 6.066
1207 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.008 | 5.564 | 2.126 | 5.957
1208 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.031 | 5.433 | 2.144 | 5.841
1209 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.021 | 5.833 | 2.138 | 6.213
1210 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.055 | -5.537 | 2.132 | 5.933
1211 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.045 | -5.704 | 2.163 | 6.101
1212 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.025 | -5.680 | 2.135 | 6.068
1213 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | -0.030 | 0.008 | 3.381 | 3.381
1214 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | -0.031 | -0.072 | 3.430 | 3.430
1215 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | -0.018 | 0.040 | 3.413 | 3.413
1216 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | -0.030 | 0.008 | 3.381 | 3.381
1217 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | -0.031 | -0.072 | 3.430 | 3.430
1218 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | -0.018 | 0.040 | 3.413 | 3.413
1219 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.062 | 0.827 | 5.067 | 5.135
1220 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.048 | 0.515 | 3.989 | 4.023
1221 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.027 | 0.669 | 3.976 | 4.032
1222 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.049 | -0.799 | 5.072 | 5.135
1223 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.037 | -0.717 | 4.000 | 4.064
1224 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.022 | -0.556 | 3.975 | 4.014
1225 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.046 | 0.624 | 3.935 | 3.985
1226 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.048 | 0.515 | 3.989 | 4.023
1227 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.036 | 0.887 | 5.122 | 5.198
1228 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.037 | -0.602 | 3.939 | 3.985
1229 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.037 | -0.717 | 4.000 | 4.064
1230 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.030 | -0.737 | 5.120 | 5.173
1231 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.046 | 0.624 | 3.935 | 3.985
1232 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.064 | 0.683 | 5.139 | 5.185
1233 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.027 | 0.669 | 3.976 | 4.032
1234 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.037 | -0.602 | 3.939 | 3.985
1235 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.050 | -0.951 | 5.154 | 5.241
1236 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.022 | -0.556 | 3.975 | 4.014
1237 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.088 | 5.327 | 2.306 | 5.805
1238 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.119 | 5.220 | 2.328 | 5.717
1239 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.072 | 5.578 | 2.321 | 6.042
1240 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | -0.024 | -5.305 | 2.321 | 5.791
1241 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.033 | -5.445 | 2.357 | 5.934
1242 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | -0.045 | -5.453 | 2.325 | 5.928
1243 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.205 | 7.041 | 5.330 | 8.834
1244 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.148 | 6.896 | 5.347 | 8.727
1245 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.192 | 7.094 | 5.429 | 8.935
1246 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.171 | -6.925 | 5.329 | 8.740
1247 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.146 | -7.069 | 5.349 | 8.866
1248 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.158 | -6.875 | 5.427 | 8.760
1249 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.221 | 7.041 | 5.329 | 8.833
1250 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.163 | 6.896 | 5.346 | 8.727
1251 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.204 | 7.094 | 5.428 | 8.935
1252 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.195 | -6.925 | 5.328 | 8.740
1253 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.168 | -7.069 | 5.348 | 8.865
1254 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.177 | -6.875 | 5.425 | 8.760
1255 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.205 | 7.041 | 0.479 | 7.061
1256 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.148 | 6.896 | 0.479 | 6.914
1257 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.192 | 7.094 | 0.480 | 7.113
1258 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.171 | -6.925 | 0.479 | 6.944
1259 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.146 | -7.069 | 0.479 | 7.086
1260 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.158 | -6.875 | 0.480 | 6.893
1261 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.221 | 7.041 | 0.479 | 7.061
1262 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.163 | 6.896 | 0.479 | 6.915
1263 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.204 | 7.094 | 0.480 | 7.113
1264 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.195 | -6.925 | 0.479 | 6.944
1265 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.168 | -7.069 | 0.479 | 7.087
1266 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.177 | -6.875 | 0.480 | 6.894
1267 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.205 | 7.041 | 5.232 | 8.775
1268 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.148 | 6.896 | 5.249 | 8.667
1269 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.192 | 7.094 | 5.331 | 8.876
1270 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.171 | -6.925 | 5.231 | 8.680
1271 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.146 | -7.069 | 5.251 | 8.807
1272 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.158 | -6.875 | 5.329 | 8.700
1273 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.221 | 7.041 | 5.231 | 8.775
1274 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.163 | 6.896 | 5.248 | 8.667
1275 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.204 | 7.094 | 5.330 | 8.875
1276 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.195 | -6.925 | 5.230 | 8.680
1277 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.168 | -7.069 | 5.250 | 8.806
1278 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.177 | -6.875 | 5.327 | 8.699
1279 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.205 | 7.041 | -4.350 | 8.279
1280 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.148 | 6.896 | -4.367 | 8.164
1281 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.192 | 7.094 | -4.449 | 8.376
1282 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.171 | -6.925 | -4.349 | 8.179
1283 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.146 | -7.069 | -4.369 | 8.311
1284 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.158 | -6.875 | -4.447 | 8.189
1285 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.221 | 7.041 | -4.349 | 8.279
1286 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.163 | 6.896 | -4.366 | 8.163
1287 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.204 | 7.094 | -4.448 | 8.375
1288 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.195 | -6.925 | -4.348 | 8.179
1289 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.168 | -7.069 | -4.368 | 8.311
1290 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.177 | -6.875 | -4.445 | 8.189
1291 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.095 | 5.758 | 5.290 | 7.820
1292 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.043 | 5.630 | 5.307 | 7.737
1293 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.074 | 6.022 | 5.399 | 8.089
1294 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.065 | -5.646 | 5.289 | 7.736
1295 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.039 | -5.798 | 5.310 | 7.862
1296 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.042 | -5.807 | 5.396 | 7.927
1297 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.110 | 5.758 | 5.289 | 7.820
1298 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.630 | 5.306 | 7.737
1299 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.086 | 6.022 | 5.398 | 8.088
1300 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.088 | -5.646 | 5.287 | 7.736
1301 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.061 | -5.797 | 5.308 | 7.861
1302 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.062 | -5.807 | 5.395 | 7.926
1303 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.095 | 5.758 | 0.479 | 5.779
1304 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.043 | 5.630 | 0.479 | 5.651
1305 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.074 | 6.022 | 0.480 | 6.042
1306 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.065 | -5.646 | 0.479 | 5.667
1307 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.039 | -5.798 | 0.479 | 5.817
1308 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.042 | -5.807 | 0.480 | 5.827
1309 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.110 | 5.758 | 0.479 | 5.779
1310 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.630 | 0.479 | 5.651
1311 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.086 | 6.022 | 0.480 | 6.042
1312 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.088 | -5.646 | 0.479 | 5.667
1313 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.061 | -5.797 | 0.479 | 5.817
1314 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.062 | -5.807 | 0.480 | 5.827
1315 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.095 | 5.758 | 5.192 | 7.754
1316 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.043 | 5.630 | 5.209 | 7.670
1317 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.074 | 6.022 | 5.301 | 8.023
1318 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.065 | -5.646 | 5.191 | 7.670
1319 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.039 | -5.798 | 5.212 | 7.796
1320 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.042 | -5.807 | 5.298 | 7.861
1321 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.110 | 5.758 | 5.191 | 7.754
1322 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.630 | 5.208 | 7.670
1323 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.086 | 6.022 | 5.300 | 8.023
1324 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.088 | -5.646 | 5.189 | 7.669
1325 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.061 | -5.797 | 5.210 | 7.795
1326 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.062 | -5.807 | 5.297 | 7.860
1327 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.095 | 5.758 | -4.310 | 7.193
1328 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.043 | 5.630 | -4.327 | 7.101
1329 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.074 | 6.022 | -4.419 | 7.470
1330 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.065 | -5.646 | -4.309 | 7.103
1331 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.039 | -5.798 | -4.330 | 7.236
1332 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.042 | -5.807 | -4.416 | 7.296
1333 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.110 | 5.758 | -4.309 | 7.193
1334 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.630 | -4.326 | 7.100
1335 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.086 | 6.022 | -4.418 | 7.469
1336 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.088 | -5.646 | -4.307 | 7.102
1337 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.061 | -5.797 | -4.328 | 7.235
1338 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.062 | -5.807 | -4.415 | 7.295
1339 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.095 | 5.758 | 3.862 | 6.934
1340 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.043 | 5.630 | 3.874 | 6.834
1341 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.074 | 6.022 | 3.940 | 7.197
1342 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.065 | -5.646 | 3.861 | 6.840
1343 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.039 | -5.798 | 3.876 | 6.974
1344 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.042 | -5.807 | 3.938 | 7.016
1345 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.110 | 5.758 | 3.861 | 6.934
1346 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.057 | 5.630 | 3.873 | 6.834
1347 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.086 | 6.022 | 3.940 | 7.197
1348 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.088 | -5.646 | 3.860 | 6.840
1349 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.061 | -5.797 | 3.875 | 6.973
1350 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.062 | -5.807 | 3.937 | 7.016
1351 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.037 | 0.031 | 5.104 | 5.104
1352 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.014 | -0.047 | 5.118 | 5.119
1353 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.042 | 0.057 | 5.160 | 5.160
1354 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.037 | 0.031 | 5.104 | 5.104
1355 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.014 | -0.047 | 5.118 | 5.119
1356 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.042 | 0.057 | 5.160 | 5.160
1357 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.073 | 0.936 | 7.850 | 7.906
1358 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.020 | 0.597 | 6.039 | 6.068
1359 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.061 | 0.742 | 6.091 | 6.136
1360 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.062 | -0.821 | 7.849 | 7.892
1361 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.019 | -0.728 | 6.040 | 6.084
1362 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.052 | -0.583 | 6.089 | 6.117
1363 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.055 | 0.705 | 6.022 | 6.064
1364 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.020 | 0.597 | 6.039 | 6.068
1365 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.082 | 0.985 | 7.941 | 8.002
1366 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.046 | -0.619 | 6.022 | 6.054
1367 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.019 | -0.728 | 6.040 | 6.084
1368 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.069 | -0.772 | 7.939 | 7.977
1369 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.055 | 0.705 | 6.022 | 6.064
1370 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.027 | 0.791 | 7.872 | 7.911
1371 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.061 | 0.742 | 6.091 | 6.136
1372 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.046 | -0.619 | 6.022 | 6.054
1373 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.025 | -0.966 | 7.873 | 7.932
1374 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.052 | -0.583 | 6.089 | 6.117
1375 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.039 | 5.492 | 4.293 | 6.971
1376 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.000 | 5.388 | 4.307 | 6.898
1377 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.012 | 5.736 | 4.384 | 7.220
1378 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.017 | -5.400 | 4.292 | 6.898
1379 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.006 | -5.525 | 4.309 | 7.007
1380 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | -0.010 | -5.560 | 4.381 | 7.078
1381 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.176 | 6.842 | 4.517 | 8.201
1382 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.158 | 6.693 | 4.518 | 8.077
1383 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.105 | 6.883 | 4.636 | 8.299
1384 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.133 | -6.737 | 4.514 | 8.110
1385 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.182 | -6.886 | 4.522 | 8.239
1386 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.055 | -6.671 | 4.632 | 8.121
1387 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.195 | 6.842 | 4.517 | 8.201
1388 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.176 | 6.693 | 4.518 | 8.077
1389 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.118 | 6.883 | 4.636 | 8.299
1390 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.162 | -6.737 | 4.513 | 8.111
1391 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.209 | -6.885 | 4.521 | 8.240
1392 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.076 | -6.671 | 4.631 | 8.121
1393 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.176 | 6.842 | 0.473 | 6.861
1394 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.158 | 6.693 | 0.473 | 6.712
1395 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.105 | 6.883 | 0.474 | 6.900
1396 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.133 | -6.737 | 0.473 | 6.755
1397 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.182 | -6.886 | 0.473 | 6.904
1398 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.055 | -6.671 | 0.474 | 6.688
1399 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.195 | 6.842 | 0.473 | 6.861
1400 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.176 | 6.693 | 0.473 | 6.712
1401 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.118 | 6.883 | 0.474 | 6.900
1402 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.162 | -6.737 | 0.473 | 6.755
1403 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.209 | -6.885 | 0.473 | 6.905
1404 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.076 | -6.671 | 0.474 | 6.688
1405 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.176 | 6.842 | 4.419 | 8.147
1406 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.158 | 6.693 | 4.420 | 8.022
1407 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.105 | 6.883 | 4.538 | 8.245
1408 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.133 | -6.737 | 4.416 | 8.056
1409 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.182 | -6.886 | 4.424 | 8.186
1410 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.055 | -6.671 | 4.534 | 8.066
1411 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.195 | 6.842 | 4.419 | 8.147
1412 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.176 | 6.693 | 4.420 | 8.023
1413 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.118 | 6.883 | 4.538 | 8.245
1414 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.162 | -6.737 | 4.415 | 8.057
1415 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.209 | -6.885 | 4.423 | 8.186
1416 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.076 | -6.671 | 4.533 | 8.066
1417 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.176 | 6.842 | -3.537 | 7.704
1418 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.158 | 6.693 | -3.538 | 7.572
1419 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.105 | 6.883 | -3.656 | 7.794
1420 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.133 | -6.737 | -3.534 | 7.608
1421 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.182 | -6.886 | -3.542 | 7.745
1422 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.055 | -6.671 | -3.652 | 7.605
1423 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.195 | 6.842 | -3.537 | 7.705
1424 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.176 | 6.693 | -3.538 | 7.573
1425 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.118 | 6.883 | -3.656 | 7.794
1426 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.162 | -6.737 | -3.533 | 7.609
1427 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.209 | -6.885 | -3.541 | 7.745
1428 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.076 | -6.671 | -3.651 | 7.605
1429 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.112 | 5.572 | 4.496 | 7.161
1430 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.102 | 5.440 | 4.496 | 7.058
1431 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.068 | 5.834 | 4.616 | 7.440
1432 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.075 | -5.470 | 4.492 | 7.078
1433 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.114 | -5.627 | 4.500 | 7.206
1434 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.027 | -5.625 | 4.610 | 7.272
1435 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.131 | 5.572 | 4.496 | 7.161
1436 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.120 | 5.440 | 4.496 | 7.058
1437 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.083 | 5.834 | 4.615 | 7.439
1438 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.104 | -5.470 | 4.492 | 7.079
1439 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.141 | -5.627 | 4.500 | 7.206
1440 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.049 | -5.625 | 4.609 | 7.272
1441 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.112 | 5.572 | 0.473 | 5.593
1442 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.102 | 5.440 | 0.473 | 5.461
1443 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.068 | 5.834 | 0.474 | 5.854
1444 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.075 | -5.470 | 0.473 | 5.490
1445 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.114 | -5.627 | 0.473 | 5.648
1446 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.027 | -5.625 | 0.474 | 5.645
1447 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.131 | 5.572 | 0.473 | 5.593
1448 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.120 | 5.440 | 0.473 | 5.462
1449 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.083 | 5.834 | 0.474 | 5.854
1450 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.104 | -5.470 | 0.473 | 5.491
1451 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.141 | -5.627 | 0.473 | 5.649
1452 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.049 | -5.625 | 0.474 | 5.645
1453 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.112 | 5.572 | 4.398 | 7.099
1454 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.102 | 5.440 | 4.398 | 6.996
1455 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.068 | 5.834 | 4.518 | 7.379
1456 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.075 | -5.470 | 4.394 | 7.016
1457 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.114 | -5.627 | 4.402 | 7.146
1458 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.027 | -5.625 | 4.512 | 7.211
1459 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.131 | 5.572 | 4.398 | 7.100
1460 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.120 | 5.440 | 4.398 | 6.996
1461 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.083 | 5.834 | 4.517 | 7.379
1462 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.104 | -5.470 | 4.394 | 7.017
1463 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.141 | -5.627 | 4.402 | 7.146
1464 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.049 | -5.625 | 4.511 | 7.211
1465 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.112 | 5.572 | -3.516 | 6.589
1466 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.102 | 5.440 | -3.516 | 6.478
1467 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.068 | 5.834 | -3.636 | 6.875
1468 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.075 | -5.470 | -3.512 | 6.500
1469 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.114 | -5.627 | -3.520 | 6.639
1470 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.027 | -5.625 | -3.630 | 6.694
1471 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.131 | 5.572 | -3.516 | 6.590
1472 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.120 | 5.440 | -3.516 | 6.478
1473 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.083 | 5.834 | -3.635 | 6.874
1474 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.104 | -5.470 | -3.512 | 6.501
1475 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.141 | -5.627 | -3.520 | 6.639
1476 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.049 | -5.625 | -3.629 | 6.694
1477 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.112 | 5.572 | 3.290 | 6.472
1478 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | 0.102 | 5.440 | 3.290 | 6.358
1479 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.068 | 5.834 | 3.376 | 6.741
1480 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.075 | -5.470 | 3.287 | 6.382
1481 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.114 | -5.627 | 3.293 | 6.521
1482 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.027 | -5.625 | 3.372 | 6.558
1483 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.131 | 5.572 | 3.290 | 6.472
1484 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | 0.120 | 5.440 | 3.290 | 6.359
1485 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.083 | 5.834 | 3.376 | 6.741
1486 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.104 | -5.470 | 3.287 | 6.382
1487 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.141 | -5.627 | 3.293 | 6.521
1488 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.049 | -5.625 | 3.372 | 6.558
1489 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.019 | 0.027 | 4.511 | 4.511
1490 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.022 | -0.052 | 4.514 | 4.514
1491 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.026 | 0.055 | 4.593 | 4.594
1492 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.019 | 0.027 | 4.511 | 4.511
1493 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.022 | -0.052 | 4.514 | 4.514
1494 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.026 | 0.055 | 4.593 | 4.594
1495 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.043 | 0.893 | 6.894 | 6.952
1496 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.032 | 0.563 | 5.307 | 5.337
1497 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.041 | 0.712 | 5.406 | 5.452
1498 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.031 | -0.792 | 6.891 | 6.937
1499 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.031 | -0.708 | 5.309 | 5.356
1500 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.031 | -0.560 | 5.403 | 5.432
1501 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.032 | 0.673 | 5.305 | 5.348
1502 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.032 | 0.563 | 5.307 | 5.337
1503 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.055 | 0.944 | 7.028 | 7.091
1504 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.023 | -0.597 | 5.303 | 5.337
1505 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.031 | -0.708 | 5.309 | 5.356
1506 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.042 | -0.742 | 7.024 | 7.063
1507 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.032 | 0.673 | 5.305 | 5.348
1508 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.043 | 0.746 | 6.896 | 6.937
1509 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.041 | 0.712 | 5.406 | 5.452
1510 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.023 | -0.597 | 5.303 | 5.337
1511 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.042 | -0.939 | 6.899 | 6.963
1512 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.031 | -0.560 | 5.403 | 5.432
1513 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.072 | 5.320 | 3.642 | 6.447
1514 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.063 | 5.213 | 3.642 | 6.359
1515 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.040 | 5.565 | 3.742 | 6.706
1516 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.043 | -5.235 | 3.639 | 6.376
1517 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | 0.072 | -5.367 | 3.646 | 6.489
1518 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.007 | -5.392 | 3.737 | 6.560
1519 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.092 | 5.294 | 4.114 | 6.705
1520 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.089 | 5.046 | 4.085 | 6.493
1521 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.107 | 5.379 | 4.304 | 6.890
1522 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.207 | 2.222 | 2.100 | 3.065
1523 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.041 | -5.195 | 4.120 | 6.630
1524 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.067 | -5.455 | 4.105 | 6.828
1525 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.037 | -5.110 | 4.320 | 6.691
1526 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.110 | -2.360 | 2.100 | 3.161
1527 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.104 | 5.294 | 4.114 | 6.705
1528 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.100 | 5.047 | 4.085 | 6.493
1529 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.118 | 5.379 | 4.303 | 6.889
1530 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.216 | 2.222 | 2.100 | 3.065
1531 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.014 | -5.195 | 4.119 | 6.630
1532 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.040 | -5.455 | 4.103 | 6.826
1533 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.013 | -5.111 | 4.318 | 6.690
1534 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.131 | -2.360 | 2.100 | 3.161
1535 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.092 | 5.294 | 0.470 | 5.315
1536 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.089 | 5.046 | 0.469 | 5.069
1537 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.107 | 5.379 | 0.471 | 5.401
1538 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.207 | 2.222 | 0.106 | 2.235
1539 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.041 | -5.195 | 0.470 | 5.216
1540 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.067 | -5.455 | 0.470 | 5.476
1541 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.037 | -5.110 | 0.471 | 5.132
1542 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.110 | -2.360 | 0.106 | 2.365
1543 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.104 | 5.294 | 0.470 | 5.316
1544 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.100 | 5.047 | 0.469 | 5.070
1545 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.118 | 5.379 | 0.471 | 5.401
1546 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.216 | 2.222 | 0.106 | 2.235
1547 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.014 | -5.195 | 0.470 | 5.216
1548 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.040 | -5.455 | 0.470 | 5.475
1549 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.013 | -5.111 | 0.471 | 5.132
1550 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.131 | -2.360 | 0.106 | 2.366
1551 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.092 | 5.294 | 4.016 | 6.646
1552 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.089 | 5.046 | 3.987 | 6.432
1553 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.107 | 5.379 | 4.206 | 6.829
1554 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.207 | 2.222 | 2.080 | 3.051
1555 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.041 | -5.195 | 4.022 | 6.570
1556 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.067 | -5.455 | 4.007 | 6.769
1557 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.037 | -5.110 | 4.222 | 6.628
1558 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.110 | -2.360 | 2.080 | 3.147
1559 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.104 | 5.294 | 4.016 | 6.645
1560 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.100 | 5.047 | 3.987 | 6.432
1561 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.118 | 5.379 | 4.205 | 6.828
1562 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.216 | 2.222 | 2.080 | 3.052
1563 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.014 | -5.195 | 4.021 | 6.569
1564 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.040 | -5.455 | 4.005 | 6.768
1565 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.013 | -5.111 | 4.220 | 6.628
1566 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.131 | -2.360 | 2.080 | 3.148
1567 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.092 | 5.294 | -3.134 | 6.153
1568 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.089 | 5.046 | -3.105 | 5.926
1569 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.107 | 5.379 | -3.324 | 6.324
1570 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.207 | 2.222 | -1.900 | 2.931
1571 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.041 | -5.195 | -3.140 | 6.070
1572 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.067 | -5.455 | -3.125 | 6.287
1573 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.037 | -5.110 | -3.340 | 6.104
1574 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.110 | -2.360 | -1.900 | 3.031
1575 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.104 | 5.294 | -3.134 | 6.153
1576 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.100 | 5.047 | -3.105 | 5.926
1577 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.118 | 5.379 | -3.323 | 6.324
1578 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.216 | 2.222 | -1.900 | 2.932
1579 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.014 | -5.195 | -3.139 | 6.070
1580 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.040 | -5.455 | -3.123 | 6.286
1581 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.013 | -5.111 | -3.338 | 6.104
1582 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.131 | -2.360 | -1.900 | 3.032
1583 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.160 | 4.445 | 4.081 | 6.036
1584 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.161 | 4.217 | 4.050 | 5.849
1585 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.179 | 4.705 | 4.280 | 6.363
1586 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.215 | 1.963 | 2.051 | 2.847
1587 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.002 | -4.349 | 4.087 | 5.968
1588 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.005 | -4.609 | 4.073 | 6.151
1589 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.002 | -4.437 | 4.298 | 6.177
1590 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | 0.100 | -2.089 | 2.051 | 2.929
1591 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.172 | 4.445 | 4.080 | 6.036
1592 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.217 | 4.049 | 5.849
1593 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.190 | 4.704 | 4.279 | 6.362
1594 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.224 | 1.963 | 2.051 | 2.848
1595 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.029 | -4.349 | 4.086 | 5.967
1596 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.021 | -4.609 | 4.071 | 6.150
1597 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.023 | -4.438 | 4.296 | 6.177
1598 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | 0.121 | -2.089 | 2.051 | 2.929
1599 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.160 | 4.445 | 0.469 | 4.473
1600 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.161 | 4.217 | 0.469 | 4.246
1601 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.179 | 4.705 | 0.471 | 4.731
1602 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.215 | 1.963 | 0.106 | 1.978
1603 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.002 | -4.349 | 0.469 | 4.374
1604 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.005 | -4.609 | 0.469 | 4.633
1605 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.002 | -4.437 | 0.471 | 4.462
1606 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | 0.100 | -2.089 | 0.106 | 2.094
1607 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.172 | 4.445 | 0.469 | 4.473
1608 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.217 | 0.469 | 4.247
1609 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.190 | 4.704 | 0.471 | 4.732
1610 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.224 | 1.963 | 0.106 | 1.979
1611 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.029 | -4.349 | 0.469 | 4.375
1612 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.021 | -4.609 | 0.469 | 4.633
1613 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.023 | -4.438 | 0.471 | 4.463
1614 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | 0.121 | -2.089 | 0.106 | 2.095
1615 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.160 | 4.445 | 3.983 | 5.970
1616 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.161 | 4.217 | 3.952 | 5.781
1617 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.179 | 4.705 | 4.182 | 6.297
1618 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.215 | 1.963 | 2.031 | 2.833
1619 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.002 | -4.349 | 3.989 | 5.901
1620 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.005 | -4.609 | 3.975 | 6.086
1621 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.002 | -4.437 | 4.200 | 6.109
1622 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | 0.100 | -2.089 | 2.031 | 2.915
1623 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.172 | 4.445 | 3.982 | 5.970
1624 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.217 | 3.951 | 5.782
1625 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.190 | 4.704 | 4.181 | 6.297
1626 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.224 | 1.963 | 2.031 | 2.833
1627 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.029 | -4.349 | 3.988 | 5.901
1628 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.021 | -4.609 | 3.973 | 6.085
1629 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.023 | -4.438 | 4.198 | 6.109
1630 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | 0.121 | -2.089 | 2.031 | 2.916
1631 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.160 | 4.445 | -3.101 | 5.422
1632 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.161 | 4.217 | -3.070 | 5.218
1633 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.179 | 4.705 | -3.300 | 5.750
1634 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.215 | 1.963 | -1.851 | 2.707
1635 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.002 | -4.349 | -3.107 | 5.345
1636 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.005 | -4.609 | -3.093 | 5.551
1637 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.002 | -4.437 | -3.318 | 5.540
1638 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | 0.100 | -2.089 | -1.851 | 2.793
1639 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.172 | 4.445 | -3.100 | 5.422
1640 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.217 | -3.069 | 5.219
1641 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.190 | 4.704 | -3.299 | 5.749
1642 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.224 | 1.963 | -1.851 | 2.707
1643 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.029 | -4.349 | -3.106 | 5.344
1644 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.021 | -4.609 | -3.091 | 5.550
1645 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.023 | -4.438 | -3.316 | 5.540
1646 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | 0.121 | -2.089 | -1.851 | 2.793
1647 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.160 | 4.445 | 2.991 | 5.360
1648 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.161 | 4.217 | 2.969 | 5.159
1649 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.179 | 4.705 | 3.135 | 5.656
1650 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.215 | 1.963 | 1.487 | 2.472
1651 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | -0.002 | -4.349 | 2.996 | 5.281
1652 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.005 | -4.609 | 2.985 | 5.492
1653 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.002 | -4.437 | 3.147 | 5.440
1654 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | 0.100 | -2.089 | 1.487 | 2.566
1655 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.172 | 4.445 | 2.990 | 5.360
1656 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.217 | 2.969 | 5.160
1657 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.190 | 4.704 | 3.134 | 5.656
1658 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.224 | 1.963 | 1.487 | 2.473
1659 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | -0.029 | -4.349 | 2.995 | 5.281
1660 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.021 | -4.609 | 2.984 | 5.491
1661 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.023 | -4.438 | 3.146 | 5.440
1662 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | 0.121 | -2.089 | 1.487 | 2.567
1663 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | -0.039 | 0.022 | 3.875 | 3.875
1664 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | -0.039 | -0.094 | 3.857 | 3.858
1665 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | -0.036 | 0.067 | 3.994 | 3.995
1666 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 4 | Suspension | EWP Arm:E | 0.012 | -0.029 | 1.796 | 1.797
1667 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | -0.039 | 0.022 | 3.875 | 3.875
1668 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | -0.039 | -0.094 | 3.857 | 3.858
1669 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | -0.036 | 0.067 | 3.994 | 3.995
1670 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 4 | Suspension | EWP Arm:E | 0.012 | -0.029 | 1.796 | 1.797
1671 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.091 | 0.679 | 5.882 | 5.922
1672 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.067 | 0.352 | 4.523 | 4.537
1673 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.068 | 0.577 | 4.690 | 4.726
1674 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | 0.029 | 0.167 | 2.140 | 2.147
1675 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.052 | -0.598 | 5.883 | 5.914
1676 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.040 | -0.613 | 4.528 | 4.570
1677 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.033 | -0.391 | 4.695 | 4.711
1678 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | 0.014 | -0.248 | 2.140 | 2.154
1679 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.068 | 0.513 | 4.547 | 4.576
1680 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.067 | 0.352 | 4.523 | 4.537
1681 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.091 | 0.765 | 6.074 | 6.123
1682 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | 0.029 | 0.167 | 2.140 | 2.147
1683 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.039 | -0.452 | 4.547 | 4.570
1684 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.040 | -0.613 | 4.528 | 4.570
1685 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.044 | -0.517 | 6.080 | 6.102
1686 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | 0.014 | -0.248 | 2.140 | 2.154
1687 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.068 | 0.513 | 4.547 | 4.576
1688 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.090 | 0.464 | 5.851 | 5.870
1689 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.068 | 0.577 | 4.690 | 4.726
1690 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | 0.029 | 0.167 | 2.140 | 2.147
1691 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | -0.039 | -0.452 | 4.547 | 4.570
1692 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.053 | -0.813 | 5.858 | 5.914
1693 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | -0.033 | -0.391 | 4.695 | 4.711
1694 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | 0.014 | -0.248 | 2.140 | 2.154
1695 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.190 | 4.246 | 3.334 | 5.401
1696 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.195 | 4.054 | 3.306 | 5.235
1697 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.217 | 4.484 | 3.502 | 5.694
1698 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 4 | Suspension | EWP Arm:E | 0.216 | 1.897 | 1.641 | 2.517
1699 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | -0.048 | -4.164 | 3.339 | 5.338
1700 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.055 | -4.384 | 3.327 | 5.504
1701 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | -0.053 | -4.258 | 3.518 | 5.524
1702 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 4 | Suspension | EWP Arm:E | 0.117 | -1.994 | 1.641 | 2.585
1703 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.128 | 5.129 | 3.256 | 6.077
1704 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.088 | 4.996 | 3.260 | 5.966
1705 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.089 | 5.168 | 3.334 | 6.151
1706 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.200 | 2.094 | 1.432 | 2.545
1707 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.206 | -4.913 | 3.250 | 5.895
1708 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.160 | -5.057 | 3.262 | 6.020
1709 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.173 | -4.861 | 3.327 | 5.893
1710 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.135 | -2.193 | 1.432 | 2.623
1711 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.123 | 5.129 | 3.256 | 6.077
1712 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.084 | 4.996 | 3.260 | 5.966
1713 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.085 | 5.167 | 3.334 | 6.150
1714 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.203 | 2.094 | 1.432 | 2.545
1715 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.194 | -4.913 | 3.250 | 5.894
1716 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.149 | -5.057 | 3.263 | 6.020
1717 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.163 | -4.861 | 3.327 | 5.893
1718 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.142 | -2.193 | 1.432 | 2.623
1719 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.128 | 5.129 | 0.463 | 5.151
1720 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.088 | 4.996 | 0.463 | 5.018
1721 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.089 | 5.168 | 0.463 | 5.189
1722 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.200 | 2.094 | 0.101 | 2.106
1723 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.206 | -4.913 | 0.463 | 4.939
1724 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.160 | -5.057 | 0.463 | 5.081
1725 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.173 | -4.861 | 0.463 | 4.886
1726 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.135 | -2.193 | 0.101 | 2.199
1727 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.123 | 5.129 | 0.463 | 5.151
1728 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.084 | 4.996 | 0.463 | 5.018
1729 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.085 | 5.167 | 0.463 | 5.189
1730 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.203 | 2.094 | 0.101 | 2.106
1731 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.194 | -4.913 | 0.463 | 4.939
1732 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.149 | -5.057 | 0.463 | 5.080
1733 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.163 | -4.861 | 0.463 | 4.886
1734 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.142 | -2.193 | 0.101 | 2.200
1735 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.128 | 5.129 | 3.158 | 6.025
1736 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.088 | 4.996 | 3.162 | 5.913
1737 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.089 | 5.168 | 3.236 | 6.098
1738 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.200 | 2.094 | 1.412 | 2.534
1739 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.206 | -4.913 | 3.152 | 5.841
1740 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.160 | -5.057 | 3.164 | 5.968
1741 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.173 | -4.861 | 3.229 | 5.838
1742 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.135 | -2.193 | 1.412 | 2.612
1743 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.123 | 5.129 | 3.158 | 6.025
1744 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.084 | 4.996 | 3.162 | 5.913
1745 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.085 | 5.167 | 3.236 | 6.098
1746 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.203 | 2.094 | 1.412 | 2.534
1747 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.194 | -4.913 | 3.152 | 5.841
1748 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.149 | -5.057 | 3.165 | 5.967
1749 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.163 | -4.861 | 3.229 | 5.838
1750 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.142 | -2.193 | 1.412 | 2.612
1751 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | 0.128 | 5.129 | -2.276 | 5.613
1752 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | 0.088 | 4.996 | -2.280 | 5.492
1753 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | 0.089 | 5.168 | -2.354 | 5.679
1754 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | 0.200 | 2.094 | -1.232 | 2.438
1755 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | 0.206 | -4.913 | -2.270 | 5.416
1756 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | 0.160 | -5.057 | -2.282 | 5.551
1757 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | 0.173 | -4.861 | -2.347 | 5.401
1758 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | 0.135 | -2.193 | -1.232 | 2.519
1759 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | 0.123 | 5.129 | -2.276 | 5.613
1760 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | 0.084 | 4.996 | -2.280 | 5.492
1761 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | 0.085 | 5.167 | -2.354 | 5.679
1762 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | 0.203 | 2.094 | -1.232 | 2.438
1763 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | 0.194 | -4.913 | -2.270 | 5.416
1764 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | 0.149 | -5.057 | -2.283 | 5.550
1765 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | 0.163 | -4.861 | -2.347 | 5.400
1766 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | 0.142 | -2.193 | -1.232 | 2.520
1767 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.037 | 4.348 | 3.245 | 5.425
1768 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.013 | 4.229 | 3.249 | 5.333
1769 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.020 | 4.564 | 3.318 | 5.643
1770 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.005 | 1.870 | 1.430 | 2.354
1771 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.114 | -4.138 | 3.237 | 5.255
1772 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -4.288 | 3.251 | 5.381
1773 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.105 | -4.259 | 3.309 | 5.394
1774 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.059 | -1.964 | 1.430 | 2.430
1775 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.033 | 4.348 | 3.245 | 5.425
1776 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.017 | 4.230 | 3.249 | 5.333
1777 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.015 | 4.564 | 3.318 | 5.643
1778 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.008 | 1.870 | 1.430 | 2.354
1779 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.103 | -4.139 | 3.237 | 5.255
1780 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.052 | -4.288 | 3.251 | 5.381
1781 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.095 | -4.259 | 3.309 | 5.394
1782 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.052 | -1.964 | 1.430 | 2.430
1783 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.037 | 4.348 | 0.463 | 4.373
1784 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.013 | 4.229 | 0.463 | 4.255
1785 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.020 | 4.564 | 0.463 | 4.588
1786 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.005 | 1.870 | 0.101 | 1.872
1787 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.114 | -4.138 | 0.463 | 4.166
1788 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -4.288 | 0.463 | 4.313
1789 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.105 | -4.259 | 0.463 | 4.285
1790 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.059 | -1.964 | 0.101 | 1.967
1791 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.033 | 4.348 | 0.463 | 4.373
1792 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.017 | 4.230 | 0.463 | 4.255
1793 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.015 | 4.564 | 0.463 | 4.588
1794 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.008 | 1.870 | 0.101 | 1.872
1795 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.103 | -4.139 | 0.463 | 4.166
1796 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.052 | -4.288 | 0.463 | 4.313
1797 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.095 | -4.259 | 0.463 | 4.285
1798 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.052 | -1.964 | 0.101 | 1.967
1799 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.037 | 4.348 | 3.147 | 5.367
1800 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.013 | 4.229 | 3.151 | 5.274
1801 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.020 | 4.564 | 3.220 | 5.586
1802 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.005 | 1.870 | 1.410 | 2.342
1803 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.114 | -4.138 | 3.139 | 5.195
1804 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -4.288 | 3.153 | 5.323
1805 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.105 | -4.259 | 3.211 | 5.334
1806 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.059 | -1.964 | 1.410 | 2.418
1807 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.033 | 4.348 | 3.147 | 5.367
1808 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.017 | 4.230 | 3.151 | 5.274
1809 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.015 | 4.564 | 3.220 | 5.586
1810 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.008 | 1.870 | 1.410 | 2.342
1811 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.103 | -4.139 | 3.139 | 5.196
1812 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.052 | -4.288 | 3.153 | 5.323
1813 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.095 | -4.259 | 3.211 | 5.334
1814 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.052 | -1.964 | 1.410 | 2.418
1815 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.037 | 4.348 | -2.265 | 4.903
1816 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.013 | 4.229 | -2.269 | 4.800
1817 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.020 | 4.564 | -2.338 | 5.128
1818 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.005 | 1.870 | -1.230 | 2.238
1819 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.114 | -4.138 | -2.257 | 4.715
1820 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -4.288 | -2.271 | 4.852
1821 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.105 | -4.259 | -2.329 | 4.855
1822 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.059 | -1.964 | -1.230 | 2.318
1823 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.033 | 4.348 | -2.265 | 4.903
1824 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.017 | 4.230 | -2.269 | 4.800
1825 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.015 | 4.564 | -2.338 | 5.128
1826 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.008 | 1.870 | -1.230 | 2.238
1827 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.103 | -4.139 | -2.257 | 4.715
1828 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.052 | -4.288 | -2.271 | 4.853
1829 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.095 | -4.259 | -2.329 | 4.855
1830 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.052 | -1.964 | -1.230 | 2.318
1831 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | 0.037 | 4.348 | 2.389 | 4.961
1832 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.013 | 4.229 | 2.392 | 4.859
1833 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | 0.020 | 4.564 | 2.442 | 5.177
1834 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | 0.005 | 1.870 | 1.040 | 2.140
1835 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.114 | -4.138 | 2.384 | 4.777
1836 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.062 | -4.288 | 2.393 | 4.911
1837 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | 0.105 | -4.259 | 2.435 | 4.907
1838 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.059 | -1.964 | 1.040 | 2.223
1839 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | 0.033 | 4.348 | 2.389 | 4.961
1840 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.017 | 4.230 | 2.392 | 4.859
1841 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | 0.015 | 4.564 | 2.442 | 5.177
1842 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | 0.008 | 1.870 | 1.040 | 2.140
1843 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.103 | -4.139 | 2.384 | 4.777
1844 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | 0.052 | -4.288 | 2.394 | 4.911
1845 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | 0.095 | -4.259 | 2.435 | 4.907
1846 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.052 | -1.964 | 1.040 | 2.223
1847 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.019 | 0.051 | 3.299 | 3.299
1848 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | -0.005 | -0.013 | 3.308 | 3.308
1849 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.026 | 0.072 | 3.343 | 3.344
1850 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 4 | Suspension | EWP Arm:E | -0.101 | -0.023 | 1.427 | 1.430
1851 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.019 | 0.051 | 3.299 | 3.299
1852 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | -0.005 | -0.013 | 3.308 | 3.308
1853 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.026 | 0.072 | 3.343 | 3.344
1854 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 4 | Suspension | EWP Arm:E | -0.101 | -0.023 | 1.427 | 1.430
1855 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.028 | 0.694 | 4.954 | 5.002
1856 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.012 | 0.437 | 3.859 | 3.884
1857 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.029 | 0.554 | 3.904 | 3.944
1858 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | -0.136 | 0.164 | 1.690 | 1.703
1859 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.044 | -0.507 | 4.950 | 4.976
1860 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.000 | -0.473 | 3.860 | 3.889
1861 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.043 | -0.354 | 3.901 | 3.917
1862 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | -0.143 | -0.227 | 1.690 | 1.711
1863 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.021 | 0.524 | 3.850 | 3.886
1864 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.012 | 0.437 | 3.859 | 3.884
1865 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.039 | 0.734 | 5.026 | 5.080
1866 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | -0.136 | 0.164 | 1.690 | 1.703
1867 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.033 | -0.384 | 3.848 | 3.867
1868 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.000 | -0.473 | 3.860 | 3.889
1869 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.057 | -0.467 | 5.022 | 5.044
1870 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | -0.143 | -0.227 | 1.690 | 1.711
1871 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.021 | 0.524 | 3.850 | 3.886
1872 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.017 | 0.578 | 4.966 | 5.000
1873 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.029 | 0.554 | 3.904 | 3.944
1874 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | -0.136 | 0.164 | 1.690 | 1.703
1875 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.033 | -0.384 | 3.848 | 3.867
1876 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | -0.000 | -0.626 | 4.967 | 5.006
1877 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.043 | -0.354 | 3.901 | 3.917
1878 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | -0.143 | -0.227 | 1.690 | 1.711
1879 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.029 | 4.149 | 2.634 | 4.914
1880 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.077 | 4.050 | 2.638 | 4.833
1881 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.041 | 4.351 | 2.695 | 5.118
1882 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 4 | Suspension | EWP Arm:E | -0.099 | 1.801 | 1.154 | 2.141
1883 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.038 | -3.971 | 2.626 | 4.761
1884 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | -0.015 | -4.099 | 2.639 | 4.875
1885 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.036 | -4.091 | 2.686 | 4.894
1886 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 4 | Suspension | EWP Arm:E | -0.153 | -1.876 | 1.154 | 2.208
1887 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.128 | 4.946 | 3.784 | 6.229
1888 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.169 | 4.830 | 3.773 | 6.131
1889 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.149 | 4.976 | 3.885 | 6.315
1890 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | -0.326 | 2.060 | 1.780 | 2.742
1891 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.070 | -4.811 | 3.787 | 6.123
1892 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.106 | -4.927 | 3.779 | 6.210
1893 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.090 | -4.737 | 3.887 | 6.128
1894 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | -0.366 | -2.080 | 1.781 | 2.762
1895 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.131 | 4.946 | 3.784 | 6.229
1896 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.830 | 3.773 | 6.131
1897 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.153 | 4.976 | 3.884 | 6.315
1898 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | -0.324 | 2.060 | 1.780 | 2.741
1899 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.079 | -4.811 | 3.787 | 6.123
1900 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.114 | -4.927 | 3.779 | 6.210
1901 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.098 | -4.737 | 3.887 | 6.128
1902 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | -0.360 | -2.080 | 1.781 | 2.762
1903 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.128 | 4.946 | 0.467 | 4.970
1904 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.169 | 4.830 | 0.467 | 4.855
1905 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.149 | 4.976 | 0.468 | 5.000
1906 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | -0.326 | 2.060 | 0.103 | 2.088
1907 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.070 | -4.811 | 0.467 | 4.834
1908 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.106 | -4.927 | 0.467 | 4.950
1909 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.090 | -4.737 | 0.468 | 4.761
1910 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | -0.366 | -2.080 | 0.103 | 2.114
1911 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.131 | 4.946 | 0.467 | 4.970
1912 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.830 | 0.467 | 4.855
1913 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.153 | 4.976 | 0.468 | 5.000
1914 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | -0.324 | 2.060 | 0.103 | 2.087
1915 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.079 | -4.811 | 0.467 | 4.835
1916 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.114 | -4.927 | 0.467 | 4.950
1917 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.098 | -4.737 | 0.468 | 4.761
1918 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | -0.360 | -2.080 | 0.103 | 2.113
1919 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.128 | 4.946 | 3.686 | 6.170
1920 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.169 | 4.830 | 3.675 | 6.071
1921 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.149 | 4.976 | 3.787 | 6.255
1922 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | -0.326 | 2.060 | 1.760 | 2.729
1923 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.070 | -4.811 | 3.689 | 6.063
1924 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.106 | -4.927 | 3.681 | 6.151
1925 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.090 | -4.737 | 3.789 | 6.066
1926 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | -0.366 | -2.080 | 1.761 | 2.750
1927 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.131 | 4.946 | 3.686 | 6.170
1928 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.830 | 3.675 | 6.071
1929 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.153 | 4.976 | 3.786 | 6.255
1930 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | -0.324 | 2.060 | 1.760 | 2.728
1931 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.079 | -4.811 | 3.689 | 6.063
1932 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.114 | -4.927 | 3.681 | 6.151
1933 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.098 | -4.737 | 3.789 | 6.066
1934 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | -0.360 | -2.080 | 1.761 | 2.749
1935 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 1 | Suspension | X-arm_B:E | -0.128 | 4.946 | -2.804 | 5.687
1936 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 3 | Suspension | X-arm_M:O | -0.169 | 4.830 | -2.793 | 5.582
1937 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 2 | Suspension | X-arm_T:E | -0.149 | 4.976 | -2.905 | 5.764
1938 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+ | 4 | Suspension | EWP Arm:E | -0.326 | 2.060 | -1.580 | 2.616
1939 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 1 | Suspension | X-arm_B:E | -0.070 | -4.811 | -2.807 | 5.571
1940 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 3 | Suspension | X-arm_M:O | -0.106 | -4.927 | -2.799 | 5.667
1941 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 2 | Suspension | X-arm_T:E | -0.090 | -4.737 | -2.907 | 5.558
1942 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - D_draft,T NA- | 4 | Suspension | EWP Arm:E | -0.366 | -2.080 | -1.581 | 2.638
1943 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 1 | Suspension | X-arm_B:E | -0.131 | 4.946 | -2.804 | 5.687
1944 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 3 | Suspension | X-arm_M:O | -0.172 | 4.830 | -2.793 | 5.582
1945 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 2 | Suspension | X-arm_T:E | -0.153 | 4.976 | -2.904 | 5.764
1946 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+ | 4 | Suspension | EWP Arm:E | -0.324 | 2.060 | -1.580 | 2.616
1947 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 1 | Suspension | X-arm_B:E | -0.079 | -4.811 | -2.807 | 5.571
1948 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 3 | Suspension | X-arm_M:O | -0.114 | -4.927 | -2.799 | 5.667
1949 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 2 | Suspension | X-arm_T:E | -0.098 | -4.737 | -2.907 | 5.558
1950 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - D_draft,T NL- | 4 | Suspension | EWP Arm:E | -0.360 | -2.080 | -1.581 | 2.637
1951 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.038 | 4.220 | 3.761 | 5.653
1952 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.056 | 4.116 | 3.750 | 5.568
1953 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.063 | 4.425 | 3.874 | 5.882
1954 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | -0.143 | 1.851 | 1.765 | 2.562
1955 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.018 | -4.088 | 3.763 | 5.556
1956 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.003 | -4.210 | 3.757 | 5.643
1957 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.002 | -4.186 | 3.875 | 5.704
1958 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.181 | -1.871 | 1.766 | 2.579
1959 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.041 | 4.220 | 3.761 | 5.652
1960 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.058 | 4.116 | 3.750 | 5.568
1961 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.066 | 4.425 | 3.873 | 5.881
1962 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | -0.141 | 1.851 | 1.765 | 2.562
1963 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.010 | -4.088 | 3.763 | 5.556
1964 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.004 | -4.210 | 3.757 | 5.642
1965 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.010 | -4.186 | 3.875 | 5.704
1966 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Max Weight (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.176 | -1.871 | 1.766 | 2.578
1967 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.038 | 4.220 | 0.467 | 4.246
1968 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.056 | 4.116 | 0.467 | 4.142
1969 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.063 | 4.425 | 0.468 | 4.451
1970 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | -0.143 | 1.851 | 0.103 | 1.859
1971 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.018 | -4.088 | 0.467 | 4.114
1972 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.003 | -4.210 | 0.467 | 4.236
1973 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.002 | -4.186 | 0.468 | 4.212
1974 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.181 | -1.871 | 0.103 | 1.882
1975 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.041 | 4.220 | 0.467 | 4.246
1976 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.058 | 4.116 | 0.467 | 4.143
1977 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.066 | 4.425 | 0.468 | 4.451
1978 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | -0.141 | 1.851 | 0.103 | 1.859
1979 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.010 | -4.088 | 0.467 | 4.114
1980 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.004 | -4.210 | 0.467 | 4.236
1981 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.010 | -4.186 | 0.468 | 4.212
1982 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Min Weight (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.176 | -1.871 | 0.103 | 1.882
1983 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.038 | 4.220 | 3.663 | 5.588
1984 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.056 | 4.116 | 3.652 | 5.503
1985 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.063 | 4.425 | 3.776 | 5.818
1986 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | -0.143 | 1.851 | 1.745 | 2.548
1987 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.018 | -4.088 | 3.665 | 5.491
1988 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.003 | -4.210 | 3.659 | 5.578
1989 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.002 | -4.186 | 3.777 | 5.638
1990 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.181 | -1.871 | 1.746 | 2.565
1991 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.041 | 4.220 | 3.663 | 5.588
1992 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.058 | 4.116 | 3.652 | 5.503
1993 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.066 | 4.425 | 3.775 | 5.817
1994 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | -0.141 | 1.851 | 1.745 | 2.548
1995 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.010 | -4.088 | 3.665 | 5.490
1996 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.004 | -4.210 | 3.659 | 5.578
1997 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.010 | -4.186 | 3.777 | 5.638
1998 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Uplift (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.176 | -1.871 | 1.746 | 2.565
1999 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.038 | 4.220 | -2.781 | 5.054
2000 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.056 | 4.116 | -2.770 | 4.962
2001 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.063 | 4.425 | -2.894 | 5.288
2002 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | -0.143 | 1.851 | -1.565 | 2.428
2003 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.018 | -4.088 | -2.783 | 4.946
2004 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.003 | -4.210 | -2.777 | 5.043
2005 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.002 | -4.186 | -2.895 | 5.090
2006 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.181 | -1.871 | -1.566 | 2.446
2007 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.041 | 4.220 | -2.781 | 5.054
2008 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.058 | 4.116 | -2.770 | 4.962
2009 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.066 | 4.425 | -2.893 | 5.288
2010 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | -0.141 | 1.851 | -1.565 | 2.428
2011 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.010 | -4.088 | -2.783 | 4.945
2012 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.004 | -4.210 | -2.777 | 5.043
2013 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.010 | -4.186 | -2.895 | 5.090
2014 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and Vertical Uplift (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.176 | -1.871 | -1.566 | 2.446
2015 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 1 | Suspension | X-arm_B:E | -0.038 | 4.220 | 2.761 | 5.043
2016 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 3 | Suspension | X-arm_M:O | -0.056 | 4.116 | 2.753 | 4.952
2017 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 2 | Suspension | X-arm_T:E | -0.063 | 4.425 | 2.842 | 5.260
2018 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA+) - Synoptic,T NA+ | 4 | Suspension | EWP Arm:E | -0.143 | 1.851 | 1.282 | 2.256
2019 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 1 | Suspension | X-arm_B:E | 0.018 | -4.088 | 2.763 | 4.934
2020 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 3 | Suspension | X-arm_M:O | 0.003 | -4.210 | 2.758 | 5.033
2021 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 2 | Suspension | X-arm_T:E | -0.002 | -4.186 | 2.843 | 5.060
2022 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NA-) - Synoptic,T NA- | 4 | Suspension | EWP Arm:E | -0.181 | -1.871 | 1.282 | 2.275
2023 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 1 | Suspension | X-arm_B:E | -0.041 | 4.220 | 2.761 | 5.043
2024 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 3 | Suspension | X-arm_M:O | -0.058 | 4.116 | 2.753 | 4.952
2025 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 2 | Suspension | X-arm_T:E | -0.066 | 4.425 | 2.842 | 5.260
2026 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL+) - Synoptic,T NL+ | 4 | Suspension | EWP Arm:E | -0.141 | 1.851 | 1.282 | 2.256
2027 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 1 | Suspension | X-arm_B:E | 0.010 | -4.088 | 2.762 | 4.934
2028 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 3 | Suspension | X-arm_M:O | -0.004 | -4.210 | 2.758 | 5.033
2029 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 2 | Suspension | X-arm_T:E | -0.010 | -4.186 | 2.843 | 5.060
2030 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Max Wind and vert min (no uplift, susp) (NL-) - Synoptic,T NL- | 4 | Suspension | EWP Arm:E | -0.176 | -1.871 | 1.282 | 2.275
2031 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 1 | Suspension | X-arm_B:E | 0.010 | 0.033 | 3.587 | 3.587
2032 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 3 | Suspension | X-arm_M:O | 0.011 | -0.022 | 3.580 | 3.580
2033 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 2 | Suspension | X-arm_T:E | 0.018 | 0.058 | 3.645 | 3.646
2034 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA+),T NA+ | 4 | Suspension | EWP Arm:E | -0.010 | -0.005 | 1.596 | 1.596
2035 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 1 | Suspension | X-arm_B:E | 0.010 | 0.033 | 3.587 | 3.587
2036 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 3 | Suspension | X-arm_M:O | 0.011 | -0.022 | 3.580 | 3.580
2037 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 2 | Suspension | X-arm_T:E | 0.018 | 0.058 | 3.645 | 3.646
2038 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Everyday condition (Sustained loads) (NA-),T NA- | 4 | Suspension | EWP Arm:E | -0.010 | -0.005 | 1.596 | 1.596
2039 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.011 | 0.654 | 5.421 | 5.460
2040 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.011 | 0.417 | 4.191 | 4.212
2041 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.018 | 0.527 | 4.272 | 4.304
2042 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | -0.012 | 0.182 | 1.897 | 1.906
2043 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.025 | -0.530 | 5.422 | 5.448
2044 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.021 | -0.478 | 4.193 | 4.220
2045 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.031 | -0.366 | 4.272 | 4.288
2046 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | -0.017 | -0.195 | 1.897 | 1.907
2047 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.008 | 0.494 | 4.201 | 4.229
2048 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.011 | 0.417 | 4.191 | 4.212
2049 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.025 | 0.698 | 5.516 | 5.560
2050 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | -0.012 | 0.182 | 1.897 | 1.906
2051 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.019 | -0.401 | 4.201 | 4.220
2052 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.021 | -0.478 | 4.193 | 4.220
2053 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.041 | -0.483 | 5.516 | 5.537
2054 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | -0.017 | -0.195 | 1.897 | 1.907
2055 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 1 | Suspension | X-arm_B:E | 0.008 | 0.494 | 4.201 | 4.229
2056 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 3 | Suspension | X-arm_M:O | 0.015 | 0.551 | 5.408 | 5.436
2057 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 2 | Suspension | X-arm_T:E | 0.018 | 0.527 | 4.272 | 4.304
2058 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+ | 4 | Suspension | EWP Arm:E | -0.012 | 0.182 | 1.897 | 1.906
2059 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 1 | Suspension | X-arm_B:E | 0.019 | -0.401 | 4.201 | 4.220
2060 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 3 | Suspension | X-arm_M:O | 0.028 | -0.633 | 5.411 | 5.448
2061 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 2 | Suspension | X-arm_T:E | 0.031 | -0.366 | 4.272 | 4.288
2062 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA- | 4 | Suspension | EWP Arm:E | -0.017 | -0.195 | 1.897 | 1.907
2063 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 1 | Suspension | X-arm_B:E | -0.029 | 4.029 | 3.077 | 5.069
2064 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 3 | Suspension | X-arm_M:O | -0.042 | 3.943 | 3.069 | 4.996
2065 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 2 | Suspension | X-arm_T:E | -0.045 | 4.224 | 3.175 | 5.284
2066 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (+),T NA+ | 4 | Suspension | EWP Arm:E | 0.022 | 1.777 | 1.426 | 2.279
2067 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 1 | Suspension | X-arm_B:E | 0.015 | -3.917 | 3.079 | 4.982
2068 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 3 | Suspension | X-arm_M:O | 0.005 | -4.023 | 3.075 | 5.063
2069 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 2 | Suspension | X-arm_T:E | 0.002 | -4.020 | 3.176 | 5.123
2070 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 5% deflection - ULS (-),T NA- | 4 | Suspension | EWP Arm:E | -0.009 | -1.793 | 1.427 | 2.291

## Tab_9
rowtext | str_no | structure_name | element_label | element_type | maximum_usage | load_case
1 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 48.11 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
2 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 58.08 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
3 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 24.28 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
4 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Suspension | 11.66 | Max Wind and Max Weight (NA+) - D_draft,T NA+
5 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 3 | Suspension | 11.70 | Max Wind and Max Weight (NA-) - D_draft,T NA-
6 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 2 | Suspension | 11.86 | Max Wind and Max Weight (NA+) - D_draft,T NA+
7 | 284A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 64.79 | Max Wind and Vertical Uplift (NA+) - D_draft,T NA+
8 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 47.83 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
9 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 57.69 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
10 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 24.13 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
11 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Suspension | 11.49 | Max Wind and Max Weight (NA+) - D_draft,T NA+
12 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 3 | Suspension | 11.62 | Max Wind and Max Weight (NA-) - D_draft,T NA-
13 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 2 | Suspension | 11.70 | Max Wind and Max Weight (NA+) - D_draft,T NA+
14 | 285A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 65.60 | Max Wind and Max Weight (NA-) - D_draft,T NA-
15 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 42.50 | Max Wind and Max Weight (NL+) - D_draft,T NL+
16 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 49.89 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
17 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 21.19 | Max Wind and Max Weight (NL+) - D_draft,T NL+
18 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Suspension | 9.89 | Max Wind and Max Weight (NA+) - D_draft,T NA+
19 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 3 | Suspension | 9.57 | Max Wind and Max Weight (NA-) - D_draft,T NA-
20 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 2 | Suspension | 10.10 | Max Wind and Max Weight (NA+) - D_draft,T NA+
21 | 288A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 59.01 | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+
22 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 42.80 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
23 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 54.93 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
24 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 21.81 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
25 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Suspension | 11.35 | Max Wind and Max Weight (NA-) - D_draft,T NA-
26 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 3 | Suspension | 11.67 | Max Wind and Max Weight (NA-) - D_draft,T NA-
27 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 2 | Suspension | 11.30 | Max Wind and Max Weight (NA-) - D_draft,T NA-
28 | 290A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 68.97 | Max Wind and Max Weight (NL-) - D_draft,T NL-
29 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 45.36 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
30 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 55.34 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
31 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 23.01 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
32 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Suspension | 11.36 | Max Wind and Max Weight (NL+) - D_draft,T NL+
33 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 3 | Suspension | 11.44 | Max Wind and Max Weight (NA-) - D_draft,T NA-
34 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 2 | Suspension | 11.59 | Max Wind and Max Weight (NA+) - D_draft,T NA+
35 | 303A | T724-0000-000044 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 70.62 | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+
36 | 304A | WB8025 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 53.74 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
37 | 304A | WB8025 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 63.71 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
38 | 304A | WB8025 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 26.57 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
39 | 304A | WB8025 Updated Crossarm NO EP.POL | 1 | Suspension | 12.51 | Max Wind and Max Weight (NA+) - D_draft,T NA+
40 | 304A | WB8025 Updated Crossarm NO EP.POL | 3 | Suspension | 12.48 | Max Wind and Max Weight (NA-) - D_draft,T NA-
41 | 304A | WB8025 Updated Crossarm NO EP.POL | 2 | Suspension | 12.62 | Max Wind and Max Weight (NA+) - D_draft,T NA+
42 | 304A | WB8025 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 45.77 | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+
43 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 52.12 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
44 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 64.08 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
45 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 26.96 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
46 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Suspension | 12.02 | Max Wind and Max Weight (NA+) - D_draft,T NA+
47 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 3 | Suspension | 12.23 | Max Wind and Max Weight (NA-) - D_draft,T NA-
48 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 2 | Suspension | 12.41 | Max Wind and Max Weight (NA+) - D_draft,T NA+
49 | 355A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 70.53 | Max Wind and Max Weight (NL-) - D_draft,T NL-
50 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 47.53 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
51 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 58.11 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
52 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 24.57 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
53 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Suspension | 11.45 | Max Wind and Max Weight (NL+) - D_draft,T NL+
54 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 3 | Suspension | 11.58 | Max Wind and Max Weight (NL-) - D_draft,T NL-
55 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 2 | Suspension | 11.64 | Max Wind and Max Weight (NA+) - D_draft,T NA+
56 | 365A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 69.01 | Max Wind and Max Weight (NL-) - D_draft,T NL-
57 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 36.56 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
58 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 43.50 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
59 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 18.10 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
60 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Suspension | 10.60 | Max Wind and Max Weight (NL+) - D_draft,T NL+
61 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 3 | Suspension | 10.80 | Max Wind and Max Weight (NL-) - D_draft,T NL-
62 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 2 | Suspension | 10.69 | Max Wind and Max Weight (NL+) - D_draft,T NL+
63 | 366A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 68.83 | Max Wind and Max Weight (NL-) - D_draft,T NL-
64 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 54.07 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
65 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 65.04 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
66 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 27.38 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
67 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 1 | Suspension | 12.62 | Max Wind and Max Weight (NA+) - D_draft,T NA+
68 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 3 | Suspension | 12.67 | Max Wind and Max Weight (NA-) - D_draft,T NA-
69 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 2 | Suspension | 12.76 | Max Wind and Max Weight (NA+) - D_draft,T NA+
70 | 382A | WB8025 Zone 3 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 45.35 | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+
71 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_B | X-Arm | 47.85 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
72 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_M | X-Arm | 58.03 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
73 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | X-arm_T | X-Arm | 24.29 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
74 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Suspension | 11.72 | Max Wind and Max Weight (NL+) - D_draft,T NL+
75 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 3 | Suspension | 11.77 | Max Wind and Max Weight (NL-) - D_draft,T NL-
76 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 2 | Suspension | 11.86 | Max Wind and Max Weight (NA+) - D_draft,T NA+
77 | 383A | T724-0000-000044 Zone 3 Updated Crossarm NO EP.POL | 1 | Concrete Pole | 67.26 | Max Wind and Vertical Uplift (NL+) - D_draft,T NL+
78 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_B | X-Arm | 41.53 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
79 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_M | X-Arm | 50.27 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
80 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_T | X-Arm | 21.33 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
81 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | EWP Ups | X-Arm | 28.68 | Max Wind and Max Weight (NL-) - D_draft,T NL-
82 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | EWP Arm | X-Arm | 6.98 | Max Wind and Max Weight (NL+) - D_draft,T NL+
83 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 1 | Suspension | 9.58 | Max Wind and Max Weight (NA+) - D_draft,T NA+
84 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 3 | Suspension | 9.75 | Max Wind and Max Weight (NA-) - D_draft,T NA-
85 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 2 | Suspension | 9.84 | Max Wind and Max Weight (NA+) - D_draft,T NA+
86 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 4 | Suspension | 7.02 | Max Wind and Max Weight (NL-) - D_draft,T NL-
87 | 411A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 1 | Concrete Pole | 66.06 | Max Wind and Max Weight (NA-) - D_draft,T NA-
88 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_B | X-Arm | 35.37 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
89 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_M | X-Arm | 42.30 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
90 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_T | X-Arm | 17.61 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
91 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | EWP Ups | X-Arm | 25.60 | Max Wind and Max Weight (NL-) - D_draft,T NL-
92 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | EWP Arm | X-Arm | 5.53 | Mtce load - Suspension - [P3Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
93 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 1 | Suspension | 8.68 | Max Wind and Max Weight (NA+) - D_draft,T NA+
94 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 3 | Suspension | 8.60 | Max Wind and Max Weight (NA-) - D_draft,T NA-
95 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 2 | Suspension | 8.79 | Max Wind and Max Weight (NA+) - D_draft,T NA+
96 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 4 | Suspension | 5.83 | Max Wind and Max Weight (NL-) - D_draft,T NL-
97 | 413A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 1 | Concrete Pole | 65.83 | Max Wind and Max Weight (NA-) - D_draft,T NA-
98 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_B | X-Arm | 38.12 | Mtce load - Suspension - [P1Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
99 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_M | X-Arm | 46.11 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (-),T NA-
100 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | X-arm_T | X-Arm | 19.10 | Mtce load - Suspension - [P2Q=2.0, APQ=1.5, 100Pa, max weight] (+),T NA+
101 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | EWP Ups | X-Arm | 27.50 | Max Wind and Max Weight (NA-) - D_draft,T NA-
102 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | EWP Arm | X-Arm | 6.46 | Max Wind and Max Weight (NA-) - D_draft,T NA-
103 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 1 | Suspension | 8.90 | Max Wind and Max Weight (NA+) - D_draft,T NA+
104 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 3 | Suspension | 8.87 | Max Wind and Max Weight (NA-) - D_draft,T NA-
105 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 2 | Suspension | 9.02 | Max Wind and Max Weight (NA+) - D_draft,T NA+
106 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 4 | Suspension | 6.14 | Max Wind and Max Weight (NA-) - D_draft,T NA-
107 | 414A | T724-0000-000044 Zone 3 Updated Crossarm.POL | 1 | Concrete Pole | 66.51 | Max Wind and Max Weight (NL-) - D_draft,T NL-